26511 | SCHEDULED MAINTENANCE - WAVERLEY RD | 2011-11-09 09:58 | 2011-11-09 | 2011-11-09 13:00 | Calculated | TF1537 | TF1537 - Transformer Fuse: TF1537 |  | 111SEG359RET | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 182 | 3 | 24466 | 546 | 0.02232 | 0.00012262 | 15 | 2732 | 2011/2012 | November-2011 | 11 | 2011
26512 | LV LINE DOWN - SH 3 - MAHOENUI | 2011-11-09 13:16 | 2011-11-09 | 2011-11-09 14:40 | Calculated | TF1891 | TF1891 - Transformer Fuse: TF1891 |  | 128SEG1358-1602 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 2 | 24466 | 166 | 0.00678 | 8.1746e-05 | 30 | 2496 | 2011/2012 | November-2011 | 11 | 2011
26513 | LV MAINTENANCE - UPGRADING LV FUSING - KAWAKAWA RD | 2011-11-10 10:20 | 2011-11-10 | 2011-11-10 11:47 | Calculated | TF2697 | TF2697 - Transformer Fuse: TF2697 |  | 123SEG468 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 86 | 1 | 24466 | 86 | 0.00352 | 4.0873e-05 | 30 | 2584 | 2011/2012 | November-2011 | 11 | 2011
26514 | LV MAINTENANCE - SH 4 ARAMATAI | 2011-11-11 10:03 | 2011-11-11 | 2011-11-11 14:58 | Calculated | TF2080 | TF2080 - Transformer Fuse: TF2080 |  | No Segment | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 295 | 2 | 24466 | 590 | 0.02412 | 8.1746e-05 | 10 | 2951 | 2011/2012 | November-2011 | 11 | 2011
26515 | LV LINE DOWN - SH 3 KOPAKI | 2011-11-11 13:16 | 2011-11-11 | 2011-11-11 14:14 | Calculated | TF1126 | TF1126 - Transformer Fuse: TF1126 |  | 103SEG237 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 3 | 24466 | 174 | 0.00711 | 0.00012262 | 15 | 874 | 2011/2012 | November-2011 | 11 | 2011
26516 | HV FUSE AT TX06E09 REPLACED - WAITANGATA RD | 2011-11-11 21:46 | 2011-11-11 | 2011-11-11 23:31 | Calculated | TF6E9 | TF6E9 - Transformer Fuse: TF6E9 |  | No Segment | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 105 | 4 | 24466 | 420 | 0.01717 | 0.00016349 | 15 | 1578 | 2011/2012 | November-2011 | 11 | 2011
26522 | HV FUSE AT TX 4272 GOT REPLACED - MANGAPAPA RD | 2011-11-12 19:25 | 2011-11-12 | 2011-11-12 20:20 | Calculated | TF4272 | TF4272 - Transformer Fuse:TF4272 |  | 422SEG5272-5274 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 55 | 1 | 24466 | 55 | 0.00225 | 4.0873e-05 | 0 | 0 | 2011/2012 | November-2011 | 11 | 2011
26523 | BIRD ON LINE - LOWER RETARUKE SUB | 2011-11-14 06:45 | 2011-11-14 | 2011-11-14 09:16 | Calculated | 5490 | 5490 - Recloser with Bypass 5490 |  | 410SEG5490-5438 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 150 | 73 | 24466 | 8069 | 0.3298 | 0.0029837 | 428 | 49811 | 2011/2012 | November-2011 | 11 | 2011
26524 | LINE MAINTENANCE - POKURU RD - AT OKAMA BLOCK | 2011-11-14 09:06 | 2011-11-14 | 2011-11-14 16:04 | Calculated | 442 | 442 - Fused Link 442 |  | 129SEG442-2238 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 418 | 28 | 24466 | 11708 | 0.47854 | 0.0011444 | 265 | 110809 | 2011/2012 | November-2011 | 11 | 2011
26526 | LV MAINTENANCE - TE WAITERE RD | 2011-11-14 10:33 | 2011-11-14 | 2011-11-14 18:55 | Calculated | TF538 | TF538 - Transformer Fuse: TF538 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 502 | 5 | 24466 | 2510 | 0.10259 | 0.00020437 | 30 | 15064 | 2011/2012 | November-2011 | 11 | 2011
26527 | DOWNGRADE TX 21O4 - TANGIWAI STATION RD | 2011-11-14 11:16 | 2011-11-14 | 2011-11-14 14:45 | Calculated | TF21O4 | TF21O4 - Transformer Fuse: TF21O4 |  | 416SEG6174-5689 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 209 | 4 | 24466 | 836 | 0.03417 | 0.00016349 | 30 | 6274 | 2011/2012 | November-2011 | 11 | 2011
26528 | UPGRADE TX 21O16 - TANGIWAI STATION RD | 2011-11-14 11:56 | 2011-11-14 | 2011-11-14 13:49 | Calculated | TF21O16 | TF21O16 - Transformer Fuse: TF21O16 |  | 416SEG6174-5689 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 112 | 3 | 24466 | 336 | 0.01373 | 0.00012262 | 22.5 | 2523 | 2011/2012 | November-2011 | 11 | 2011
26535 | STOCK RUBBING - PIAWA RD | 2011-11-15 08:19 | 2011-11-15 | 2011-11-15 09:16 | Calculated | TF6J11 | TF6J11 - Transformer Fuse: TF6J11 |  | No Segment | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AFAR | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 57 | 2 | 24466 | 114 | 0.00466 | 8.1746e-05 | 15 | 857 | 2011/2012 | November-2011 | 11 | 2011
26539 | LINE MAINTENANCE - POKURU RD - AT OKAMA BLOCK | 2011-11-15 09:00 | 2011-11-15 | 2011-11-15 15:14 | Calculated | 442 | 442 - Fused Link 442 |  | 129SEG442-2238 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 374 | 28 | 24466 | 10475 | 0.42815 | 0.0011444 | 315 | 117851 | 2011/2012 | November-2011 | 11 | 2011
26537 | LV MAINTENANCE - MIRO ST | 2011-11-15 10:56 | 2011-11-15 | 2011-11-15 12:37 | Calculated | TF8J48 | TF8J48 - Transformer Fuse: TF8J48 |  | 408SEG5390-5621 | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 101 | 27 | 24466 | 2730 | 0.11158 | 0.0011036 | 200 | 20223 | 2011/2012 | November-2011 | 11 | 2011
26538 | UPGRADE TX 2531 - TIROHANGA RD | 2011-11-15 11:38 | 2011-11-15 | 2011-11-15 16:02 | Calculated | TF2531 | TF2531 - Transformer Fuse: TF2531 |  | 129SEG451-787 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 2 | 24466 | 528 | 0.02158 | 8.1746e-05 | 25 | 6603 | 2011/2012 | November-2011 | 11 | 2011
26540 | REPLACE POLES AND XARMS - TAHAROA RD - BY OLD QUARRY | 2011-11-16 09:02 | 2011-11-16 | 2011-11-16 15:35 | Calculated | 277 | 277 - Recloser with Bypass 277 |  | 125SEG277-268 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 346 | 57 | 24466 | 17879 | 0.73077 | 0.0023298 | 391 | 124107 | 2011/2012 | November-2011 | 11 | 2011
26542 | HV FUSE AT TX 10K11 REPLACED - HIKUMUTU RD | 2011-11-16 11:46 | 2011-11-16 | 2011-11-16 12:11 | Calculated | TF10K11 | TF10K11 - Transformer Fuse: TF10K11 |  | 409SEG5403-5662RET | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 24 | 2 | 24466 | 48 | 0.00196 | 8.1746e-05 | 15 | 362 | 2011/2012 | November-2011 | 11 | 2011
26546 | REPLACE POLES AND XARMS - TAHAROA RD - BY OLD QUARRY | 2011-11-17 09:00 | 2011-11-17 | 2011-11-17 15:35 | Calculated | 268 | 268 - Air Break Switch 268 |  | 125SEG268-281 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 323 | 99 | 24466 | 8745 | 0.35743 | 0.0040464 | 773 | 46705 | 2011/2012 | November-2011 | 11 | 2011
26543 | UPGRADE TX - SH 3 HANGATIKI | 2011-11-17 09:38 | 2011-11-17 | 2011-11-17 15:34 | Calculated | TF176 | TF176 - Transformer Fuse: TF176 |  | 110SEG383 | Hangatiki East 102-01 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 355 | 3 | 24466 | 1065 | 0.04353 | 0.00012262 | 25 | 8879 | 2011/2012 | November-2011 | 11 | 2011
26547 | COCKY VS LINE - LINES DOWN | 2011-11-17 10:29 | 2011-11-17 | 2011-11-17 16:06 | Calculated | 557 | 557 - Air Break Switch 557 |  | 120SEG557 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 337 | 6 | 24466 | 2023 | 0.08269 | 0.00024524 | 35.8333 | 12087 | 2011/2012 | November-2011 | 11 | 2011
26548 | HIGH WINDS - C PHASE E/F - TAHAROA "A" | 2011-11-18 01:42 | 2011-11-18 | 2011-11-18 01:52 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24466 |  | 0 | 0 |  |  | 2011/2012 | November-2011 | 11 | 2011
26551 | REPLACE POLES AND XARMS - TAHAROA RD - BY OLD QUARRY | 2011-11-18 08:59 | 2011-11-18 | 2011-11-18 15:36 | Calculated | 268 | 268 - Air Break Switch 268 |  | 125SEG268-281 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 300 | 99 | 24466 | 8083 | 0.33038 | 0.0040464 | 773 | 43065 | 2011/2012 | November-2011 | 11 | 2011
26552 | CHANGE TX2080 - SH 4 ARAMATAI | 2011-11-18 10:02 | 2011-11-18 | 2011-11-18 12:31 | Calculated | TF2080 | TF2080 - Transformer Fuse: TF2080 |  | No Segment | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 149 | 2 | 24466 | 298 | 0.01218 | 8.1746e-05 | 10 | 1492 | 2011/2012 | November-2011 | 11 | 2011
26553 | INSTALL NEW XIRIA SWITCHGEAR AT SAWMILL - TE KUMI RD | 2011-11-18 11:38 | 2011-11-18 | 2011-11-18 17:41 | Calculated | TF564 | TF564 - Transformer Fuse: TF564 |  | 108SEG180-182 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 363 | 1 | 24466 | 363 | 0.01484 | 4.0873e-05 | 750 | 272450 | 2011/2012 | November-2011 | 11 | 2011
26554 | TREE THROUGH LINE - TIHOI RD | 2011-11-18 12:44 | 2011-11-18 | 2011-11-18 17:32 | Calculated | 2102 | 2102 - Circuit Breaker Mareatai 11 kV 2102 |  | No Segment | 210-01 Maraetai | Rural D | Whakamaru | Maraetai Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 286 | 605 | 24466 | 22592 | 0.9234 | 0.024728 | 4604.1502 | 182499 | 2011/2012 | November-2011 | 11 | 2011
26549 | HIGH WINDS - C PHASE O/C - TAHAROA "A" | 2011-11-18 12:47 | 2011-11-18 | 2011-11-18 12:54 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24466 |  | 0 | 0 |  |  | 2011/2012 | November-2011 | 11 | 2011
26550 | HIGH WINDS - C PHASE O/C - TAHAROA "A" | 2011-11-18 13:31 | 2011-11-18 | 2011-11-18 15:11 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24466 |  | 0 | 0 |  |  | 2011/2012 | November-2011 | 11 | 2011
26555 | FAULTY RECLOSER 5641 - NIHONIHO | 2011-11-19 06:45 | 2011-11-19 | 2011-11-19 09:10 | Calculated | 5641 | 5641 - Recloser with Bypass & Links 5641 |  | 413SEG6781-5666 | Ohura 413-01 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 381 | 24466 | 55327 | 2.2614 | 0.015573 | 2600.4048 | 377622 | 2011/2012 | November-2011 | 11 | 2011
26558 | BROKEN DDO - MAIRE RD | 2011-11-20 13:53 | 2011-11-20 | 2011-11-20 16:26 | Calculated | 1529 | 1529 - Fused Link 1529 |  | No Segment | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 152 | 2 | 24466 | 211 | 0.00862 | 8.1746e-05 | 18 | 2461 | 2011/2012 | November-2011 | 11 | 2011
26559 | ROTTEN DEADEND AT ABS 516 - KAIRIMU RD - OFF MARAKOPA | 2011-11-20 15:11 | 2011-11-20 | 2011-11-20 16:11 | Calculated | 516 | 516 - Fused Link 516 |  | 125SEG516-740 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) | Cables : Other | Asset Related | Cable - Underground | FAIL:FCAB:FCBT | Underground Cable Termination Failure - Other | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 147 | 24466 | 6159 | 0.25174 | 0.0060083 | 972.1831 | 44934 | 2011/2012 | November-2011 | 11 | 2011
26560 | LV CLASH - TIHOI RD | 2011-11-21 09:17 | 2011-11-21 | 2011-11-21 10:28 | Calculated | TF743 | TF743 - Transformer Fuse: TF743 |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 2 | 24466 | 142 | 0.0058 | 8.1746e-05 | 25 | 1779 | 2011/2012 | November-2011 | 11 | 2011
26561 | HIGH WINDS - POIHIPI RD - CORNER WERETA | 2011-11-21 10:27 | 2011-11-21 | 2011-11-21 11:49 | Calculated | 471 | 471 - Fused Link 471 |  | 123SEG471 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 10 | 24466 | 821 | 0.03356 | 0.00040873 | 85 | 6981 | 2011/2012 | November-2011 | 11 | 2011
26562 | FUSE PULLED APART - SH 32 | 2011-11-22 08:35 | 2011-11-22 | 2011-11-22 10:39 | Calculated | TF6Q5 | TF6Q5 - Transformer Fuse: TF6Q5 |  | No Segment | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 124 | 2 | 24466 | 248 | 0.01014 | 8.1746e-05 | 15 | 1862 | 2011/2012 | November-2011 | 11 | 2011
26581 | REPLACE POLES 42100040 - ONGAURE | 2011-11-22 08:38 | 2011-11-22 | 2011-11-22 16:41 | Calculated | 5462 | 5462 - Sectionaliser with Bypass & Links 5462 |  | 421SEG6554-5462RET | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 430 | 123 | 24466 | 4536 | 0.1854 | 0.0050274 | 877.5 | 33833 | 2011/2012 | November-2011 | 11 | 2011
26579 | BROKEN LV XARM - SH 41 | 2011-11-22 09:58 | 2011-11-22 | 2011-11-22 11:31 | Calculated | TF9R5 | TF9R5 - Transformer Fuse: TF9R5 |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 93 | 3 | 24466 | 279 | 0.0114 | 0.00012262 | 15 | 1398 | 2011/2012 | November-2011 | 11 | 2011
26583 | WIRE ON XARM AT POLE 45 - POKURU RD | 2011-11-22 10:30 | 2011-11-22 | 2011-11-22 14:47 | Calculated | 634 | 634 - Air Break Switch 634 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 54 | 24466 | 7676 | 0.31374 | 0.0022071 | 795 | 113009 | 2011/2012 | November-2011 | 11 | 2011
26582 | FAULTY TX 2884 - SH 3 | 2011-11-22 11:25 | 2011-11-22 | 2011-11-22 12:54 | Calculated | TF2884 | TF2884 - Transformer Fuse: TF2884 |  | 128SEG1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 1 | 24466 | 89 | 0.00364 | 4.0873e-05 | 15 | 1337 | 2011/2012 | November-2011 | 11 | 2011
26595 | UNKNOWN - MANGAKINO FEEDER | 2011-11-22 16:11 | 2011-11-22 | 2011-11-22 17:04 | Calculated | 2082 | 2082 - Circuit Breaker Maraetai Sub 2082 |  | No Segment | 210-01 Maraetai | Rural D | Mangakino | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 493 | 24466 | 25375 | 1.0372 | 0.02015 | 2094.2742 | 105402 | 2011/2012 | November-2011 | 11 | 2011
26597 | REPLACE POLES AND XARMS - LINE RENEWAL PROJECT | 2011-11-23 09:11 | 2011-11-23 | 2011-11-23 15:21 | Calculated | 5686 | 5686 - Fused Link 5686 |  | 416SEG5686 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 370 | 15 | 24466 | 5552 | 0.22693 | 0.0006131 | 130 | 48121 | 2011/2012 | November-2011 | 11 | 2011
26598 | BROKEN STAY - WAIHORO RD | 2011-11-23 14:25 | 2011-11-23 | 2011-11-23 14:55 | Calculated | TF969 | TF969 - Transformer Fuse: TF969 |  | No Segment | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation | OH Lines : Stay Wire | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 1 | 24466 | 30 | 0.00123 | 4.0873e-05 | 15 | 453 | 2011/2012 | November-2011 | 11 | 2011
26599 | UNKNOWN - MANGATEITEI RD | 2011-11-23 15:11 | 2011-11-23 | 2011-11-23 16:59 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 27 | 24466 | 2922 | 0.11943 | 0.0011036 | 281.4286 | 30464 | 2011/2012 | November-2011 | 11 | 2011
26600 | UNKNOWN - WAITOMO VALLEY RD | 2011-11-24 06:56 | 2011-11-24 | 2011-11-24 07:20 | Calculated | TF214 | TF214 - Transformer Fuse: TF214 |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 5 | 24466 | 121 | 0.00495 | 0.00020437 | 30 | 727 | 2011/2012 | November-2011 | 11 | 2011
26601 | WIND - TAUMATATOTORO WEST | 2011-11-24 07:20 | 2011-11-24 | 2011-11-24 10:31 | Calculated | 292 | 292 - Fused Link 292 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 190 | 8 | 24466 | 1521 | 0.06217 | 0.00032698 | 73 | 13887 | 2011/2012 | November-2011 | 11 | 2011
26602 | LINE DOWN - ONGARUE RD | 2011-11-24 07:30 | 2011-11-24 | 2011-11-24 13:45 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 375 | 15 | 24466 | 4277 | 0.17481 | 0.0006131 | 117.5 | 31148 | 2011/2012 | November-2011 | 11 | 2011
26603 | JUMPER OFF AT LINK 5896 | 2011-11-24 08:33 | 2011-11-24 | 2011-11-24 11:25 | Calculated | 5959 | 5959 - Air Break Switch 5959 |  | 406SEG5959-5899 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 326 | 24466 | 54530 | 2.2288 | 0.013325 | 1541.25 | 257550 | 2011/2012 | November-2011 | 11 | 2011
26604 | JUMPER OFF | 2011-11-24 13:55 | 2011-11-24 | 2011-11-24 14:46 | Calculated | 1627 | 1627 - Recloser with Incoming Link1627 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 51 | 9 | 24466 | 460 | 0.0188 | 0.00036786 | 80 | 4090 | 2011/2012 | November-2011 | 11 | 2011
26605 | REPLACE POLES AND XARMS - COAST FEEDER | 2011-11-25 09:19 | 2011-11-25 | 2011-11-25 15:36 | Calculated | 268 | 268 - Air Break Switch 268 |  | 125SEG268-281 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 284 | 99 | 24466 | 7703 | 0.31485 | 0.0040464 | 773 | 41050 | 2011/2012 | November-2011 | 11 | 2011
26607 | CONNECT EARTH - SH 40 | 2011-11-25 12:38 | 2011-11-25 | 2011-11-25 12:56 | Calculated | TF4H2 | TF4H2 - Transformer Fuse: TF4H2 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 18 | 1 | 24466 | 18 | 0.00074 | 4.0873e-05 | 7.5 | 137 | 2011/2012 | November-2011 | 11 | 2011
26608 | TRACTOR VS LV POLE AT TX 414 - WAVERLEY RD | 2011-11-25 17:48 | 2011-11-25 | 2011-11-25 22:58 | Calculated | TF414 | TF414 - Transformer Fuse: TF414 |  | 111SEG359RET | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 310 | 2 | 24466 | 620 | 0.02534 | 8.1746e-05 | 30 | 9306 | 2011/2012 | November-2011 | 11 | 2011
26609 | BLOWN HV FUSE AT TX 3289 - TAHAE RD | 2011-11-26 02:26 | 2011-11-26 | 2011-11-26 04:40 | Calculated | TF3289 | TF3289 - Transformer Fuse: TF3289 |  | 119SEG241 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 1 | 24466 | 134 | 0.00548 | 4.0873e-05 | 75 | 10063 | 2011/2012 | November-2011 | 11 | 2011
26610 | TREE VS LINE - TE KUITI SOUTH FEEDER | 2011-11-26 11:26 | 2011-11-26 | 2011-11-26 15:43 | Calculated | 103 | 103 - Circuit Breaker Te Kuiti South 103 |  | No Segment | 206-01 Waitete | Urban A | Te Kuiti South | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 245 | 1203 | 24466 | 40270 | 1.646 | 0.04917 | 8242.9167 | 271344 | 2011/2012 | November-2011 | 11 | 2011
26611 | BLOWN LINK 696 - MAROTIRI RD | 2011-11-26 12:01 | 2011-11-26 | 2011-11-26 14:00 | Calculated | 696 | 696 - Fused Link 696 |  | 123SEG696 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 2 | 24466 | 238 | 0.00973 | 8.1746e-05 | 40 | 4766 | 2011/2012 | November-2011 | 11 | 2011
26615 | BLOWN LINK 5513 - HIKUMUTU RD | 2011-11-27 07:55 | 2011-11-27 | 2011-11-27 09:20 | Calculated | 5513 | 5513 - Fused Link 5513 |  | 403SEG5513 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 85 | 2 | 24466 | 170 | 0.00695 | 8.1746e-05 | 30 | 2556 | 2011/2012 | November-2011 | 11 | 2011
26617 | TRACTOR VS STAY - WAITOMO CAVES RD | 2011-11-27 17:10 | 2011-11-27 | 2011-11-27 18:55 | Calculated | 679 | 679 - Air Break Switch 679 |  | 101SEG679-267 | Caves 101-05 | Urban A | Caves | Hangatiki Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 19 | 24466 | 1238 | 0.0506 | 0.00077659 | 175 | 11407 | 2011/2012 | November-2011 | 11 | 2011
26618 | DISCONNECT GENSET AND REPAIR LINE - AWAKINO RD | 2011-11-28 09:16 | 2011-11-28 | 2011-11-28 11:01 | Calculated | 220 | 220 - Fused Link 220 |  | 104SEG217-730 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 6 | 24466 | 631 | 0.02579 | 0.00024524 | 45 | 4732 | 2011/2012 | November-2011 | 11 | 2011
26619 | MAINTENANCE - RAURIMU FEEDER | 2011-11-28 09:34 | 2011-11-28 | 2011-11-28 14:50 | Calculated | 5161 | 5161 - Fused Link 5161 |  | 409SEG5138-5235 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 300 | 14 | 24466 | 4188 | 0.17118 | 0.00057222 | 150 | 44872 | 2011/2012 | November-2011 | 11 | 2011
26620 | FUSE PULLED APART AND LV SHORTING ON POLE - SH 1 | 2011-11-29 07:10 | 2011-11-29 | 2011-11-29 11:51 | Calculated | TF9U5 | TF9U5 - Transformer Fuse: TF9U5 |  | No Segment | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 265 | 67 | 24466 | 8933 | 0.36512 | 0.0027385 | 350 | 46358 | 2011/2012 | November-2011 | 11 | 2011
26624 | REPLACE XARMS ON POLE 4210037 - ONGARUE FEEDER | 2011-11-29 08:42 | 2011-11-29 | 2011-11-29 15:03 | Calculated | 6640 | 6640 - Air Break Switch 6640 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 197 | 251 | 24466 | 9673 | 0.39536 | 0.010259 | 1746.5 | 63444 | 2011/2012 | November-2011 | 11 | 2011
26627 | FAULTY LA AT TX 4237 - MILL RD | 2011-11-29 10:51 | 2011-11-29 | 2011-11-29 16:59 | Calculated | TF4237 | TF4237 - Transformer Fuse: TF4237 |  | No Segment | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 187 | 1 | 24466 | 186 | 0.0076 | 4.0873e-05 | 50 | 9325 | 2011/2012 | November-2011 | 11 | 2011
26628 | UPGRADE TX 4040 TO PAD MOUNT - WAIOTAKA RD | 2011-11-30 09:36 | 2011-11-30 | 2011-11-30 13:28 | Calculated | TF4040 | TF4040 - Transformer Fuse: TF4040 |  | No Segment | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 232 | 1 | 24466 | 232 | 0.00948 | 4.0873e-05 | 15 | 3483 | 2011/2012 | November-2011 | 11 | 2011
26630 | LIGHTNING - WHAREPAPA RD | 2011-11-30 11:08 | 2011-11-30 | 2011-11-30 12:23 | Calculated | TF1310 | TF1310 - Transformer Fuse: TF1310 |  | 122SEG392-568 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 24466 | 75 | 0.00307 | 4.0873e-05 | 10 | 751 | 2011/2012 | November-2011 | 11 | 2011
26631 | BLOWN HV FUSE AT TX1359 - PAEWHENUA RD | 2011-11-30 12:18 | 2011-11-30 | 2011-11-30 14:15 | Calculated | TF1359 | TF1359 - Transformer Fuse: TF1359 |  | 111SEG1148 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 1 | 24466 | 117 | 0.00478 | 4.0873e-05 | 5 | 585 | 2011/2012 | November-2011 | 11 | 2011
26632 | REPLACE ROTTEN POLES 1222149 AND 1222140 - WHAREPAPA | 2011-12-01 09:07 | 2011-12-01 | 2011-12-01 15:11 | Calculated | 369 | 369 - Fused Link 369 |  | 122SEG369-678 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 363 | 14 | 24466 | 5084 | 0.2078 | 0.00057222 | 195 | 70817 | 2011/2012 | December-2011 | 12 | 2011
26633 | INSERT PROP POLE BETWEEN 32/4 AND 32/5 - WAIHAHA FEEDER | 2011-12-01 10:04 | 2011-12-01 | 2011-12-01 11:26 | Calculated | 5529 | 5529 - Recloser 5529 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 81 | 69 | 24466 | 5597 | 0.22877 | 0.0028202 | 432.5 | 35082 | 2011/2012 | December-2011 | 12 | 2011
26650 | ISOLATE FOR PRIVATE LINE TREE WORK - WAIHAHA FEEDER | 2011-12-02 09:11 | 2011-12-02 | 2011-12-02 15:10 | Calculated | 5531 | 5531 - Sectionaliser 5531 |  | 426SEG5531 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 359 | 12 | 24466 | 4313 | 0.17629 | 0.00049048 | 125 | 44929 | 2011/2012 | December-2011 | 12 | 2011
26651 | ADJUST TAPS - NGAPEKE RD | 2011-12-02 10:06 | 2011-12-02 | 2011-12-02 10:35 | Calculated | TF3345 | TF3345 - Transformer Fusa TF3345 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | PTRN2 | POUT:PTRN2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 11 | 2 | 24466 | 10 | 0.00041 | 8.1746e-05 | 125 | 664 | 2011/2012 | December-2011 | 12 | 2011
26660 | LV FAULT - MANGAOKEWA RD | 2011-12-02 11:43 | 2011-12-02 | 2011-12-02 13:01 | Calculated | TF141 | TF141 - Transformer Fuse: TF141 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 2 | 24466 | 156 | 0.00638 | 8.1746e-05 | 15 | 1172 | 2011/2012 | December-2011 | 12 | 2011
26661 | BROKEN XARM AT TX 1503 - RANGITOTO RD | 2011-12-02 17:26 | 2011-12-02 | 2011-12-02 19:11 | Calculated | TF1503 | TF1503 - Transformer Fuse: TF1503 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 2 | 24466 | 208 | 0.0085 | 8.1746e-05 | 15 | 1562 | 2011/2012 | December-2011 | 12 | 2011
26662 | FAULTY LA - SANDEL RD | 2011-12-02 19:01 | 2011-12-02 | 2011-12-02 21:28 | Calculated | TF734 | TF734 - Transformer Fuse: TF734 |  | No Segment | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 3 | 24466 | 441 | 0.01803 | 0.00012262 | 30 | 4416 | 2011/2012 | December-2011 | 12 | 2011
26663 | BIRD CONTACT - WHAREROA SUB | 2011-12-03 07:34 | 2011-12-03 | 2011-12-03 09:00 | Calculated | 5619 | 5619 - Fused Link 5619 |  | 426SEG6205-5619 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 86 | 81 | 24466 | 6979 | 0.28525 | 0.0033107 | 527.5 | 45452 | 2011/2012 | December-2011 | 12 | 2011
26665 | MAGPIE AT TX 3H8 - TAPUWAHINE SUB | 2011-12-04 19:54 | 2011-12-04 | 2011-12-05 08:05 | Calculated | 5465 | 5465 - Recloser 5465 |  | No Segment | No Asset Group | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 731 | 44 | 24466 | 24814 | 1.0142 | 0.0017984 | 285.5 | 156344 | 2011/2012 | December-2011 | 12 | 2011
26666 | REPLACE HV FUSE AT TX9J11 - MAIN SOUTH RD | 2011-12-05 13:04 | 2011-12-05 | 2011-12-05 14:01 | Calculated | TF9J11 | TF9J11 - Transformer Fuse: TF9J11 |  | No Segment | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 1 | 24466 | 57 | 0.00233 | 4.0873e-05 | 10 | 571 | 2011/2012 | December-2011 | 12 | 2011
26667 | UNKNOWN EARTH FAULT - TAHAROA A | 2011-12-06 00:14 | 2011-12-06 | 2011-12-06 07:51 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24466 |  | 0 | 0 |  |  | 2011/2012 | December-2011 | 12 | 2011
26668 | REPLACE HV FUSE AT TX2373 - TAPUWAE RD | 2011-12-06 08:01 | 2011-12-06 | 2011-12-06 10:00 | Calculated | TF2373 | TF2373 - Transformer Fuse: TF2373 |  | No Segment | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 119 | 1 | 24466 | 119 | 0.00486 | 4.0873e-05 | 10 | 1191 | 2011/2012 | December-2011 | 12 | 2011
26669 | CHANGE TX AND POLE - SCOTT RD | 2011-12-06 09:02 | 2011-12-06 | 2011-12-06 12:09 | Calculated | TF922 | TF922 - Transformer Fuse: TF922 |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 187 | 2 | 24466 | 374 | 0.01529 | 8.1746e-05 | 25 | 4679 | 2011/2012 | December-2011 | 12 | 2011
26670 | LV FAULT - PARITANNIWHA RD | 2011-12-06 09:12 | 2011-12-06 | 2011-12-06 11:11 | Calculated | TF1424 | TF1424 - Transformer Fuse: TF1424 |  | 120SEG745 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 1 | 24466 | 118 | 0.00482 | 4.0873e-05 | 50 | 5907 | 2011/2012 | December-2011 | 12 | 2011
26671 | MAGPIE - SH 4 ARAMATAI | 2011-12-06 09:13 | 2011-12-06 | 2011-12-06 10:57 | Calculated | TF2080 | TF2080 - Transformer Fuse: TF2080 |  | No Segment | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 103 | 2 | 24466 | 206 | 0.00842 | 8.1746e-05 | 10 | 1033 | 2011/2012 | December-2011 | 12 | 2011
26672 | DISCONNECT OLD SPUR LINE - RAURIMU FEEDER | 2011-12-06 09:20 | 2011-12-06 | 2011-12-06 14:09 | Calculated | 5438 | 5438 - Fused Link 5438 |  | 410SEG5438-5597 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 228 | 73 | 24466 | 11618 | 0.47486 | 0.0029837 | 418 | 56393 | 2011/2012 | December-2011 | 12 | 2011
26673 | REPLACE POLES AND XARMS - MOKAU | 2011-12-06 10:34 | 2011-12-06 | 2011-12-06 15:03 | Calculated | 1623 | 1623 - Fused Link 1623 |  | 128SEG1600-1623 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 268 | 17 | 24466 | 4563 | 0.1865 | 0.00069484 | 95 | 25502 | 2011/2012 | December-2011 | 12 | 2011
26674 | BIRDS NEST IN LV - MAIHIIHI RD | 2011-12-06 10:46 | 2011-12-06 | 2011-12-06 12:16 | Calculated | TF604 | TF604 - Transformer Fuse: TF604 |  | No Segment | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 1 | 24466 | 90 | 0.00368 | 4.0873e-05 | 5 | 451 | 2011/2012 | December-2011 | 12 | 2011
26675 | LIGHTNING - SH 47 | 2011-12-06 15:26 | 2011-12-06 | 2011-12-06 16:49 | Calculated | TF12P05 | TF12P05 - Transformer Fuse: TF12P05 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 83 | 1 | 24466 | 83 | 0.00339 | 4.0873e-05 | 15 | 1247 | 2011/2012 | December-2011 | 12 | 2011
26676 | MAGPIE AT TX 8E7 - ROTO RD | 2011-12-06 15:26 | 2011-12-06 | 2011-12-06 16:32 | Calculated | TF8E7 | TF8E7 - Transformer Fuse: TF8E7 |  | No Segment | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 66 | 1 | 24466 | 66 | 0.0027 | 4.0873e-05 | 3 | 198 | 2011/2012 | December-2011 | 12 | 2011
26677 | BRANCH ON LINE - TAHAIA RD | 2011-12-06 17:57 | 2011-12-06 | 2011-12-06 18:23 | Calculated | TF385 | TF385 - Transformer Fuse: TF385 |  | No Segment | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 2 | 24466 | 50 | 0.00204 | 8.1746e-05 | 25 | 629 | 2011/2012 | December-2011 | 12 | 2011
26678 | SECTIONALISER 5170 TRIPPED - LOWER RETARUKE RD | 2011-12-06 18:18 | 2011-12-06 | 2011-12-06 19:29 | Calculated | 5170 | 5170 - Sectionaliser 5170 |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 71 | 21 | 24466 | 1495 | 0.06111 | 0.00085833 | 168 | 11964 | 2011/2012 | December-2011 | 12 | 2011
26679 | RECLOSER 5529 TRIPPED - WAIHAHA FEEDER | 2011-12-07 07:23 | 2011-12-07 | 2011-12-07 09:05 | Calculated | 5529 | 5529 - Recloser 5529 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 102 | 69 | 24466 | 7048 | 0.28807 | 0.0028202 | 432.5 | 44179 | 2011/2012 | December-2011 | 12 | 2011
26680 | LV FAULT - PAERATA RD | 2011-12-07 09:14 | 2011-12-07 | 2011-12-07 10:24 | Calculated | TF2572 | TF2572 - Transformer Fuse: TF2572 |  | 129SEG402-725 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 1 | 24466 | 70 | 0.00286 | 4.0873e-05 | 30 | 2104 | 2011/2012 | December-2011 | 12 | 2011
26681 | REPLACE POLES AND XARMS - MOKAU FEEDER | 2011-12-07 10:38 | 2011-12-07 | 2011-12-07 15:08 | Calculated | 1623 | 1623 - Fused Link 1623 |  | 128SEG1600-1623 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 270 | 17 | 24466 | 4594 | 0.18777 | 0.00069484 | 95 | 25676 | 2011/2012 | December-2011 | 12 | 2011
26682 | MAINTENANCE - MAIHIIHI FEEDER | 2011-12-08 09:04 | 2011-12-08 | 2011-12-08 15:43 | Calculated | 357 | 357 - Fused Link 357 |  | 111SEG357-579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 399 | 29 | 24466 | 11575 | 0.47311 | 0.0011853 | 370 | 147685 | 2011/2012 | December-2011 | 12 | 2011
26683 | FAULTY INSULATOR AT POLE 3 - KURATAU/TAUMANUNUI 33 | 2011-12-08 09:18 | 2011-12-08 | 2011-12-08 11:46 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 1230 | 24466 | 1291 | 0.05277 | 0.050274 | 9011.4251 | 9461 | 2011/2012 | December-2011 | 12 | 2011
26684 | REPLACE POLES AND XARMS - MOKAU FEEDER | 2011-12-08 10:33 | 2011-12-08 | 2011-12-08 14:35 | Calculated | 1623 | 1623 - Fused Link 1623 |  | 128SEG1600-1623 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 242 | 17 | 24466 | 4116 | 0.16823 | 0.00069484 | 95 | 23004 | 2011/2012 | December-2011 | 12 | 2011
26685 | LOW LINE - BENT PIN AT POLE 21 - SH 4 BY NEAL'S | 2011-12-08 11:44 | 2011-12-08 | 2011-12-08 14:38 | Calculated | 1723 | 1723 - Fused Link 1723 |  | 115SEG1723-1724 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 173 | 48 | 24466 | 4568 | 0.18671 | 0.0019619 | 363 | 33653 | 2011/2012 | December-2011 | 12 | 2011
26686 | LV FAULT AT TX 4157 - PAREKAWA DR | 2011-12-08 14:38 | 2011-12-08 | 2011-12-08 15:41 | Calculated | TF4157 | TF4157 - Transformer Fuse: TF4157 |  | 425SEG6552-6550 | Motuoapa 425-01 | Rural D | Motuoapa | Kiko Road Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 36 | 24466 | 2236 | 0.09139 | 0.0014714 | 300 | 18639 | 2011/2012 | December-2011 | 12 | 2011
26688 | REPLACE HV LINK 6617 - KOKAOROA RD | 2011-12-09 07:51 | 2011-12-09 | 2011-12-09 12:55 | Calculated | 755 | 755 - Fused Link 755 |  | 101SEG755 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 304 | 6 | 24466 | 965 | 0.03944 | 0.00024524 | 60 | 8576 | 2011/2012 | December-2011 | 12 | 2011
26689 | REPLACE POLE 1191056 - PUREORA FEEDER | 2011-12-09 08:56 | 2011-12-09 | 2011-12-09 13:08 | Calculated | 405 | 405 - Air Break Switch 405 |  | 119SEG2205-489 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 232 | 22 | 24466 | 5093 | 0.20817 | 0.00089921 | 435 | 100702 | 2011/2012 | December-2011 | 12 | 2011
26690 | SCHEDULED MAINTENANCE - SOLDIERS RD | 2011-12-09 09:09 | 2011-12-09 | 2011-12-09 14:37 | Calculated | 5947 | 5947 - Air Break Switch 5947 |  | 415SEG5947-6617 | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 328 | 17 | 24466 | 5584 | 0.22824 | 0.00069484 | 210 | 68984 | 2011/2012 | December-2011 | 12 | 2011
26691 | MAGPIE - SH 43 | 2011-12-09 18:23 | 2011-12-09 | 2011-12-09 20:00 | Calculated | TF9C2 | TF9C2 - Transformer Fuse: TF9C2 |  | 413SEG5456-5461 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 97 | 2 | 24466 | 194 | 0.00793 | 8.1746e-05 | 15 | 1457 | 2011/2012 | December-2011 | 12 | 2011
26692 | REPLACE HV FUSE AT TX2601 - HANGATIKI EAST RD | 2011-12-11 17:11 | 2011-12-11 | 2011-12-11 18:46 | Calculated | TF2601 | TF2601 - Transformer Fuse: TF2601 |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 5 | 24466 | 470 | 0.01921 | 0.00020437 | 50 | 4709 | 2011/2012 | December-2011 | 12 | 2011
26693 | REPLACE LINK 5936 | 2011-12-11 19:24 | 2011-12-11 | 2011-12-11 20:11 | Calculated | 5936 | 5936 - Fuse Switch 5936 |  | 408SEG5936-5557 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 36 | 24466 | 1661 | 0.06789 | 0.0014714 | 161 | 7430 | 2011/2012 | December-2011 | 12 | 2011
26694 | SHIFT 154 CUBICLE AND COMMS, CONTROL WIRING ALTERATIONS AND REMOVE CB 156 EF RELAY FOR TESTING - 33/11 KV TAWHAI SUB | 2011-12-12 09:05 | 2011-12-12 | 2011-12-12 13:00 | Calculated | 442 | 442 - Fused Link 442 |  | 129SEG442-2238 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 235 | 28 | 24466 | 6589 | 0.26931 | 0.0011444 | 315 | 74129 | 2011/2012 | December-2011 | 12 | 2011
26695 | BULL VS STAY - MANGAOKEWA RD | 2011-12-12 10:52 | 2011-12-12 | 2011-12-12 14:14 | Calculated | TF733 | TF733 - Transformer Fuse: TF733 |  | No Segment | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AFAR | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 201 | 1 | 24466 | 201 | 0.00822 | 4.0873e-05 | 10 | 2012 | 2011/2012 | December-2011 | 12 | 2011
26696 | REPLCE HV FUSE AT TX 3021 - SH 3 | 2011-12-12 14:00 | 2011-12-12 | 2011-12-12 15:17 | Calculated | TF3021 | TF3021 - Transformer Fuse: TF3021 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 1 | 24466 | 76 | 0.00311 | 4.0873e-05 | 3 | 228 | 2011/2012 | December-2011 | 12 | 2011
26697 | FUSE FELL OUT - VIRATION - MAITETE/ARIA RD | 2011-12-12 21:46 | 2011-12-12 | 2011-12-12 22:31 | Calculated | TF5F4 | TF5F4 - Transformer Fuse: TF5F4 |  | No Segment | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 45 | 4 | 24466 | 180 | 0.00736 | 0.00016349 | 25 | 1129 | 2011/2012 | December-2011 | 12 | 2011
26698 | TREE BURNING AT POLE 541 - BENEYDALE FEEDER | 2011-12-13 02:08 | 2011-12-13 | 2011-12-13 13:13 | Calculated | 714 | 714 - Recloser with Bypass 714 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 664 | 66 | 24466 | 24646 | 1.0074 | 0.0026976 | 1058 | 197554 | 2011/2012 | December-2011 | 12 | 2011
26699 | FAULTY POTHEAD - BOROUGH SUB | 2011-12-13 07:17 | 2011-12-13 | 2011-12-13 08:03 | Calculated | 5955 | 5955 - Circuit Breaker Northern 5955 |  | No Segment | 508-01 Borough | Rural B | Northern | Borough Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 46 | 1241 | 24466 | 57292 | 2.3417 | 0.050723 | 7773.108 | 358858 | 2011/2012 | December-2011 | 12 | 2011
26700 | LV LINE DOWN - MADONALD RD | 2011-12-13 09:06 | 2011-12-13 | 2011-12-13 12:29 | Calculated | TF722 | TF722 - Transformer Fuse: TF722 |  | 120SEG408-465 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 203 | 3 | 24466 | 609 | 0.02489 | 0.00012262 | 15 | 3049 | 2011/2012 | December-2011 | 12 | 2011
26703 | OHURA FEEDER RENEWAL WORK - OHURA FEEDER | 2011-12-14 08:54 | 2011-12-14 | 2011-12-14 16:04 | Calculated | 5295 | 5295 - Air Break Switch 5295 |  | 413SEG5295-5454 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 407 | 33 | 24466 | 3785 | 0.1547 | 0.0013488 | 208 | 23184 | 2011/2012 | December-2011 | 12 | 2011
26704 | REPLACE FUSE LINK 668 - TURONGO ST | 2011-12-15 08:18 | 2011-12-15 | 2011-12-15 10:19 | Calculated | 668 | 668 - Fused Link 668 |  | 112SEG668-229 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 39 | 24466 | 4685 | 0.19149 | 0.001594 | 400 | 48059 | 2011/2012 | December-2011 | 12 | 2011
26705 | REPLACE HV FUSE AT TX 05I12 - ONGARUE RD | 2011-12-15 14:47 | 2011-12-15 | 2011-12-15 17:04 | Calculated | TF5I2 | TF5I2 - Transformer Fuse: TF5I2 |  | 402SEG5446-5797 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 137 | 1 | 24466 | 137 | 0.0056 | 4.0873e-05 | 10 | 1374 | 2011/2012 | December-2011 | 12 | 2011
26706 | LOWER TAP - ONGARUE RD | 2011-12-15 17:56 | 2011-12-15 | 2011-12-15 18:23 | Calculated | TF5I3 | TF5I3 - Transformer Fuse: TF5I3 |  | 402SEG5798 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 27 | 4 | 24466 | 109 | 0.00446 | 0.00016349 | 15 | 409 | 2011/2012 | December-2011 | 12 | 2011
26708 | BROKEN EARTH - MANGAKAHU RD | 2011-12-16 11:09 | 2011-12-16 | 2011-12-16 12:46 | Calculated | TF6K4 | TF6K4 - Transformer Fuse: TF6K4 |  | No Segment | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 97 | 1 | 24466 | 97 | 0.00396 | 4.0873e-05 | 10 | 972 | 2011/2012 | December-2011 | 12 | 2011
26709 | REPLACE ROTTEN HV POLE - RAVENSDOWN | 2011-12-17 09:12 | 2011-12-17 | 2011-12-17 13:34 | Calculated | 191 | 191 - Air Break Switch 191 |  | 102SEG191-361 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 257 | 3 | 24466 | 772 | 0.03155 | 0.00012262 | 1100 | 283378 | 2011/2012 | December-2011 | 12 | 2011
26710 | REPLACE HV FUSE AT TX 707 - LAKE RD | 2011-12-18 15:50 | 2011-12-18 | 2011-12-18 16:03 | Calculated | TF707 | TF707 - Transformer Fuse: TF707 |  | No Segment | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 4 | 24466 | 48 | 0.00196 | 0.00016349 | 50 | 610 | 2011/2012 | December-2011 | 12 | 2011
26711 | MAGPIE - SH 32 | 2011-12-18 17:15 | 2011-12-18 | 2011-12-18 18:24 | Calculated | TF7Q10 | TF7Q10 - Transformer Fuse: TF7Q10 |  | 426SEG5526-5359 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 68 | 3 | 24466 | 204 | 0.00834 | 0.00012262 | 15 | 1023 | 2011/2012 | December-2011 | 12 | 2011
26713 | WIND - WAITANGURU - FOR PUNGAREH | 2011-12-18 20:15 | 2011-12-18 | 2011-12-18 21:54 | Calculated | 1528 | 1528 - Fused Link 1528 |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 12 | 24466 | 1184 | 0.04839 | 0.00049048 | 58 | 5724 | 2011/2012 | December-2011 | 12 | 2011
26715 | OHURA FEEDER RENEWAL WORK - OHURA | 2011-12-19 09:00 | 2011-12-19 | 2011-12-19 15:53 | Calculated | 5295 | 5295 - Air Break Switch 5295 |  | 413SEG5295-5454 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 364 | 33 | 24466 | 3351 | 0.13697 | 0.0013488 | 208 | 20513 | 2011/2012 | December-2011 | 12 | 2011
26717 | LV WRAPPED - MAIHIIHI RD | 2011-12-19 09:34 | 2011-12-19 | 2011-12-19 14:05 | Calculated | TF1091 | TF1091 - Transformer Fuse: TF1091 |  | 111SEG360-395 | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 271 | 2 | 24466 | 543 | 0.02219 | 8.1746e-05 | 25 | 6796 | 2011/2012 | December-2011 | 12 | 2011
26716 | REPLACE RED TAGGED POLE 1031181 - BENNEYDALE | 2011-12-19 10:34 | 2011-12-19 | 2011-12-19 14:05 | Calculated | 260 | 260 - Circuit Breaker 260 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 211 | 23 | 24466 | 4857 | 0.19852 | 0.00094008 | 185.5 | 39174 | 2011/2012 | December-2011 | 12 | 2011
26720 | RECLOSER 5119 TRIPPED - GOLF RD EXTENSION | 2011-12-20 06:57 | 2011-12-20 | 2011-12-20 08:11 | Calculated | 5119 | 5119 - Recloser 5119 |  | 402SEG5118-5119RET | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 159 | 24466 | 4646 | 0.1899 | 0.0064988 | 1623.5 | 47247 | 2011/2012 | December-2011 | 12 | 2011
26722 | REPLACE POLES AND XARMS - ALSO REPLACE ABS 561 - COAST FEEDER | 2011-12-20 08:51 | 2011-12-20 | 2011-12-20 15:47 | Calculated | 281 | 281 - Air Break Switch 281 |  | 125SEG281-298 | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 72 | 24466 | 5781 | 0.23629 | 0.0029429 | 630 | 44593 | 2011/2012 | December-2011 | 12 | 2011
26721 | MAIHIIHI LINE RENEWAL PROJECT - MAIHIIHI FEEDER | 2011-12-20 09:03 | 2011-12-20 | 2011-12-20 15:22 | Calculated | 359 | 359 - Fused Link 359 |  | 111SEG359RET | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 379 | 19 | 24466 | 7203 | 0.29441 | 0.00077659 | 235 | 89096 | 2011/2012 | December-2011 | 12 | 2011
26723 | REPLACE IR POLE FOR NEW TAPE OFF - MAIHIIHI FEEDER | 2011-12-20 10:21 | 2011-12-20 | 2011-12-20 13:21 | Calculated | 374 | 374 - Fused Link 374 |  | 111SEG374-783 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 179 | 20 | 24466 | 3583 | 0.14645 | 0.00081746 | 335 | 60015 | 2011/2012 | December-2011 | 12 | 2011
26724 | LIGHTNING - HANGATIKI EAST RD | 2011-12-20 18:50 | 2011-12-20 | 2011-12-20 19:11 | Calculated | TF118 | TF118 - Transformer Fuse: TF118 |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 4 | 24466 | 84 | 0.00343 | 0.00016349 | 15 | 316 | 2011/2012 | December-2011 | 12 | 2011
26725 | LIGHTING - FAULTY TX - HANGATIKI EAST RD | 2011-12-20 19:05 | 2011-12-20 | 2011-12-20 22:28 | Calculated | TF1395 | TF1395 - Transformer Fuse: TF1395 |  | 102SEG521-505 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 203 | 3 | 24466 | 609 | 0.02489 | 0.00012262 | 15 | 3047 | 2011/2012 | December-2011 | 12 | 2011
26726 | LIGHTING - HANGATIKI EAST RD | 2011-12-20 22:41 | 2011-12-20 | 2011-12-20 23:02 | Calculated | TF2546 | TF2546 - Transformer Fuse: TF2546 |  | No Segment | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 1 | 24466 | 21 | 0.00086 | 4.0873e-05 | 10 | 211 | 2011/2012 | December-2011 | 12 | 2011
26727 | BIRD IN ARRESTOR AT TX 7I44 - GOLF RD EXTENSION | 2011-12-21 06:20 | 2011-12-21 | 2011-12-21 09:08 | Calculated | 5119 | 5119 - Recloser 5119 |  | 402SEG5118-5119RET | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 159 | 24466 | 5232 | 0.21385 | 0.0064988 | 1623.5 | 48526 | 2011/2012 | December-2011 | 12 | 2011
26728 | LIGHTNING - HANGATIKI EAST RD | 2011-12-21 08:00 | 2011-12-21 | 2011-12-21 08:30 | Calculated | TF118 | TF118 - Transformer Fuse: TF118 |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 4 | 24466 | 116 | 0.00474 | 0.00016349 | 15 | 437 | 2011/2012 | December-2011 | 12 | 2011
26729 | CHANGE TX 7R14 TO RTE TYPE AND INSTALL MAGNAFIX AT TX 8R 15 | 2011-12-21 08:08 | 2011-12-21 | 2011-12-21 20:09 | Calculated | 5226 | 5226 - Air Break Switch 5226 |  | 426SEG5226RET | Waihaha 426-02 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 713 | 111 | 24466 | 78078 | 3.1913 | 0.0045369 | 600 | 420813 | 2011/2012 | December-2011 | 12 | 2011
26731 | REPLACE POLES AND XARMS - ALSO REPLACE ABS 561 | 2011-12-21 08:50 | 2011-12-21 | 2011-12-21 15:44 | Calculated | 281 | 281 - Air Break Switch 281 |  | 125SEG281-298 | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 385 | 72 | 24466 | 6745 | 0.27569 | 0.0029429 | 630 | 50292 | 2011/2012 | December-2011 | 12 | 2011
26730 | MAIHIIHI LINE RENEWAL PROJECT - MAIHIIHI FEEDER | 2011-12-21 09:10 | 2011-12-21 | 2011-12-21 15:24 | Calculated | 579 | 579 - Fused Link 579 |  | 111SEG579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 373 | 10 | 24466 | 3731 | 0.1525 | 0.00040873 | 95 | 35452 | 2011/2012 | December-2011 | 12 | 2011
26732 | REPLACE POLES AND XARMS - ALSO INSTALL NEW LINKS | 2011-12-21 09:50 | 2011-12-21 | 2011-12-21 15:47 | Calculated | 5721 | 5721 - Air Break Switch 5721 |  | 416SEG5721-5684 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 356 | 66 | 24466 | 23505 | 0.96072 | 0.0026976 | 632.5 | 225264 | 2011/2012 | December-2011 | 12 | 2011
26733 | LIGHTNING - TAHAIA RD | 2011-12-21 21:10 | 2011-12-21 | 2011-12-21 21:44 | Calculated | TF385 | TF385 - Transformer Fuse: TF385 |  | No Segment | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 2 | 24466 | 68 | 0.00278 | 8.1746e-05 | 25 | 852 | 2011/2012 | December-2011 | 12 | 2011
26734 | REPLACE POLES AND XARMS - ALSO REPLACE ABS 561 - COAST FEEDER | 2011-12-22 09:34 | 2011-12-22 | 2011-12-22 13:10 | Calculated | 561 | 561 - Air Break Switch 561 |  | 125SEG561-1758 | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 215 | 17 | 24466 | 3658 | 0.14951 | 0.00069484 | 115 | 24751 | 2011/2012 | December-2011 | 12 | 2011
26735 | FAULTY INSULATOR - MAIN RD - PAST TUNANUI RD | 2011-12-22 10:02 | 2011-12-22 | 2011-12-22 11:33 | Calculated | 5311 | 5311 - Air Break Switch 5311 |  | 409SEG5311-5452 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 96 | 24466 | 8788 | 0.35919 | 0.0039238 | 429 | 39274 | 2011/2012 | December-2011 | 12 | 2011
26736 | FAULTY TX 385 - TAHAIA RD | 2011-12-22 10:04 | 2011-12-22 | 2011-12-22 15:25 | Calculated | TF385 | TF385 - Transformer Fuse: TF385 |  | No Segment | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation | Transformers : Other | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 2 | 24466 | 279 | 0.0114 | 8.1746e-05 | 25 | 3487 | 2011/2012 | December-2011 | 12 | 2011
26738 | FUSE PULLED APART AT TX 2295 - HUIRUMU RD | 2011-12-22 10:16 | 2011-12-22 | 2011-12-22 11:12 | Calculated | TF2295 | TF2295 - Transformer Fuse: TF2295 |  | No Segment | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 3 | 24466 | 168 | 0.00687 | 0.00012262 | 15 | 841 | 2011/2012 | December-2011 | 12 | 2011
26737 | LV FAULT - SH 32 | 2011-12-22 10:51 | 2011-12-22 | 2011-12-22 15:02 | Calculated | TF4P3 | TF4P3 - Transformer Fuse: TF4P3 |  | 426SEG5333-5532 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 251 | 5 | 24466 | 1255 | 0.0513 | 0.00020437 | 15 | 3767 | 2011/2012 | December-2011 | 12 | 2011
26740 | REPLACE HV FUSE AT TX 2471 - PARITANIWHA RD | 2011-12-24 14:20 | 2011-12-24 | 2011-12-24 16:11 | Calculated | TF2471 | TF2471 - Transformer Fuse: TF2471 |  | No Segment | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 3 | 24466 | 333 | 0.01361 | 0.00012262 | 25 | 2780 | 2011/2012 | December-2011 | 12 | 2011
26741 | REPLACE HV FUSE AT TX 6Q5 - SH 32 | 2011-12-25 10:35 | 2011-12-25 | 2011-12-25 13:04 | Calculated | TF6Q5 | TF6Q5 - Transformer Fuse: TF6Q5 |  | No Segment | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 149 | 2 | 24466 | 298 | 0.01218 | 8.1746e-05 | 15 | 2238 | 2011/2012 | December-2011 | 12 | 2011
26742 | REPLACE HV FUSE AT TX 2698 - KAWAKAWA RD | 2011-12-25 12:31 | 2011-12-25 | 2011-12-25 14:44 | Calculated | TF2698 | TF2698 - Transformer Fuse: TF2698 |  | 123SEG468 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 3 | 24466 | 399 | 0.01631 | 0.00012262 | 15 | 1998 | 2011/2012 | December-2011 | 12 | 2011
26743 | RECLOSER 1717 TRIPPED - MOKAUITI RD E/W SUB | 2011-12-25 16:26 | 2011-12-25 | 2011-12-25 17:45 | Calculated | 1717 | 1717 - Recloser with Bypass 1717 |  | 115SEG1717-1723 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 79 | 22 | 24466 | 1741 | 0.07116 | 0.00089921 | 165.5 | 13099 | 2011/2012 | December-2011 | 12 | 2011
26744 | JUMPER OFF AT TX 3075 - MURPHY RD | 2011-12-26 19:51 | 2011-12-26 | 2011-12-26 20:33 | Calculated | 1331 | 1331 - Fused Link 1331 |  | 103SEG1331 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 4 | 24466 | 168 | 0.00687 | 0.00016349 | 45 | 1896 | 2011/2012 | December-2011 | 12 | 2011
26745 | REPLACE HV FUSE AT TX 1393 - HANGATIKI EAST RD | 2011-12-27 09:01 | 2011-12-27 | 2011-12-27 09:26 | Calculated | TF1393 | TF1393 - Transformer Fuse: TF1393 |  | 102SEG521-505 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 1 | 24466 | 25 | 0.00102 | 4.0873e-05 | 5 | 125 | 2011/2012 | December-2011 | 12 | 2011
26748 | LV LINE DOWN - RANGIATEA RD | 2011-12-28 15:58 | 2011-12-28 | 2011-12-28 17:03 | Calculated | TF345 | TF345 - Transformer Fuse: TF345 |  | No Segment | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 7 | 24466 | 456 | 0.01864 | 0.00028611 | 30 | 1954 | 2011/2012 | December-2011 | 12 | 2011
26747 | LIGHTNING - MANGANUI RD | 2011-12-28 22:25 | 2011-12-28 | 2011-12-29 08:54 | Calculated | TF2616 | TF2616 - Transformer Fuse: TF2616 |  | 128SEG1610-1611 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 628 | 1 | 24466 | 628 | 0.02567 | 4.0873e-05 | 10 | 6281 | 2011/2012 | December-2011 | 12 | 2011
26749 | OVER CURRENT - TAHAROA A | 2011-12-29 01:00 | 2011-12-29 | 2011-12-29 01:10 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24466 |  | 0 | 0 |  |  | 2011/2012 | December-2011 | 12 | 2011
26752 | INSTALL NEW PTF AND SHIFT EXISTING POLE 24 | 2011-12-29 09:35 | 2011-12-29 | 2011-12-29 14:35 | Calculated | 2061 | 2061 - Fused Link 2061 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 300 | 2 | 24466 | 600 | 0.02452 | 8.1746e-05 | 45 | 13510 | 2011/2012 | December-2011 | 12 | 2011
26753 | SCHEDULED MAINTENANCE - TE KUMI RD | 2011-12-29 10:08 | 2011-12-29 | 2011-12-29 16:02 | Calculated | TF2763 | TF2763 - Transformer Fuse: TF2763 |  | 107SEG221-299 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 354 | 1 | 24466 | 354 | 0.01447 | 4.0873e-05 | 200 | 70863 | 2011/2012 | December-2011 | 12 | 2011
26754 | UPGRADE TX - KARANGAHAPE RD | 2011-12-29 10:12 | 2011-12-29 | 2011-12-29 11:54 | Calculated | TF7R19 | TF7R19 - Transformer Fuse: TF7R19 |  | No Segment | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 101 | 1 | 24466 | 101 | 0.00413 | 4.0873e-05 | 15 | 1517 | 2011/2012 | December-2011 | 12 | 2011
26755 | JUMPER OFF POLE 59 - BORCK'S RD - FOR OPOTIKI RD | 2011-12-29 22:21 | 2011-12-29 | 2011-12-29 22:50 | Calculated | 5339 | 5339 - Fused Link 5339 |  | 402SEG5339 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 10 | 24466 | 291 | 0.01189 | 0.00040873 | 75 | 2186 | 2011/2012 | December-2011 | 12 | 2011
26759 | BIRD - POLE 47/31 - MATIERE SUB | 2011-12-31 08:11 | 2011-12-31 | 2011-12-31 10:04 | Calculated | 5107 | 5107 - Recloser with Bypass & Links 5107 |  | 422SEG05F14-5107 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 113 | 64 | 24466 | 7244 | 0.29608 | 0.0026159 | 454 | 51392 | 2011/2012 | December-2011 | 12 | 2011
26760 | LV CLASH - TX 14N2 - SH 47 | 2011-12-31 12:43 | 2011-12-31 | 2011-12-31 14:02 | Calculated | TF14N02 | TF14N02 - Transformer Fuse: TF14N02 |  | 609SEG5787-6007 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 2 | 24466 | 158 | 0.00646 | 8.1746e-05 | 15 | 1189 | 2011/2012 | December-2011 | 12 | 2011
26761 | OCB 5992 TRIPPED - BOROUGH SUB | 2012-01-01 06:26 | 2012-01-01 | 2012-01-01 06:34 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 1230 | 24471 | 10086 | 0.41216 | 0.050264 | 9011.4251 | 73893 | 2011/2012 | January-2012 | 1 | 2012
26762 | BLOWN HV FUSE AT TX 10K13 - OWHANGO RD | 2012-01-01 06:57 | 2012-01-01 | 2012-01-01 07:31 | Calculated | TF10K13 | TF10K13 - Transformer Fuse: TF10K13 |  | 409SEG5135-5136 | Southern 409-04 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 31 | 24471 | 1058 | 0.04323 | 0.0012668 | 200 | 6826 | 2011/2012 | January-2012 | 1 | 2012
26763 | LINE DOWN - OHURA FEEDER | 2012-01-01 10:49 | 2012-01-01 | 2012-01-01 15:30 | Calculated | 5417 | 5417 - Recloser 5417 |  | 413SEG5418-5417 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 262 | 61 | 24471 | 8915 | 0.36431 | 0.0024927 | 413 | 61042 | 2011/2012 | January-2012 | 1 | 2012
26769 | LIGHTNING - HV FUSE AT TX 2860 BLOWN - RANGITOTO RD | 2012-01-01 13:05 | 2012-01-01 | 2012-01-01 13:38 | Calculated | TF2860 | TF2860 - Transformer Fuse: TF2860 |  | No Segment | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 1 | 24471 | 33 | 0.00135 | 4.0865e-05 | 15 | 498 | 2011/2012 | January-2012 | 1 | 2012
26770 | LIGHTNING - HV FUSE AT TX 1136 BLOWN - RANGITOTO RD | 2012-01-01 13:05 | 2012-01-01 | 2012-01-01 14:30 | Calculated | TF1136 | TF1136 - Transformer Fuse: TF1136 |  | 106SEG112-REG30 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 3 | 24471 | 255 | 0.01042 | 0.00012259 | 15 | 1278 | 2011/2012 | January-2012 | 1 | 2012
26771 | LIGHTNING - HV FUSE AT TX 23N4 BLOWN - NGAMOKAI RD | 2012-01-01 14:20 | 2012-01-01 | 2012-01-01 14:57 | Calculated | TF23N4 | TF23N4 - Transformer Fuse: TF23N4 |  | 416SEG5716 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 5 | 24471 | 186 | 0.0076 | 0.00020432 | 30 | 1116 | 2011/2012 | January-2012 | 1 | 2012
26772 | LIGHTNING - HV FUSE AT TX 8J25 BLOWN - MARSACK RD | 2012-01-01 15:10 | 2012-01-01 | 2012-01-01 15:40 | Calculated | TF8J25 | TF8J25 - Transformer Fuse: TF8J25 |  | 404SEG5915-5838 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 4 | 24471 | 120 | 0.0049 | 0.00016346 | 30 | 906 | 2011/2012 | January-2012 | 1 | 2012
26774 | LIGHTNING - HV FUSE AT TX 4Q4 BLOWN - WAIHAHA RD | 2012-01-01 15:25 | 2012-01-01 | 2012-01-01 16:36 | Calculated | TF4Q4 | TF4Q4 - Transformer Fuse: TF4Q4 |  | No Segment | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 71 | 4 | 24471 | 284 | 0.01161 | 0.00016346 | 15 | 1068 | 2011/2012 | January-2012 | 1 | 2012
26780 | LIGHTNING - HV FUSE AT TX 2850 BLOWN - MANGATUTU RD | 2012-01-01 15:30 | 2012-01-01 | 2012-01-01 20:00 | Calculated | TF2850 | TF2850 - Transformer Fuse: TF2850 |  | No Segment | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 270 | 2 | 24471 | 540 | 0.02207 | 8.1729e-05 | 50 | 13510 | 2011/2012 | January-2012 | 1 | 2012
26776 | LIGHTNING - HV FUSE AT TX 306 BLOWN - BAYLEY RD | 2012-01-01 15:47 | 2012-01-01 | 2012-01-01 17:20 | Calculated | TF306 | TF306 - Transformer Fuse: TF306 |  | 122SEG366-398 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 4 | 24471 | 372 | 0.0152 | 0.00016346 | 30 | 2796 | 2011/2012 | January-2012 | 1 | 2012
26773 | LIGHTNING - MAIHIIHI RD - BY SCHOOL | 2012-01-01 16:06 | 2012-01-01 | 2012-01-01 16:14 | Calculated | 117 | 117 - Circuit Breaker 117 |  | 111SEG647-117RET | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 228 | 24471 | 1873 | 0.07654 | 0.0093172 | 2261.25 | 18579 | 2011/2012 | January-2012 | 1 | 2012
26777 | LIGHTNING - HV FUSE AT TX 7K12 BLOWN - ECHOLANDS RD | 2012-01-01 16:10 | 2012-01-01 | 2012-01-01 17:03 | Calculated | TF7K12 | TF7K12 - Transformer Fuse: TF7K12 |  | No Segment | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 3 | 24471 | 159 | 0.0065 | 0.00012259 | 11.25 | 598 | 2011/2012 | January-2012 | 1 | 2012
26775 | LIGHTNING - HV FUSE AT TX 8Q4 BLOWN - SH 41 KURATAU | 2012-01-01 16:15 | 2012-01-01 | 2012-01-01 16:58 | Calculated | TF8Q4 | TF8Q4 - Transformer Fuse: TF8Q4 |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 43 | 1 | 24471 | 43 | 0.00176 | 4.0865e-05 | 5 | 216 | 2011/2012 | January-2012 | 1 | 2012
26779 | LIGHTNING - HV FUSE AT TX 133 BLOWN - RANGITOTO RD | 2012-01-01 16:55 | 2012-01-01 | 2012-01-01 17:17 | Calculated | TF133 | TF133 - Transformer Fuse: TF133 |  | 106SEG112-REG30 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 3 | 24471 | 66 | 0.0027 | 0.00012259 | 25 | 555 | 2011/2012 | January-2012 | 1 | 2012
26778 | LIGHTNING - HV FUSE AT TX 8K23 BLOWN - BODY RD | 2012-01-01 18:25 | 2012-01-01 | 2012-01-01 18:51 | Calculated | TF8K23 | TF8K23 - Transformer Fuse: TF8K23 |  | No Segment | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 26 | 2 | 24471 | 52 | 0.00212 | 8.1729e-05 | 15 | 393 | 2011/2012 | January-2012 | 1 | 2012
26781 | LIGHTNING - HV FUSE AT TX 372 BLOWN - WALL RD | 2012-01-01 20:55 | 2012-01-01 | 2012-01-01 22:00 | Calculated | TF372 | TF372 - Transformer Fuse: TF372 |  | No Segment | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 3 | 24471 | 195 | 0.00797 | 0.00012259 | 5 | 326 | 2011/2012 | January-2012 | 1 | 2012
26782 | LIGHTNING - HV FUSE AT TX 419 BLOWN - DUNCAN RD | 2012-01-01 21:50 | 2012-01-01 | 2012-01-01 23:10 | Calculated | TF419 | TF419 - Transformer Fuse: TF419 |  | No Segment | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 2 | 24471 | 160 | 0.00654 | 8.1729e-05 | 25 | 2005 | 2011/2012 | January-2012 | 1 | 2012
26787 | LIGHTNING - MANGAOTAKI RD - BY JACKSONS | 2012-01-02 07:00 | 2012-01-02 | 2012-01-02 08:52 | Calculated | 1516 | 1516 - Air Break Switch 1516 |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 138 | 24471 | 15476 | 0.63242 | 0.0056393 | 885.5 | 99308 | 2011/2012 | January-2012 | 1 | 2012
26786 | LIGHTNING - CHANGE FAULTY TX 1444 - WHAREPUHUNGA RD | 2012-01-02 08:20 | 2012-01-02 | 2012-01-02 10:10 | Calculated | TF1444 | TF1444 - Transformer Fuse: TF1444 |  | 111SEG395-549 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 4 | 24471 | 440 | 0.01798 | 0.00016346 | 15 | 1651 | 2011/2012 | January-2012 | 1 | 2012
26788 | LIGHTNING - HV FUSE AT TX 1103 BLOWN - WAIHORA RD | 2012-01-02 10:16 | 2012-01-02 | 2012-01-02 11:16 | Calculated | TF1103 | TF1103 - Transformer Fuse: TF1103 |  | 123SEG806-493 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 2 | 24471 | 120 | 0.0049 | 8.1729e-05 | 15 | 901 | 2011/2012 | January-2012 | 1 | 2012
26789 | LIGHTNING - HV FUSE AT TX 301 BLOWN - DUNCAN RD | 2012-01-02 11:31 | 2012-01-02 | 2012-01-02 12:26 | Calculated | TF301 | TF301 - Transformer Fuse: TF301 |  | No Segment | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 2 | 24471 | 110 | 0.0045 | 8.1729e-05 | 10 | 551 | 2011/2012 | January-2012 | 1 | 2012
26790 | LIGHTNING - HV FUSE AT TX 372 BLOWN - WALL RD | 2012-01-02 12:26 | 2012-01-02 | 2012-01-02 13:11 | Calculated | TF372 | TF372 - Transformer Fuse: TF372 |  | No Segment | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 3 | 24471 | 120 | 0.0049 | 0.00012259 | 5 | 200 | 2011/2012 | January-2012 | 1 | 2012
26792 | OCB 2092 TRIPPED - MARAETAI SUBSTATION | 2012-01-02 14:00 | 2012-01-02 | 2012-01-02 14:06 | Calculated | 2092 | 2092 - Circuit Breaker Maraetai 11 kV 2092 |  | No Segment | 210-01 Maraetai | Rural D | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 166 | 24471 | 1015 | 0.04148 | 0.0067835 | 3163 | 19347 | 2011/2012 | January-2012 | 1 | 2012
26791 | LIGHTNING - HV FUSE AT TX 14N2 BLOWN - WSH 47 | 2012-01-02 14:26 | 2012-01-02 | 2012-01-02 15:35 | Calculated | TF14N02 | TF14N02 - Transformer Fuse: TF14N02 |  | 609SEG5787-6007 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 2 | 24471 | 138 | 0.00564 | 8.1729e-05 | 15 | 1036 | 2011/2012 | January-2012 | 1 | 2012
26793 | REPLACE HV FUSE AT TX 2819 - HENDERSON RD | 2012-01-04 06:31 | 2012-01-04 | 2012-01-04 07:18 | Calculated | TF2819 | TF2819 - Transformer Fuse: TF2819 |  | 120SEG416-479 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 1 | 24471 | 47 | 0.00192 | 4.0865e-05 | 10 | 471 | 2011/2012 | January-2012 | 1 | 2012
26794 | FAULTY DDO - SH 4 | 2012-01-04 08:01 | 2012-01-04 | 2012-01-04 11:10 | Calculated | 5436 | 5436 - Fused Link 5436 |  | 421SEG5436-5434 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation | Switchgear : Fuse Carriers | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 189 | 41 | 24471 | 2804 | 0.11458 | 0.0016755 | 255.5 | 16848 | 2011/2012 | January-2012 | 1 | 2012
26795 | FUSE PULLED APART AT TX 14L8 - SH 4 | 2012-01-04 10:31 | 2012-01-04 | 2012-01-04 11:23 | Calculated | TF14L08 | TF14L08 - Transformer Fuse: TF14L08 |  | 410SEG6766-5141 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation | Switchgear : Auxiliary Fuses / Carriers | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 3 | 24471 | 156 | 0.00637 | 0.00012259 | 7.5 | 391 | 2011/2012 | January-2012 | 1 | 2012
26796 | LINE DOWN - TE MAPARA FEEDER | 2012-01-05 04:12 | 2012-01-05 | 2012-01-05 16:06 | Calculated | 687 | 687 - Circuit Breaker 687 |  | 117SEG687-1289 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 500 | 235 | 24471 | 27396 | 1.1195 | 0.0096032 | 1870 | 220419 | 2011/2012 | January-2012 | 1 | 2012
26798 | REPLACE HV FUSE AT TX 14M5 - SH 47 | 2012-01-05 08:01 | 2012-01-05 | 2012-01-05 11:21 | Calculated | TF14M05 | TF14M05 - Transformer Fuse: TF14M05 |  | 609SEG5787-6007 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 200 | 1 | 24471 | 200 | 0.00817 | 4.0865e-05 | 15 | 3003 | 2011/2012 | January-2012 | 1 | 2012
26797 | REPLACING POLES AND XARMS - MOKAU | 2012-01-05 09:38 | 2012-01-05 | 2012-01-05 15:44 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 366 | 27 | 24471 | 9886 | 0.40399 | 0.0011033 | 165 | 60420 | 2011/2012 | January-2012 | 1 | 2012
26799 | REPLACE HV FUSE AT TX 4J11 - MANGAKAHU VALLEY | 2012-01-05 12:00 | 2012-01-05 | 2012-01-05 14:36 | Calculated | TF4J11 | TF4J11 - Transformer Fuse: TF4J11 |  | No Segment | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 156 | 1 | 24471 | 156 | 0.00637 | 4.0865e-05 | 10 | 1561 | 2011/2012 | January-2012 | 1 | 2012
26800 | BROKEN XARM AT 1673 - KURATAHI STREET | 2012-01-05 15:34 | 2012-01-05 | 2012-01-05 20:07 | Calculated | 655 | 655 - Fused Link 655 |  | 116SEG655 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation | Transformers : Supports / Structures / Foundations | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 273 | 2 | 24471 | 546 | 0.02231 | 8.1729e-05 | 65 | 17754 | 2011/2012 | January-2012 | 1 | 2012
26811 | LINE DOWN - GRAVEL SCOOP FEEDER | 2012-01-06 07:07 | 2012-01-06 | 2012-01-06 09:48 | Calculated | 334 | 334 - Circuit Breaker with Bypass & Links 334 |  | 109SEG303-334 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 220 | 24471 | 9545 | 0.39005 | 0.0089902 | 1895 | 69652 | 2011/2012 | January-2012 | 1 | 2012
26814 | REPLACE POLES AND XARMS - MOKAU FEEDER | 2012-01-06 09:37 | 2012-01-06 | 2012-01-06 15:17 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 340 | 27 | 24471 | 9189 | 0.37551 | 0.0011033 | 165 | 56160 | 2011/2012 | January-2012 | 1 | 2012
26816 | POLE LEANING OVER IN RIVER - PARAHEKA SUB - LOOP RD | 2012-01-06 12:09 | 2012-01-06 | 2012-01-06 14:19 | Calculated | 1125 | 1125 - Fused Link 1125 |  | 114SEG1125-2160 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOL1 | Pole Leaning | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 16 | 24471 | 2082 | 0.08508 | 0.00065384 | 108 | 14056 | 2011/2012 | January-2012 | 1 | 2012
26817 | BALL VS LINES - TUKU ST | 2012-01-06 21:20 | 2012-01-06 | 2012-01-06 22:32 | Calculated | TF1B25 | TF1B25 - Transformer Fuse: TF1B25 |  | 404SEGF1.16 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 35 | 24471 | 2525 | 0.10318 | 0.0014303 | 100 | 7214 | 2011/2012 | January-2012 | 1 | 2012
26818 | SECT 591 TRIPPED - TREES - BY TE ROTO SCHOOL | 2012-01-07 11:12 | 2012-01-07 | 2012-01-07 12:23 | Calculated | 5591 | 5591 - Sectionaliser with Bypass & Links 5591 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 70 | 52 | 24471 | 3652 | 0.14924 | 0.002125 | 198 | 13906 | 2011/2012 | January-2012 | 1 | 2012
26819 | BROKEN DDO AT TX 8J47 - TRANSPOWER LOCAL SERVICE | 2012-01-07 17:42 | 2012-01-07 | 2012-01-07 19:58 | Calculated | TF8J47 | TF8J47 - Transformer Fuse: TF8J47 |  | 408SEG5129-5882 | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation | Switchgear : Fuse Carriers | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 93 | 24471 | 9410 | 0.38454 | 0.0038004 | 675 | 68298 | 2011/2012 | January-2012 | 1 | 2012
26823 | VCB 682 TRIPPED - WAIRERE FALLS | 2012-01-08 06:14 | 2012-01-08 | 2012-01-08 06:23 | Calculated | 682 | 682 - Circuit Breaker 682 |  | No Segment | 207-01 Wairere Falls | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 184 | 24471 |  | 0 | 0.0075191 | 1525.5 |  | 2011/2012 | January-2012 | 1 | 2012
26824 | TREE ON LINE - RAURIMU FEEDER | 2012-01-08 10:50 | 2012-01-08 | 2012-01-08 15:59 | Calculated | 5494 | 5494 - Recloser with Bypass 5494 |  | 410SEG5494-5493 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 241 | 43 | 24471 | 6405 | 0.26174 | 0.0017572 | 273.3333 | 39983 | 2011/2012 | January-2012 | 1 | 2012
26825 | TREE ON LINE - OTUKOU FEEDER | 2012-01-08 11:38 | 2012-01-08 | 2012-01-08 17:10 | Calculated | 5584 | 5584 - Recloser with Bypass & Links 5584 |  | 418SEG5584-5591 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 332 | 74 | 24471 | 8883 | 0.363 | 0.003024 | 346 | 48817 | 2011/2012 | January-2012 | 1 | 2012
26826 | SECTIONALISER 5278 OPERATED - FAUCHELLE RD | 2012-01-09 08:14 | 2012-01-09 | 2012-01-09 11:01 | Calculated | 5278 | 5278 - Sectionaliser with Bypass & Links 5278 |  | 422SEG5278-5307 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 167 | 20 | 24471 | 3343 | 0.13661 | 0.00081729 | 141 | 23568 | 2011/2012 | January-2012 | 1 | 2012
26827 | REPLACE HV FUSE LINK 1263 - TANGITU RD | 2012-01-09 14:01 | 2012-01-09 | 2012-01-09 16:32 | Calculated | 1263 | 1263 - Sectionaliser with Incoming Link 1263 |  | 115SEG1356-1725 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 150 | 1 | 24471 | 150 | 0.00613 | 4.0865e-05 | 15 | 2252 | 2011/2012 | January-2012 | 1 | 2012
26828 | BROKEN DDO AT TX 372 - WALL RD | 2012-01-09 20:20 | 2012-01-09 | 2012-01-09 21:24 | Calculated | TF372 | TF372 - Transformer Fuse: TF372 |  | No Segment | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 3 | 24471 | 192 | 0.00785 | 0.00012259 | 5 | 320 | 2011/2012 | January-2012 | 1 | 2012
26829 | MAGPIE - WAIKAKA RD | 2012-01-10 08:23 | 2012-01-10 | 2012-01-10 12:38 | Calculated | TF6E18 | TF6E18 - Transformer Fuse: TF6E18 |  | No Segment | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 254 | 1 | 24471 | 254 | 0.01038 | 4.0865e-05 | 15 | 3813 | 2011/2012 | January-2012 | 1 | 2012
26830 | BROKEN STAY WIRE - TURAKINA VALLEY RD | 2012-01-10 08:58 | 2012-01-10 | 2012-01-10 12:06 | Calculated | TF22O4 | TF22O4 - Transformer Fuse: TF22O4 |  | 416SEG5555 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Pole | FAIL:FPOL2:FPOL1 | Pole Leaning | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 188 | 1 | 24471 | 188 | 0.00768 | 4.0865e-05 | 15 | 2824 | 2011/2012 | January-2012 | 1 | 2012
26831 | REPLACE FAULTY LA - TIHOI RD | 2012-01-10 11:05 | 2012-01-10 | 2012-01-10 12:06 | Calculated | TF743 | TF743 - Transformer Fuse: TF743 |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 61 | 2 | 24471 | 122 | 0.00499 | 8.1729e-05 | 25 | 1531 | 2011/2012 | January-2012 | 1 | 2012
26832 | BROKEN XARM AT POLE 19 - PIOPIO FEEDER | 2012-01-10 15:58 | 2012-01-10 | 2012-01-10 18:19 | Calculated | 683 | 683 - Circuit Breaker 683 |  | No Segment | 207-01 Wairere Falls | Rural D | Piopio | Wairere Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 477 | 24471 |  | 0 | 0.019492 | 3051 |  | 2011/2012 | January-2012 | 1 | 2012
26834 | REPLACE POLE - LINK 5716 - TANGIWAI FEEDER | 2012-01-11 10:35 | 2012-01-11 | 2012-01-11 12:54 | Calculated | 5685 | 5685 - Fused Link 5685 |  | 416SEG5685-5716 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 138 | 19 | 24471 | 2625 | 0.10727 | 0.00077643 | 135 | 18652 | 2011/2012 | January-2012 | 1 | 2012
26835 | REPLACE HV FUSE AT TX 21K03 - LAKES RD | 2012-01-11 16:04 | 2012-01-11 | 2012-01-11 17:27 | Calculated | TF21K3 | TF21K3 - Transformer Fuse: TF21K3 |  | 416SEG5730-5676 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 2 | 24471 | 166 | 0.00678 | 8.1729e-05 | 15 | 1247 | 2011/2012 | January-2012 | 1 | 2012
26836 | FUSE PULLED APART - KURURAU RD | 2012-01-11 21:16 | 2012-01-11 | 2012-01-11 23:00 | Calculated | TF8F5 | TF8F5 - Transformer Fuse: TF8F5 |  | No Segment | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 104 | 2 | 24471 | 208 | 0.0085 | 8.1729e-05 | 25 | 2604 | 2011/2012 | January-2012 | 1 | 2012
26838 | POLE OVER - SH 4 PUKETUTU SPUR | 2012-01-12 10:28 | 2012-01-12 | 2012-01-12 10:53 | Calculated | 1322 | 1322 - Sectionaliser 1322 |  | 117SEG1322 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOL1 | Pole Leaning | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 27 | 24471 | 678 | 0.02771 | 0.0011033 | 161 | 4046 | 2011/2012 | January-2012 | 1 | 2012
26839 | BROKEN X/ARM AT POLE 105 - WHAKAMARU | 2012-01-13 03:14 | 2012-01-13 | 2012-01-13 14:53 | Calculated | 1022 | 1022 - Circuit Breaker 1022, 33 kV |  | No Segment | 214-01 Whakamaru | Rural D | No Feeder |  | OH Lines : Crossarm - Wood | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 24 | 2605 | 24471 | 50294 | 2.0553 | 0.10645 | 24138.2578 | 477260 | 2011/2012 | January-2012 | 1 | 2012
26844 | LIGHTNING - MANGAKAHU RD | 2012-01-13 07:00 | 2012-01-13 | 2012-01-13 08:13 | Calculated | 5108 | 5108 - Sectionaliser with Bypass 5108 |  | 402SEG5115-5108 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 73 | 21 | 24471 | 1538 | 0.06285 | 0.00085816 | 145 | 10623 | 2011/2012 | January-2012 | 1 | 2012
26845 | LIGHTNING - ONGARUE STREAM RD | 2012-01-13 07:16 | 2012-01-13 | 2012-01-13 10:06 | Calculated | TF1M4 | TF1M4 - Transformer Fuse: TF1M4 |  | No Segment | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 170 | 1 | 24471 | 170 | 0.00695 | 4.0865e-05 | 10 | 1702 | 2011/2012 | January-2012 | 1 | 2012
26846 | JUMPER OFF AT TX 143 - BARBERS RD | 2012-01-13 08:15 | 2012-01-13 | 2012-01-13 08:41 | Calculated | TF143 | TF143 - Transformer Fuse: TF143 |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 2 | 24471 | 52 | 0.00212 | 8.1729e-05 | 30 | 786 | 2011/2012 | January-2012 | 1 | 2012
26847 | LIGHTNING - MANGAITI RD | 2012-01-13 08:30 | 2012-01-13 | 2012-01-13 10:33 | Calculated | TF2244 | TF2244 - Transformer Fuse: TF2244 |  | 117SEG1721-1307 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 123 | 2 | 24471 | 246 | 0.01005 | 8.1729e-05 | 10 | 1232 | 2011/2012 | January-2012 | 1 | 2012
26848 | LIGHTNING - ONGARUE STREAM RD | 2012-01-13 10:01 | 2012-01-13 | 2012-01-13 13:49 | Calculated | TF1M1 | TF1M1 - Transformer Fuse: TF1M1 |  | No Segment | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 228 | 1 | 24471 | 228 | 0.00932 | 4.0865e-05 | 7.5 | 1711 | 2011/2012 | January-2012 | 1 | 2012
26849 | REPLACE KNACKERED STUCTURE - TX 5I3 - NORTHERN FEEDER | 2012-01-13 10:19 | 2012-01-13 | 2012-01-13 14:10 | Calculated | 5798 | 5798 - Fused Link 5798 |  | 402SEG5798 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 231 | 11 | 24471 | 2542 | 0.10388 | 0.00044951 | 55 | 12712 | 2011/2012 | January-2012 | 1 | 2012
26850 | WIND - SH 41 | 2012-01-13 14:18 | 2012-01-13 | 2012-01-13 16:03 | Calculated | TF09P02 | TF09P02 - Transformer Fuse: TF09P02 |  | 609SEG5839-5163 | National Park / Kuratau 609-01 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 105 | 1 | 24471 | 105 | 0.00429 | 4.0865e-05 | 100 | 10518 | 2011/2012 | January-2012 | 1 | 2012
26851 | FAULTY LA AT TX 1B7 - ECHOLANDS RD - WATER TREATMENT | 2012-01-13 14:46 | 2012-01-13 | 2012-01-13 17:36 | Calculated | 1.27 | 1.27 - Fused Link 1.27 |  | 404SEGF1.27 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 6 | 24471 | 1020 | 0.04168 | 0.00024519 | 25 | 4253 | 2011/2012 | January-2012 | 1 | 2012
26852 | WIND LV CLASH - TE KUMI RD | 2012-01-13 15:15 | 2012-01-13 | 2012-01-13 15:52 | Calculated | TF1489 | TF1489 - Transformer Fuse: TF1489 |  | 107SEG388-295 | Oparure 107-03 | Rural C | Oparure | Gadsby Road Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 7 | 24471 | 260 | 0.01062 | 0.00028605 | 25 | 928 | 2011/2012 | January-2012 | 1 | 2012
26853 | FUSE PULLED APART - OIO NO 1 RD | 2012-01-14 07:31 | 2012-01-14 | 2012-01-14 10:00 | Calculated | TF12H05 | TF12H05 - Transformer Fuse: TF12H05 |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation | Miscellaneous : Meter Wiring / Fuses | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 149 | 1 | 24471 | 149 | 0.00609 | 4.0865e-05 | 15 | 2237 | 2011/2012 | January-2012 | 1 | 2012
26854 | HV FUSE BLOWN AT TX 13H02 - KOUTUROA RD | 2012-01-16 09:30 | 2012-01-16 | 2012-01-16 11:22 | Calculated | TF13H02 | TF13H02 - Transformer Fuse: TF13H02 |  | 410SEG5597-5396 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 112 | 4 | 24471 | 448 | 0.01831 | 0.00016346 | 15 | 1682 | 2011/2012 | January-2012 | 1 | 2012
26855 | JUMPER OFF AT TX 1892 - NGATARAWA RD | 2012-01-16 10:09 | 2012-01-16 | 2012-01-16 11:22 | Calculated | 1100 | 1100 - Sectionaliser with Incoming Link 1100 |  | 114SEG1128 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 73 | 13 | 24471 | 950 | 0.03882 | 0.00053124 | 90 | 6580 | 2011/2012 | January-2012 | 1 | 2012
26856 | INSTALL PTFS AT POLES 33/39/10 AND 11 - LAKE TAUPO - 33KV AND AWAMATE - 11KV | 2012-01-16 10:25 | 2012-01-16 | 2012-01-16 14:14 | Calculated | 6626 | 6626 - Solid Link 6626 |  | 405SEG6628-6626 | Hirangi 405-02 | Rural C | Hirangi | Awamate Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 199 | 27 | 24471 | 5350 | 0.21863 | 0.0011033 | 397.5 | 78771 | 2011/2012 | January-2012 | 1 | 2012
26857 | HANDLE BROKE ON ABS 576 - TAHAROA | 2012-01-16 11:28 | 2012-01-16 | 2012-01-16 12:42 | Calculated | 788 | 788 - Circuit Breaker 788 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa B 33 | Direct from Hangatiki Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 73 | 111 | 24471 | 8175 | 0.33407 | 0.004536 | 3280.8571 | 241635 | 2011/2012 | January-2012 | 1 | 2012
26858 | FUSE PULLED APART AT TX 1A52 - WARD ST | 2012-01-16 16:24 | 2012-01-16 | 2012-01-16 17:09 | Calculated | TF1A52 | TF1A52 - Transformer Fuse: TF1A52 |  | 402SEGA4.6-5351 | Northern 402-01 | Rural B | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 40 | 24471 | 1806 | 0.0738 | 0.0016346 | 200 | 9030 | 2011/2012 | January-2012 | 1 | 2012
26869 | OHURA FEEDER RENEWAL WORK - OHURA | 2012-01-17 08:56 | 2012-01-17 | 2012-01-17 15:34 | Calculated | 5295 | 5295 - Air Break Switch 5295 |  | 413SEG5295-5454 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 361 | 33 | 24471 | 3372 | 0.1378 | 0.0013485 | 208 | 20661 | 2011/2012 | January-2012 | 1 | 2012
26871 | RANGITOTO FEEDER RENEWAL PROJECT - RANGITOTO FEEDER | 2012-01-17 09:04 | 2012-01-17 | 2012-01-17 15:52 | Calculated | 1790 | 1790 - Fused Link 1790 |  | 106SEG659-194 | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 408 | 10 | 24471 | 4081 | 0.16677 | 0.00040865 | 95 | 38777 | 2011/2012 | January-2012 | 1 | 2012
26872 | DUCKS - SOMMEERVILLE RD | 2012-01-18 06:28 | 2012-01-18 | 2012-01-18 07:44 | Calculated | TF3215 | TF3215 - Transformer Fuse: TF3215 |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 3 | 24471 | 228 | 0.00932 | 0.00012259 | 45 | 3428 | 2011/2012 | January-2012 | 1 | 2012
26877 | BIRDS - MAIHIIHI RD | 2012-01-18 08:28 | 2012-01-18 | 2012-01-18 09:30 | Calculated | TF604 | TF604 - Transformer Fuse: TF604 |  | No Segment | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 1 | 24471 | 62 | 0.00253 | 4.0865e-05 | 5 | 310 | 2011/2012 | January-2012 | 1 | 2012
26873 | CHANGING POLES AND XARMS - MOKAUITI FEEDER | 2012-01-18 08:35 | 2012-01-18 | 2012-01-18 16:32 | Calculated | 1705 | 1705 - Air Break Switch 1705 |  | 115SEG1705-1707 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 432 | 127 | 24471 | 17136 | 0.70026 | 0.0051898 | 878 | 131865 | 2011/2012 | January-2012 | 1 | 2012
26876 | OHURA FEEDER RENEWAL WORK | 2012-01-18 08:56 | 2012-01-18 | 2012-01-18 15:36 | Calculated | 5295 | 5295 - Air Break Switch 5295 |  | 413SEG5295-5454 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 344 | 33 | 24471 | 3192 | 0.13044 | 0.0013485 | 208 | 19545 | 2011/2012 | January-2012 | 1 | 2012
26879 | LV POLE DOWN - HAPPY VALLEY RD | 2012-01-18 11:16 | 2012-01-18 | 2012-01-18 16:57 | Calculated | TF270 | TF270 - Transformer Fuse: TF270 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 340 | 3 | 24471 | 1020 | 0.04168 | 0.00012259 | 30 | 10205 | 2011/2012 | January-2012 | 1 | 2012
26881 | MAGPIE - KURURAU RD | 2012-01-18 12:00 | 2012-01-18 | 2012-01-18 13:09 | Calculated | TF8G3 | TF8G3 - Transformer Fuse: TF8G3 |  | No Segment | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 69 | 1 | 24471 | 69 | 0.00282 | 4.0865e-05 | 10 | 691 | 2011/2012 | January-2012 | 1 | 2012
26884 | OHURA FEEDER RENEWAL WORK | 2012-01-19 08:50 | 2012-01-19 | 2012-01-19 15:36 | Calculated | 5295 | 5295 - Air Break Switch 5295 |  | 413SEG5295-5454 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 327 | 33 | 24471 | 3024 | 0.12357 | 0.0013485 | 208 | 18512 | 2011/2012 | January-2012 | 1 | 2012
26885 | REPLACE POLES AND XARMS - MOKAU FEEDER | 2012-01-19 09:33 | 2012-01-19 | 2012-01-19 16:03 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 390 | 27 | 24471 | 10534 | 0.43047 | 0.0011033 | 165 | 64377 | 2011/2012 | January-2012 | 1 | 2012
26886 | BLOWN HV FUSE AT TX 1954 - PARAKOKO RD | 2012-01-19 11:00 | 2012-01-19 | 2012-01-19 12:33 | Calculated | TF1954 | TF1954 - Transformer Fuse: TF1954 |  | 114SEG1125-2160 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 1 | 24471 | 92 | 0.00376 | 4.0865e-05 | 3 | 276 | 2011/2012 | January-2012 | 1 | 2012
26887 | FUSE PULLED APART AT TX 12I05 - KAWAUTAHI RD | 2012-01-19 18:00 | 2012-01-19 | 2012-01-19 20:01 | Calculated | TF12I5 | TF12I5 - Transformer Fuse: TF12I5 |  | 409SEG5751-5401 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 120 | 2 | 24471 | 240 | 0.00981 | 8.1729e-05 | 15 | 1806 | 2011/2012 | January-2012 | 1 | 2012
26888 | REPLACING POLES AND XARMS - MOKAU FEEDER | 2012-01-20 09:32 | 2012-01-20 | 2012-01-20 14:15 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 283 | 27 | 24471 | 7646 | 0.31245 | 0.0011033 | 165 | 46727 | 2011/2012 | January-2012 | 1 | 2012
26890 | 1 FUSE BLOWN AT TX 2417 - RANFURLY ST | 2012-01-21 10:21 | 2012-01-21 | 2012-01-21 11:31 | Calculated | TF2417 | TF2417 - Transformer Fuse: TF2417 |  | 112SEG646-313 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 11 | 24471 | 771 | 0.03151 | 0.00044951 | 200 | 14029 | 2011/2012 | January-2012 | 1 | 2012
26891 | FAULTY TX - NEWMAN RD | 2012-01-21 10:43 | 2012-01-21 | 2012-01-21 13:20 | Calculated | TF697 | TF697 - Transformer Fuse: TF697 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 3 | 24471 | 471 | 0.01925 | 0.00012259 | 15 | 2357 | 2011/2012 | January-2012 | 1 | 2012
26892 | LV LINE DOWN - MAHAKATINO RD | 2012-01-21 12:23 | 2012-01-21 | 2012-01-21 13:24 | Calculated | TF2180 | TF2180 - Transformer Fuse: TF2180 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 61 | 2 | 24471 | 122 | 0.00499 | 8.1729e-05 | 25 | 1532 | 2011/2012 | January-2012 | 1 | 2012
26893 | BLOWN HV FUSE AT TX 1263 - TANGITU RD - FOR PAREKETU RD | 2012-01-23 07:16 | 2012-01-23 | 2012-01-23 09:15 | Calculated | 1263 | 1263 - Sectionaliser with Incoming Link 1263 |  | 115SEG1356-1725 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 119 | 1 | 24471 | 119 | 0.00486 | 4.0865e-05 | 15 | 1788 | 2011/2012 | January-2012 | 1 | 2012
26894 | DUCKS - TE KUMI STATION RD | 2012-01-23 08:41 | 2012-01-23 | 2012-01-23 09:35 | Calculated | 763 | 763 - Fused Link 763 |  | 108SEG763-2140 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 2 | 24471 | 108 | 0.00441 | 8.1729e-05 | 330 | 17875 | 2011/2012 | January-2012 | 1 | 2012
26896 | REPLACE 2 POLES WITH HELICOPTER - COAST FEEDER | 2012-01-23 09:32 | 2012-01-23 | 2012-01-23 14:39 | Calculated | 561 | 561 - Air Break Switch 561 |  | 125SEG561-1758 | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 306 | 17 | 24471 | 5205 | 0.2127 | 0.0006947 | 115 | 35211 | 2011/2012 | January-2012 | 1 | 2012
26897 | LINE DOWN - TANGITU RD | 2012-01-23 16:15 | 2012-01-23 | 2012-01-23 20:36 | Calculated | 1724 | 1724 - Sectionaliser with Bypass & LInks 1724 |  | 115SEG1723-1724 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 261 | 14 | 24471 | 2464 | 0.10069 | 0.00057211 | 128 | 20017 | 2011/2012 | January-2012 | 1 | 2012
26899 | REPLACE RED TAGGED POLES 7,8,10 AND TX 1353 - TIHOI FEEDER | 2012-01-24 08:19 | 2012-01-24 | 2012-01-24 15:33 | Calculated | TF1353 | TF1353 - Transformer Fuse: TF1353 |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 371 | 4 | 24471 | 1482 | 0.06056 | 0.00016346 | 15 | 5559 | 2011/2012 | January-2012 | 1 | 2012
26901 | SCHEDULED MAINTENANCE - SH 49 | 2012-01-24 09:33 | 2012-01-24 | 2012-01-24 16:31 | Calculated | TF21N14 | TF21N14 - Transformer Fuse: TF21N14 |  | 416SEG5683-5523 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 418 | 5 | 24471 | 2091 | 0.08545 | 0.00020432 | 50 | 20916 | 2011/2012 | January-2012 | 1 | 2012
26902 | BLOWN FUSED LINK 1617 - PIOI STATION - SPUR BY ESTUARY | 2012-01-24 14:20 | 2012-01-24 | 2012-01-24 16:01 | Calculated | 1617 | 1617 - Fused Link 1617 |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 2 | 24471 | 202 | 0.00825 | 8.1729e-05 | 30 | 3034 | 2011/2012 | January-2012 | 1 | 2012
26906 | FUSE PULLED APART - VALLEY RD | 2012-01-25 06:31 | 2012-01-25 | 2012-01-25 08:34 | Calculated | TF8J6 | TF8J6 - Transformer Fuse: TF8J6 |  | No Segment | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 2 | 24471 | 246 | 0.01005 | 8.1729e-05 | 10 | 1231 | 2011/2012 | January-2012 | 1 | 2012
26907 | CHANGING POLES AND XARMS - MOKAUITI FEEDER | 2012-01-25 08:31 | 2012-01-25 | 2012-01-25 16:49 | Calculated | 1705 | 1705 - Air Break Switch 1705 |  | 115SEG1705-1707 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 430 | 136 | 24471 | 4429 | 0.18099 | 0.0055576 | 930.5 | 30741 | 2011/2012 | January-2012 | 1 | 2012
26908 | YACHT VS LINE - SH 1 | 2012-01-25 08:50 | 2012-01-25 | 2012-01-25 10:41 | Calculated | TF9T1 | TF9T1 - Transformer Fuse: TF9T1 |  | 425SEG6134-6552 | Motuoapa 425-01 | Rural D | Motuoapa | Kiko Road Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 89 | 24471 | 9890 | 0.40415 | 0.003637 | 300 | 33339 | 2011/2012 | January-2012 | 1 | 2012
26909 | REPLACE 1191005,6,9 AND 13 - PUREORA FEEDER | 2012-01-25 09:09 | 2012-01-25 | 2012-01-25 14:10 | Calculated | 495 | 495 - Fused Link 495 |  | 119SEG495 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 301 | 9 | 24471 | 2710 | 0.11074 | 0.00036778 | 110 | 33130 | 2011/2012 | January-2012 | 1 | 2012
26910 | LINE RENEWALS - RANGIPO/HAUTU | 2012-01-25 09:36 | 2012-01-25 | 2012-01-25 15:01 | Calculated | TF11S10 | TF11S10 - Transformer Fuse: TF11S10 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 324 | 13 | 24471 | 4217 | 0.17233 | 0.00053124 | 1537.5 | 498816 | 2011/2012 | January-2012 | 1 | 2012
26905 | BROKEN SUSPENSION CLAMP - ONGARUE/TAPUWAHINE | 2012-01-26 05:11 | 2012-01-26 | 2012-01-26 15:53 | Calculated | 5462 | 5462 - Sectionaliser with Bypass & Links 5462 |  | 421SEG6554-5462RET | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 642 | 123 | 24471 | 78984 | 3.2277 | 0.0050264 | 877.5 | 563486 | 2011/2012 | January-2012 | 1 | 2012
26911 | CHANGING POLES AND XARMS - MOKAUITI FEEDER | 2012-01-26 08:37 | 2012-01-26 | 2012-01-26 15:47 | Calculated | 1705 | 1705 - Air Break Switch 1705 |  | 115SEG1705-1707 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 353 | 136 | 24471 | 3695 | 0.151 | 0.0055576 | 930.5 | 25857 | 2011/2012 | January-2012 | 1 | 2012
26913 | LINE RENEWALS - RANGIPO/HAUTU | 2012-01-26 09:35 | 2012-01-26 | 2012-01-26 15:14 | Calculated | TF11S10 | TF11S10 - Transformer Fuse: TF11S10 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 338 | 13 | 24471 | 4399 | 0.17976 | 0.00053124 | 1537.5 | 520341 | 2011/2012 | January-2012 | 1 | 2012
26915 | POSSUM - MAROTIRI RD | 2012-01-26 19:12 | 2012-01-26 | 2012-01-26 21:14 | Calculated | TF1127 | TF1127 - Transformer Fuse: TF1127 |  | 123SEG696 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 1 | 24471 | 122 | 0.00499 | 4.0865e-05 | 25 | 3052 | 2011/2012 | January-2012 | 1 | 2012
26916 | FAULTY DDO FUSE CARRIER - MIRO ST | 2012-01-27 08:10 | 2012-01-27 | 2012-01-27 10:09 | Calculated | TF8J48 | TF8J48 - Transformer Fuse: TF8J48 |  | 408SEG5390-5621 | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 27 | 24471 | 3190 | 0.13036 | 0.0011033 | 200 | 23629 | 2011/2012 | January-2012 | 1 | 2012
26917 | CHANGING POLES AND XARMS - MOKAUITI FEEDER | 2012-01-27 08:43 | 2012-01-27 | 2012-01-27 16:06 | Calculated | 1705 | 1705 - Air Break Switch 1705 |  | 115SEG1705-1707 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 222 | 136 | 24471 | 2393 | 0.09779 | 0.0055576 | 930.5 | 16171 | 2011/2012 | January-2012 | 1 | 2012
26918 | LINE RENEWALS - RANGIPO/HAUTU | 2012-01-27 09:36 | 2012-01-27 | 2012-01-27 12:57 | Calculated | TF11S10 | TF11S10 - Transformer Fuse: TF11S10 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 200 | 13 | 24471 | 2605 | 0.10645 | 0.00053124 | 1537.5 | 308166 | 2011/2012 | January-2012 | 1 | 2012
26920 | INSTALL NEW POLE AND TX - WHAREPAPA FEEDR | 2012-01-27 10:05 | 2012-01-27 | 2012-01-27 13:34 | Calculated | 367 | 367 - Air Break Switch 367 |  | 122SEG367-549 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 124 | 21 | 24471 | 2590 | 0.10584 | 0.00085816 | 235 | 28983 | 2011/2012 | January-2012 | 1 | 2012
26922 | RECLOSER OCB 262 AND 788 TRIPPED - TAHAROA B | 2012-01-27 23:20 | 2012-01-27 | 2012-01-27 23:22 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 327 | 24471 | 697 | 0.02848 | 0.013363 | 2443.1831 | 5212 | 2011/2012 | January-2012 | 1 | 2012
26923 | WIND - LV CLASH - BARBERS RD | 2012-01-28 06:04 | 2012-01-28 | 2012-01-28 07:19 | Calculated | TF2863 | TF2863 - Transformer Fuse: TF2863 |  | No Segment | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 24471 | 75 | 0.00306 | 4.0865e-05 | 100 | 7515 | 2011/2012 | January-2012 | 1 | 2012
26924 | WIND - TARINGAMOTU RD | 2012-01-28 12:51 | 2012-01-28 | 2012-01-28 13:14 | Calculated | TF7I5 | TF7I5 - Transformer Fuse: TF7I5 |  | No Segment | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 18 | 24471 | 416 | 0.017 | 0.00073556 | 50 | 1156 | 2011/2012 | January-2012 | 1 | 2012
26927 | FAULTY LA AT TX 8I67 - HIKUMUTU RD | 2012-01-29 11:45 | 2012-01-29 | 2012-01-29 18:56 | Calculated | 5513 | 5513 - Fused Link 5513 |  | 403SEG5513 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 143 | 2 | 24471 | 284 | 0.01161 | 8.1729e-05 | 30 | 4266 | 2011/2012 | January-2012 | 1 | 2012
26928 | WIND - SH 3 PASTORAL HOLDINS | 2012-01-29 17:09 | 2012-01-29 | 2012-01-29 18:23 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 8 | 24471 | 593 | 0.02423 | 0.00032692 | 95 | 7045 | 2011/2012 | January-2012 | 1 | 2012
26926 | WIND - MAIN RD - NORTH OF SLALOM LODGE | 2012-01-29 23:57 | 2012-01-29 | 2012-01-30 02:15 | Calculated | 5139 | 5139 - Fused Link 5139 |  | 410SEG5543-5161 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 79 | 24471 | 10916 | 0.44608 | 0.0032283 | 440 | 60800 | 2011/2012 | January-2012 | 1 | 2012
26929 | FAULTY TX - MAIN STH RD - TE KUITI | 2012-01-30 18:37 | 2012-01-30 | 2012-01-30 21:41 | Calculated | TF45 | TF45 - Transformer Fuse: TF45 |  | No Segment | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 184 | 3 | 24471 | 552 | 0.02256 | 0.00012259 | 15 | 2764 | 2011/2012 | January-2012 | 1 | 2012
26930 | RECLOSER 5107 - MAITERE SUB | 2012-01-31 06:51 | 2012-01-31 | 2012-01-31 07:10 | Calculated | 5107 | 5107 - Recloser with Bypass & Links 5107 |  | 422SEG05F14-5107 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 19 | 64 | 24471 | 1227 | 0.05014 | 0.0026153 | 454 | 8709 | 2011/2012 | January-2012 | 1 | 2012
26931 | CHANGE POLES AND XARMS - COAST FEEDER | 2012-01-31 09:46 | 2012-01-31 | 2012-01-31 16:58 | Calculated | 298 | 298 - Fused Link 298 |  | 125SEG298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 431 | 9 | 24471 | 3886 | 0.1588 | 0.00036778 | 45 | 19433 | 2011/2012 | January-2012 | 1 | 2012
26932 | UPGRADE TX 20L57 - OHAKUNE TOWN | 2012-01-31 14:02 | 2012-01-31 | 2012-01-31 14:47 | Calculated | 5701 | 5701 - Ring Main Unit 5701 |  | 414SEG5706-5701 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 44 | 54 | 24471 | 2399 | 0.09803 | 0.0022067 | 600 | 26659 | 2011/2012 | January-2012 | 1 | 2012
26933 | OHURA FEEDER UPGRADE - OHURA FEEDER | 2012-02-01 08:08 | 2012-02-01 | 2012-02-01 16:25 | Calculated | 5294 | 5294 - Fused Link 5294 |  | 413SEG5294-5298 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 416 | 123 | 24431 | 8149 | 0.33355 | 0.0050346 | 858.5 | 76729 | 2011/2012 | February-2012 | 2 | 2012
26938 | BLOWN HV FUSE AT TX 604 - MAIHIIHI RD | 2012-02-01 08:56 | 2012-02-01 | 2012-02-01 13:02 | Calculated | TF604 | TF604 - Transformer Fuse: TF604 |  | No Segment | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 246 | 1 | 24431 | 246 | 0.01007 | 4.0932e-05 | 5 | 1231 | 2011/2012 | February-2012 | 2 | 2012
26939 | CHANGE POLES AND XARMS - COAST FEEDER | 2012-02-01 09:32 | 2012-02-01 | 2012-02-01 13:48 | Calculated | 298 | 298 - Fused Link 298 |  | 125SEG298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 256 | 9 | 24431 | 2305 | 0.09435 | 0.00036838 | 45 | 11525 | 2011/2012 | February-2012 | 2 | 2012
26940 | REPLACE POLE 1190088 LIVE LINE - PUREORA FEEDER | 2012-02-01 09:40 | 2012-02-01 | 2012-02-01 15:50 | Calculated | TF2436 | TF2436 - Transformer Fuse: TF2436 |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 370 | 1 | 24431 | 370 | 0.01514 | 4.0932e-05 | 50 | 18506 | 2011/2012 | February-2012 | 2 | 2012
26934 | CHANGE POLES AND XARMS - COAST FEEDER | 2012-02-01 09:41 | 2012-02-01 | 2012-02-01 15:46 | Calculated | 298 | 298 - Fused Link 298 |  | 125SEG298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 365 | 9 | 24431 | 3286 | 0.1345 | 0.00036838 | 45 | 16433 | 2011/2012 | February-2012 | 2 | 2012
26941 | FUSE PULLED APART - KAITUPEKA PA RD | 2012-02-01 09:53 | 2012-02-01 | 2012-02-01 11:42 | Calculated | TF7J20 | TF7J20 - Transformer Fuse: TF7J20 |  | 402SEG5635 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 108 | 1 | 24431 | 108 | 0.00442 | 4.0932e-05 | 10 | 1084 | 2011/2012 | February-2012 | 2 | 2012
26935 | REPLACE POLES - MAIHIIHI FEEDER | 2012-02-01 12:08 | 2012-02-01 | 2012-02-01 15:10 | Calculated | 1746 | 1746 - Fused Link 1746 |  | 111SEG357-579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 182 | 4 | 24431 | 728 | 0.0298 | 0.00016373 | 110 | 20034 | 2011/2012 | February-2012 | 2 | 2012
26936 | REPLACE FAULTY SUSPENSION INSULATOR - RAURIMU FEEDER | 2012-02-01 13:04 | 2012-02-01 | 2012-02-01 13:53 | Calculated | 5407 | 5407 - Sectionaliser with Bypass 5407 |  | 410SEG5407-5433 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 49 | 46 | 24431 | 2263 | 0.09263 | 0.0018829 | 267.5 | 13165 | 2011/2012 | February-2012 | 2 | 2012
26942 | BLOWN LINK 256 - AHUROA RD - OLIVER'S SPUR | 2012-02-01 16:24 | 2012-02-01 | 2012-02-01 17:03 | Calculated | 256 | 256 - Fused Link 256 |  | 106SEG256 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 6 | 24431 | 234 | 0.00958 | 0.00024559 | 35 | 1369 | 2011/2012 | February-2012 | 2 | 2012
26937 | OHURA FEEDER UPGRADE - OHURA FEEDER | 2012-02-02 08:07 | 2012-02-02 | 2012-02-02 16:49 | Calculated | 5294 | 5294 - Fused Link 5294 |  | 413SEG5294-5298 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 435 | 123 | 24431 | 8542 | 0.34964 | 0.0050346 | 858.5 | 80414 | 2011/2012 | February-2012 | 2 | 2012
26944 | FEEDER UPGRADE - OHURA FEEDER | 2012-02-03 08:11 | 2012-02-03 | 2012-02-03 15:51 | Calculated | 5298 | 5298 - Air Break Switch 5298 |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 184 | 84 | 24431 | 1067 | 0.04367 | 0.0034383 | 613 | 18258 | 2011/2012 | February-2012 | 2 | 2012
26945 | REMOVE LINE FOR TREESCAPE TO REMOVE TREE - TE KUITI SOUTH | 2012-02-03 09:05 | 2012-02-03 | 2012-02-03 14:23 | Calculated | 220 | 220 - Fused Link 220 |  | 104SEG217-730 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 318 | 6 | 24431 | 1909 | 0.07814 | 0.00024559 | 45 | 14318 | 2011/2012 | February-2012 | 2 | 2012
26948 | CONNECT NEW MAGNAFIX UNITS - OHAKUNE TOWN | 2012-02-03 09:24 | 2012-02-03 | 2012-02-03 13:21 | Calculated | 5701 | 5701 - Ring Main Unit 5701 |  | 414SEG5706-5701 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 205 | 54 | 24431 | 4920 | 0.20138 | 0.0022103 | 600 | 61429 | 2011/2012 | February-2012 | 2 | 2012
26951 | LINE DOWN - HUIA RD | 2012-02-04 07:25 | 2012-02-04 | 2012-02-04 12:55 | Calculated | 5287 | 5287 - Recloser with Bypass & Links 5287 |  | 413SEG5288-5287 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 319 | 32 | 24431 | 5828 | 0.23855 | 0.0013098 | 213 | 37783 | 2011/2012 | February-2012 | 2 | 2012
26952 | SECTIONALISER 1724 TRIPPED - SH 4 CORNER TANGITU RD | 2012-02-04 10:45 | 2012-02-04 | 2012-02-04 12:20 | Calculated | 1724 | 1724 - Sectionaliser with Bypass & LInks 1724 |  | 115SEG1723-1724 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 95 | 14 | 24431 | 1331 | 0.05448 | 0.00057304 | 128 | 12174 | 2011/2012 | February-2012 | 2 | 2012
26953 | REPLACE HV FUSE AT TX604 - MAIHIIHI RD | 2012-02-04 12:52 | 2012-02-04 | 2012-02-04 13:16 | Calculated | TF604 | TF604 - Transformer Fuse: TF604 |  | No Segment | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 1 | 24431 | 23 | 0.00094 | 4.0932e-05 | 5 | 115 | 2011/2012 | February-2012 | 2 | 2012
26954 | SECTIONALISER 5591 TRIPPED - BY TE ROTO SCHOOL | 2012-02-04 21:29 | 2012-02-04 | 2012-02-04 22:57 | Calculated | 5591 | 5591 - Sectionaliser with Bypass & Links 5591 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 88 | 52 | 24431 | 4582 | 0.18755 | 0.0021284 | 198 | 17450 | 2011/2012 | February-2012 | 2 | 2012
26955 | SECTIONALISER 5511 TRIPPED - MAKINO RD | 2012-02-06 08:21 | 2012-02-06 | 2012-02-06 09:15 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | 410SEG5511-5517 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 54 | 29 | 24431 | 1570 | 0.06426 | 0.001187 | 183.5 | 9936 | 2011/2012 | February-2012 | 2 | 2012
26959 | BLOWN FUSED LINK 1617 - PIOI STATION - SPUR BY ESTUARY | 2012-02-07 10:26 | 2012-02-07 | 2012-02-07 11:31 | Calculated | 1617 | 1617 - Fused Link 1617 |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 2 | 24431 | 130 | 0.00532 | 8.1863e-05 | 30 | 1953 | 2011/2012 | February-2012 | 2 | 2012
26958 | SCHEDULED MAINTENANCE - SH 31 | 2012-02-07 10:27 | 2012-02-07 | 2012-02-07 11:22 | Calculated | 139 | 139 - Fused Link 139 |  | 112SEG139 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 55 | 5 | 24431 | 275 | 0.01126 | 0.00020466 | 75 | 4134 | 2011/2012 | February-2012 | 2 | 2012
26960 | POSSUM - GADSBY RD | 2012-02-08 02:20 | 2012-02-08 | 2012-02-08 06:13 | Calculated | TF2951 | TF2951 - Transformer Fuse: TF2951 |  | No Segment | Oparure 107-01 | Urban A | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 232 | 1 | 24431 | 232 | 0.0095 | 4.0932e-05 | 100 | 23285 | 2011/2012 | February-2012 | 2 | 2012
26961 | BLOWN HV FUSE AT TX 1510 - BLUCKS RD | 2012-02-08 02:34 | 2012-02-08 | 2012-02-08 07:56 | Calculated | TF1510 | TF1510 - Transformer Fuse: TF1510 |  | 111SEG325 | Maihiihi 111-02 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 322 | 5 | 24431 | 1611 | 0.06594 | 0.00020466 | 30 | 9667 | 2011/2012 | February-2012 | 2 | 2012
26963 | LV LINE DOWN - LIVESTOCK - TE WAITERE RD | 2012-02-08 14:23 | 2012-02-08 | 2012-02-08 14:43 | Calculated | TF2868 | TF2868 - Transformer Fuse: TF2868 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Birds & Animals | Animals | BANI:ANIM:AFAR | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 1 | 24431 | 20 | 0.00082 | 4.0932e-05 | 3 | 60 | 2011/2012 | February-2012 | 2 | 2012
26964 | LOOSE LV CONNECTION - MANGAWHIO RD | 2012-02-08 20:00 | 2012-02-08 | 2012-02-08 20:20 | Calculated | TF836 | TF836 - Transformer Fuse: TF836 |  | No Segment | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 2 | 24431 | 40 | 0.00164 | 8.1863e-05 | 25 | 504 | 2011/2012 | February-2012 | 2 | 2012
26967 | BLOWN HV FUSE AT TX08E02 - MANGATOROTA STREAM RD | 2012-02-09 08:35 | 2012-02-09 | 2012-02-09 11:02 | Calculated | TF8E2 | TF8E2 - Transformer Fuse: TF8E2 |  | 413SEG5579-5571 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 147 | 4 | 24431 | 588 | 0.02407 | 0.00016373 | 10 | 1471 | 2011/2012 | February-2012 | 2 | 2012
26968 | REPLACE POLES AND XARM - COAST FEEDER | 2012-02-09 08:40 | 2012-02-09 | 2012-02-09 16:13 | Calculated | 281 | 281 - Air Break Switch 281 |  | 125SEG281-298 | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 437 | 72 | 24431 | 7615 | 0.31169 | 0.0029471 | 630 | 56691 | 2011/2012 | February-2012 | 2 | 2012
26969 | REPLACE POLES 98/6 AND 7 - RANGIPO/HAUTU | 2012-02-09 09:36 | 2012-02-09 | 2012-02-09 15:27 | Calculated | TF13S01 | TF13S01 - Transformer Fuse: TF13S01 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 350 | 6 | 24431 | 2100 | 0.08596 | 0.00024559 | 300 | 105045 | 2011/2012 | February-2012 | 2 | 2012
26978 | BLOWN HV FUSE AT TX 2863 - BARBERS RD | 2012-02-10 05:49 | 2012-02-10 | 2012-02-10 06:45 | Calculated | TF2863 | TF2863 - Transformer Fuse: TF2863 |  | No Segment | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 1 | 24431 | 56 | 0.00229 | 4.0932e-05 | 100 | 5611 | 2011/2012 | February-2012 | 2 | 2012
26974 | REPLACE POLES AND XARM - COAST FEEDER | 2012-02-10 08:46 | 2012-02-10 | 2012-02-10 16:05 | Calculated | 281 | 281 - Air Break Switch 281 |  | 125SEG281-298 | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 409 | 72 | 24431 | 7051 | 0.28861 | 0.0029471 | 630 | 51930 | 2011/2012 | February-2012 | 2 | 2012
26976 | LV LINE DOWN - WAITOMO CAVES RD | 2012-02-10 12:47 | 2012-02-10 | 2012-02-10 17:41 | Calculated | TF84 | TF84 - Transformer Fuse: TF84 |  | 101SEG577-679 | Caves 101-05 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 294 | 2 | 24431 | 588 | 0.02407 | 8.1863e-05 | 15 | 4412 | 2011/2012 | February-2012 | 2 | 2012
26979 | JUMPER OFF AT ABS 492 - SCOTT RD | 2012-02-11 05:51 | 2012-02-11 | 2012-02-11 07:27 | Calculated | SEG492-REG26J | SEG492-REG26J - 119SEG492-REG26J |  | No Segment | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24431 |  | 0 | 0 |  |  | 2011/2012 | February-2012 | 2 | 2012
26980 | MAINTENANCE TO LV BOARD INSIDE TX 10S30 - TURANGI FEEDER | 2012-02-13 09:21 | 2012-02-13 | 2012-02-13 11:32 | Calculated | TF10S30 | TF10S30 - Transformer Fuse: TF10S30 |  | 423SEG5209-6180 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 130 | 88 | 24431 | 11459 | 0.46904 | 0.003602 | 300 | 39064 | 2011/2012 | February-2012 | 2 | 2012
26981 | BROKEN NEUTRAL - TROOPERS RD | 2012-02-13 14:19 | 2012-02-13 | 2012-02-13 16:05 | Calculated | TF1212 | TF1212 - Transformer Fuse: TF1212 |  | 107SEG244-575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 5 | 24431 | 525 | 0.02149 | 0.00020466 | 30 | 3155 | 2011/2012 | February-2012 | 2 | 2012
26982 | COOKED HV CONNECTION AT LINKS 6645 - PAREROHI GROVE | 2012-02-13 21:44 | 2012-02-13 | 2012-02-14 00:06 | Calculated | 6023 | 6023 - Fused Link 6023 |  | 406SEG5895-5878RET | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 19 | 24431 | 2700 | 0.11052 | 0.0007777 | 120 | 17056 | 2011/2012 | February-2012 | 2 | 2012
26983 | DEAD BIRD - WAITOMO CAVES | 2012-02-14 09:01 | 2012-02-14 | 2012-02-14 09:46 | Calculated | TF88 | TF88 - Transformer Fuse: TF88 |  | 101SEG746-1656 | Caves 101-08 | Urban A | Caves | Hangatiki Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 1 | 24431 | 45 | 0.00184 | 4.0932e-05 | 200 | 9036 | 2011/2012 | February-2012 | 2 | 2012
26984 | REPLACING POLES AND HARDWARE WITH HELICOPTER | 2012-02-14 09:01 | 2012-02-14 | 2012-02-14 16:20 | Calculated | 1788 | 1788 - Fused Link 1788 |  | 129SEG1788-1780 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 439 | 2 | 24431 | 878 | 0.03594 | 8.1863e-05 | 15 | 6587 | 2011/2012 | February-2012 | 2 | 2012
26985 | CHANGE TX 1636 - LEITCH RD | 2012-02-14 13:58 | 2012-02-14 | 2012-02-14 14:56 | Calculated | TF1636 | TF1636 - Transformer Fuse: TF1636 |  | 113SEG1510-1636 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 57 | 3 | 24431 | 173 | 0.00708 | 0.00012279 | 15 | 866 | 2011/2012 | February-2012 | 2 | 2012
26986 | JUMPER OFF AT TX 05H01 - TUHUA SUB | 2012-02-14 23:07 | 2012-02-14 | 2012-02-15 00:31 | Calculated | 5726 | 5726 - Fused Link 5726 |  | 422SEG5576-5414 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 43 | 24431 | 703 | 0.02877 | 0.0017601 | 291.5 | 4689 | 2011/2012 | February-2012 | 2 | 2012
26995 | FUSE PULLED APART - PUKAWA SUB | 2012-02-15 07:04 | 2012-02-15 | 2012-02-15 17:50 | Calculated | 5616 | 5616 - Fused Link 5616 |  | 406SEG5248-5617 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 646 | 35 | 24431 | 22615 | 0.92567 | 0.0014326 | 177.5 | 114694 | 2011/2012 | February-2012 | 2 | 2012
26990 | FEEDER UPGRADE - OHURA FEEDER | 2012-02-15 08:07 | 2012-02-15 | 2012-02-15 16:04 | Calculated | 5298 | 5298 - Air Break Switch 5298 |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 397 | 84 | 24431 | 2020 | 0.08268 | 0.0034383 | 613 | 37806 | 2011/2012 | February-2012 | 2 | 2012
26991 | BLOWN HV FUSE AT TX 2844 - KAAHU RD | 2012-02-15 09:16 | 2012-02-15 | 2012-02-15 12:07 | Calculated | TF2844 | TF2844 - Transformer Fuse: TF2844 |  | 129SEG1749-2204 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 3 | 24431 | 513 | 0.021 | 0.00012279 | 15 | 2568 | 2011/2012 | February-2012 | 2 | 2012
26993 | MAGPIE AND FAULTY BUSHING - TUNANUI SUB | 2012-02-15 09:46 | 2012-02-15 | 2012-02-15 18:31 | Calculated | 5415 | 5415 - Recloser with Bypass & Links 5415 |  | 409SEG5415-5844 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 240 | 35 | 24431 | 6769 | 0.27707 | 0.0014326 | 241.5 | 47147 | 2011/2012 | February-2012 | 2 | 2012
26992 | UPGRADE TX 2703 - MANGAKOWHAI RD | 2012-02-15 09:47 | 2012-02-15 | 2012-02-15 15:00 | Calculated | TF2703 | TF2703 - Transformer Fuse: TF2703 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 313 | 2 | 24431 | 626 | 0.02562 | 8.1863e-05 | 30 | 9394 | 2011/2012 | February-2012 | 2 | 2012
26996 | REROUTING HV CABLE VIA STRAIGHT JOINT | 2012-02-16 06:16 | 2012-02-16 | 2012-02-16 15:45 | Calculated | TF9T6 | TF9T6 - Transformer Fuse: TF9T6 |  | 417SEG5927-6128 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 27 | 24431 | 1115 | 0.04564 | 0.0011052 | 103.8462 | 4292 | 2011/2012 | February-2012 | 2 | 2012
26997 | BLOWN HV FUSE AT TX 14N02 | 2012-02-16 07:39 | 2012-02-16 | 2012-02-16 09:18 | Calculated | TF14N02 | TF14N02 - Transformer Fuse: TF14N02 |  | 609SEG5787-6007 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 99 | 2 | 24431 | 198 | 0.0081 | 8.1863e-05 | 15 | 1487 | 2011/2012 | February-2012 | 2 | 2012
26999 | FEEDER UPGRADE - OHURA FEEDER | 2012-02-16 08:10 | 2012-02-16 | 2012-02-16 15:44 | Calculated | 5298 | 5298 - Air Break Switch 5298 |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 412 | 84 | 24431 | 2197 | 0.08993 | 0.0034383 | 613 | 36661 | 2011/2012 | February-2012 | 2 | 2012
27003 | REPLACING POLES AND HARDWARE WITH HELICOPTER - TIROHANGA FEEDER | 2012-02-16 09:03 | 2012-02-16 | 2012-02-16 13:41 | Calculated | 1788 | 1788 - Fused Link 1788 |  | 129SEG1788-1780 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 278 | 2 | 24431 | 556 | 0.02276 | 8.1863e-05 | 15 | 4175 | 2011/2012 | February-2012 | 2 | 2012
27004 | REPLACE POLE 1111284 LIVE LINE -MAIHIIHI FEEDER | 2012-02-16 09:07 | 2012-02-16 | 2012-02-16 13:45 | Calculated | TF619 | TF619 - Transformer Fuse: TF619 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 278 | 2 | 24431 | 556 | 0.02276 | 8.1863e-05 | 25 | 6954 | 2011/2012 | February-2012 | 2 | 2012
27006 | REPLACE HV FUSE AT TX 07I05 - TARINGAMOTU RD | 2012-02-16 10:03 | 2012-02-16 | 2012-02-16 11:28 | Calculated | TF7I5 | TF7I5 - Transformer Fuse: TF7I5 |  | No Segment | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 18 | 24431 | 1533 | 0.06275 | 0.00073677 | 50 | 4259 | 2011/2012 | February-2012 | 2 | 2012
27007 | LIGHTNING - TAPUWAE RD | 2012-02-16 19:16 | 2012-02-16 | 2012-02-16 21:51 | Calculated | TF3280 | TF3280 - Transformer Fuse: TF3280 |  | 103SEG1651-2227 | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 1 | 24431 | 155 | 0.00634 | 4.0932e-05 | 75 | 11636 | 2011/2012 | February-2012 | 2 | 2012
27008 | FEEDER UPGRADE - OHURA FEEDER | 2012-02-17 08:08 | 2012-02-17 | 2012-02-17 15:48 | Calculated | 5298 | 5298 - Air Break Switch 5298 |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 250 | 83 | 24431 | 1371 | 0.05612 | 0.0033973 | 608 | 24236 | 2011/2012 | February-2012 | 2 | 2012
27010 | REPLACE RED TAGGED LV POLE - TE WAITERE RD | 2012-02-17 09:54 | 2012-02-17 | 2012-02-17 14:00 | Calculated | TF540 | TF540 - Transformer Fuse: TF540 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 245 | 7 | 24431 | 1721 | 0.07044 | 0.00028652 | 30 | 7376 | 2011/2012 | February-2012 | 2 | 2012
27013 | LINE DOWN - KOTUROA RD | 2012-02-17 11:00 | 2012-02-17 | 2012-02-18 12:43 | Calculated | 5490 | 5490 - Recloser with Bypass 5490 |  | 410SEG5490-5438 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1527 | 73 | 24431 | 25647 | 1.0498 | 0.002988 | 418 | 157915 | 2011/2012 | February-2012 | 2 | 2012
27012 | LIGHTNING - MANGATOROTA STREAM RD | 2012-02-17 11:01 | 2012-02-17 | 2012-02-17 13:33 | Calculated | TF914 | TF914 - Transformer Fuse: TF914 |  | No Segment | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 152 | 1 | 24431 | 152 | 0.00622 | 4.0932e-05 | 10 | 1525 | 2011/2012 | February-2012 | 2 | 2012
27011 | LIGHTNING - MANGATOROTA STREAM RD | 2012-02-17 11:30 | 2012-02-17 | 2012-02-17 13:17 | Calculated | TF8E2 | TF8E2 - Transformer Fuse: TF8E2 |  | 413SEG5579-5571 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 107 | 4 | 24431 | 428 | 0.01752 | 0.00016373 | 10 | 1071 | 2011/2012 | February-2012 | 2 | 2012
27014 | LIGHTNING - SH 32 | 2012-02-17 14:33 | 2012-02-17 | 2012-02-17 15:14 | Calculated | TF3Q7 | TF3Q7 - Transformer Fuse: TF3Q7 |  | No Segment | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 1 | 24431 | 41 | 0.00168 | 4.0932e-05 | 10 | 411 | 2011/2012 | February-2012 | 2 | 2012
27016 | LIGHTNING - SH 41 | 2012-02-17 14:45 | 2012-02-17 | 2012-02-17 15:46 | Calculated | TF09P02 | TF09P02 - Transformer Fuse: TF09P02 |  | 609SEG5839-5163 | National Park / Kuratau 609-01 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 61 | 1 | 24431 | 61 | 0.0025 | 4.0932e-05 | 100 | 6113 | 2011/2012 | February-2012 | 2 | 2012
27017 | LIGHTNING - WHATAURI RD | 2012-02-17 15:00 | 2012-02-17 | 2012-02-17 16:29 | Calculated | TF881 | TF881 - Transformer Fuse: TF881 |  | No Segment | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 2 | 24431 | 178 | 0.00729 | 8.1863e-05 | 15 | 1337 | 2011/2012 | February-2012 | 2 | 2012
27018 | LIGHTNING - OLD TE KUITI RD | 2012-02-17 16:55 | 2012-02-17 | 2012-02-17 17:27 | Calculated | TF389 | TF389 - Transformer Fuse: TF389 |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 3 | 24431 | 96 | 0.00393 | 0.00012279 | 30 | 964 | 2011/2012 | February-2012 | 2 | 2012
27019 | LIGHTNING - FLEMINGS RD | 2012-02-17 16:55 | 2012-02-17 | 2012-02-17 17:34 | Calculated | TF186 | TF186 - Transformer Fuse: TF186 |  | No Segment | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 4 | 24431 | 156 | 0.00639 | 0.00016373 | 50 | 1956 | 2011/2012 | February-2012 | 2 | 2012
27020 | LIGHTNING - OLD TE KUITI RD | 2012-02-17 16:55 | 2012-02-17 | 2012-02-17 17:46 | Calculated | TF563 | TF563 - Transformer Fuse: TF563 |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 1 | 24431 | 50 | 0.00205 | 4.0932e-05 | 15 | 753 | 2011/2012 | February-2012 | 2 | 2012
27021 | LIGHTNING - IRVINE RD | 2012-02-17 16:55 | 2012-02-17 | 2012-02-17 18:07 | Calculated | TF1300 | TF1300 - Transformer Fuse: TF1300 |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 2 | 24431 | 142 | 0.00581 | 8.1863e-05 | 25 | 1780 | 2011/2012 | February-2012 | 2 | 2012
27022 | LIGHTNING - VEALE RD | 2012-02-17 16:55 | 2012-02-17 | 2012-02-17 18:34 | Calculated | TF467 | TF467 - Transformer Fuse: TF467 |  | No Segment | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 1 | 24431 | 98 | 0.00401 | 4.0932e-05 | 10 | 982 | 2011/2012 | February-2012 | 2 | 2012
27025 | LIGHTNING - OLD TE KUITI RD | 2012-02-17 16:55 | 2012-02-17 | 2012-02-17 20:45 | Calculated | TF208 | TF208 - Transformer Fuse: TF208 |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 229 | 3 | 24431 | 687 | 0.02812 | 0.00012279 | 25 | 5730 | 2011/2012 | February-2012 | 2 | 2012
27023 | LIGHTNING - WAIHAHA RD | 2012-02-17 18:07 | 2012-02-17 | 2012-02-17 19:14 | Calculated | TF4Q4 | TF4Q4 - Transformer Fuse: TF4Q4 |  | No Segment | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 4 | 24431 | 264 | 0.01081 | 0.00016373 | 15 | 993 | 2011/2012 | February-2012 | 2 | 2012
27024 | LIGHTNING - OPARURE RD | 2012-02-17 19:24 | 2012-02-17 | 2012-02-17 19:50 | Calculated | TF56 | TF56 - Transformer Fuse: TF56 |  | 107SEG706-243 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 4 | 24431 | 100 | 0.00409 | 0.00016373 | 30 | 757 | 2011/2012 | February-2012 | 2 | 2012
27026 | LIGHTNING - OPARURE RD | 2012-02-17 19:24 | 2012-02-17 | 2012-02-17 20:56 | Calculated | TF116 | TF116 - Transformer Fuse: TF116 |  | 107SEG706-243 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 2 | 24431 | 182 | 0.00745 | 8.1863e-05 | 15 | 1368 | 2011/2012 | February-2012 | 2 | 2012
27027 | LIGHTNING (FAULTY TX) - OPARURE RD | 2012-02-18 06:14 | 2012-02-18 | 2012-02-18 11:35 | Calculated | TF2707 | TF2707 - Transformer Fuse: TF2707 |  | No Segment | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 321 | 1 | 24431 | 321 | 0.01314 | 4.0932e-05 | 100 | 32115 | 2011/2012 | February-2012 | 2 | 2012
27028 | LIGHTNING - KAWAKAWA RD | 2012-02-18 07:45 | 2012-02-18 | 2012-02-18 09:47 | Calculated | 822 | 822 - Fused Link 822 |  | 123SEG822 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 2 | 24431 | 244 | 0.00999 | 8.1863e-05 | 30 | 3664 | 2011/2012 | February-2012 | 2 | 2012
27030 | LIGHTNING - KAWAKAWA RD | 2012-02-18 07:45 | 2012-02-18 | 2012-02-18 10:07 | Calculated | TF3031 | TF3031 - Transformer Fuse: TF3031 |  | No Segment | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 1 | 24431 | 142 | 0.00581 | 4.0932e-05 | 15 | 2132 | 2011/2012 | February-2012 | 2 | 2012
27029 | LIGHTNING - MAIN NORTH RD - FOR NAPINAPI RD | 2012-02-18 09:03 | 2012-02-18 | 2012-02-18 09:50 | Calculated | 717 | 717 - Fused Link 717 |  | 116SEG717 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 7 | 24431 | 330 | 0.01351 | 0.00028652 | 35 | 1650 | 2011/2012 | February-2012 | 2 | 2012
27031 | LV FAULT - MANGANUI RD | 2012-02-18 14:30 | 2012-02-18 | 2012-02-18 16:21 | Calculated | TF1837 | TF1837 - Transformer Fuse: TF1837 |  | 128SEG1612-1613 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 110 | 2 | 24431 | 220 | 0.009 | 8.1863e-05 | 10 | 1101 | 2011/2012 | February-2012 | 2 | 2012
27032 | LIGHTNING - MAROTIRI RD | 2012-02-19 18:22 | 2012-02-19 | 2012-02-19 20:30 | Calculated | TF1127 | TF1127 - Transformer Fuse: TF1127 |  | 123SEG696 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 1 | 24431 | 128 | 0.00524 | 4.0932e-05 | 25 | 3203 | 2011/2012 | February-2012 | 2 | 2012
27033 | MAGPIE - BY MAKOMIKO SUB | 2012-02-20 04:20 | 2012-02-20 | 2012-02-20 09:36 | Calculated | 5867 | 5867 - Recloser with Bypass 5867 |  | 409SEG5761-5867 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 499 | 24431 | 6716 | 0.2749 | 0.020425 | 3302.1667 | 44764 | 2011/2012 | February-2012 | 2 | 2012
27042 | OLD AGE - NGAMOKAI RD | 2012-02-20 09:21 | 2012-02-20 | 2012-02-20 11:51 | Calculated | TF23N4 | TF23N4 - Transformer Fuse: TF23N4 |  | 416SEG5716 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 5 | 24431 | 746 | 0.03053 | 0.00020466 | 30 | 4478 | 2011/2012 | February-2012 | 2 | 2012
27043 | LV FAULT - TE WAITERE RD | 2012-02-20 14:24 | 2012-02-20 | 2012-02-20 14:52 | Calculated | TF2868 | TF2868 - Transformer Fuse: TF2868 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 1 | 24431 | 28 | 0.00115 | 4.0932e-05 | 3 | 84 | 2011/2012 | February-2012 | 2 | 2012
27044 | LIGHTNING - RANGINUI RD | 2012-02-20 17:14 | 2012-02-20 | 2012-02-20 18:45 | Calculated | TF830 | TF830 - Transformer Fuse: TF830 |  | 121SEG412 | Huirimu 121-04 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 2 | 24431 | 182 | 0.00745 | 8.1863e-05 | 15 | 1371 | 2011/2012 | February-2012 | 2 | 2012
27045 | LIGHTNING - MAIN STH RD - TE KUITI | 2012-02-20 18:25 | 2012-02-20 | 2012-02-20 18:50 | Calculated | TF638 | TF638 - Transformer Fuse: TF638 |  | No Segment | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 1 | 24431 | 25 | 0.00102 | 4.0932e-05 | 50 | 1257 | 2011/2012 | February-2012 | 2 | 2012
27046 | RECLOSER 564 TRIPPED - KIRITIHERE - BY RD JUNCTION | 2012-02-21 06:35 | 2012-02-21 | 2012-02-21 08:12 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 18 | 24431 | 1732 | 0.07089 | 0.00073677 | 140 | 13472 | 2011/2012 | February-2012 | 2 | 2012
27047 | REPLACE HV FUSES AT TX 129 AND TX 673 - WAIPAPA RD | 2012-02-21 07:25 | 2012-02-21 | 2012-02-21 08:42 | Calculated | TF129 | TF129 - Transformer Fuse: TF129 |  | 107SEG250-254 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 3 | 24431 | 232 | 0.0095 | 0.00012279 | 30 | 2325 | 2011/2012 | February-2012 | 2 | 2012
27048 | CHANGING POLES AND XARMS - MOKAUITI FEEDER | 2012-02-21 08:30 | 2012-02-21 | 2012-02-21 16:00 | Calculated | 115TempABS1 | 115TempABS1 - Temp ABS1 115-03 |  | 115SEG1705-1707 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 383 | 136 | 24431 | 17500 | 0.7163 | 0.0055667 | 930.5 | 131565 | 2011/2012 | February-2012 | 2 | 2012
27049 | SECTIONALISOR 5277 TRIPPED - FAUCHELLE RD | 2012-02-21 09:41 | 2012-02-21 | 2012-02-21 11:42 | Calculated | 5277 | 5277 - Sectionaliser with Bypass & Links5277 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 121 | 16 | 24431 | 1938 | 0.07933 | 0.00065491 | 135 | 16359 | 2011/2012 | February-2012 | 2 | 2012
27051 | FIT NEW HV FUSES AT TO FOR TX 1480 - MAIHIIHI FEEDER | 2012-02-21 09:45 | 2012-02-21 | 2012-02-21 11:41 | Calculated | 335 | 335 - Air Break Switch 335 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 116 | 33 | 24431 | 3832 | 0.15685 | 0.0013507 | 260 | 30194 | 2011/2012 | February-2012 | 2 | 2012
27052 | REPLACE HV FUSE AT TX 09R32 - PAREROHI GR | 2012-02-21 11:01 | 2012-02-21 | 2012-02-21 13:39 | Calculated | TF9R32 | TF9R32 - Transformer Fuse: TF9R32 |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 3 | 24431 | 474 | 0.0194 | 0.00012279 | 15 | 2371 | 2011/2012 | February-2012 | 2 | 2012
27055 | LIGHTNING - HAUHANGAROA - WEST OF | 2012-02-22 08:49 | 2012-02-22 | 2012-02-22 11:24 | Calculated | 5177 | 5177 - Air Break Switch 5177 |  | 426SEG5177 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 154 | 1 | 24431 | 154 | 0.0063 | 4.0932e-05 | 5 | 772 | 2011/2012 | February-2012 | 2 | 2012
27057 | REPLACING POLES AND XARMS - MOKAU FEEDER | 2012-02-22 09:33 | 2012-02-22 | 2012-02-22 15:07 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 334 | 27 | 24431 | 9022 | 0.36928 | 0.0011052 | 165 | 55134 | 2011/2012 | February-2012 | 2 | 2012
27058 | BROKEN DDO AT TX 10K05 - KAWAUTAHI RD | 2012-02-22 10:58 | 2012-02-22 | 2012-02-22 14:02 | Calculated | 5884 | 5884 - Recloser 5884 |  | 409SEG5884-5403 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 184 | 30 | 24431 | 5524 | 0.22611 | 0.0012279 | 225 | 41433 | 2011/2012 | February-2012 | 2 | 2012
27059 | JUMPER OFF AT ABS 342 - MANGAORONGO RD - BY KING'S | 2012-02-22 18:30 | 2012-02-22 | 2012-02-22 21:56 | Calculated | 127 | 127 - Circuit Breaker 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 601 | 24431 | 6878 | 0.28153 | 0.0246 | 6274.75 | 71930 | 2011/2012 | February-2012 | 2 | 2012
27060 | BIRD - WAITUHI RD | 2012-02-22 18:50 | 2012-02-22 | 2012-02-22 19:41 | Calculated | TF7J23 | TF7J23 - Transformer Fuse: TF7J23 |  | 402SEG5596-5930 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 51 | 1 | 24431 | 51 | 0.00209 | 4.0932e-05 | 15 | 767 | 2011/2012 | February-2012 | 2 | 2012
27061 | MELTED MAGNAFIX UNIT - SOLDIERS RD | 2012-02-22 20:25 | 2012-02-22 | 2012-02-22 20:34 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG5949RET | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 2 | 24431 | 18 | 0.00074 | 8.1863e-05 | 65 | 594 | 2011/2012 | February-2012 | 2 | 2012
27062 | LINE DOWN - ROTTEN CONDUCT - TONGAPORUTU EW SUB | 2012-02-22 20:56 | 2012-02-22 | 2012-02-23 01:30 | Calculated | 1627 | 1627 - Recloser with Incoming Link1627 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 273 | 9 | 24431 | 1927 | 0.07888 | 0.00036838 | 80 | 17205 | 2011/2012 | February-2012 | 2 | 2012
27063 | LINE DOWN AT POLE 399/45 - OKAU - EW SUB | 2012-02-23 05:41 | 2012-02-23 | 2012-02-23 12:04 | Calculated | 1630 | 1630 - Recloser 1630 |  | No Segment | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 383 | 46 | 24431 | 12505 | 0.51185 | 0.0018829 | 325.5 | 90101 | 2011/2012 | February-2012 | 2 | 2012
27064 | LIGHTNING - CLIFTON RD | 2012-02-23 08:34 | 2012-02-23 | 2012-02-23 12:42 | Calculated | TF2196 | TF2196 - Transformer Fuse: TF2196 |  | No Segment | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 247 | 2 | 24431 | 495 | 0.02026 | 8.1863e-05 | 15 | 3717 | 2011/2012 | February-2012 | 2 | 2012
27065 | SECTIONALISOR 5511 TRIPPED - MAKINO RD | 2012-02-23 09:23 | 2012-02-23 | 2012-02-23 14:38 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | 410SEG5511-5517 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 315 | 29 | 24431 | 9142 | 0.3742 | 0.001187 | 183.5 | 57851 | 2011/2012 | February-2012 | 2 | 2012
27066 | REPLACE POLE AND XARM - MOKAU FEEDER | 2012-02-23 09:35 | 2012-02-23 | 2012-02-23 13:33 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 238 | 27 | 24431 | 6432 | 0.26327 | 0.0011052 | 165 | 39308 | 2011/2012 | February-2012 | 2 | 2012
27067 | POSSUM - WAIHI EW SUB | 2012-02-23 22:31 | 2012-02-23 | 2012-02-24 00:27 | Calculated | 5899 | 5899 - Fused Link 5899 |  | 406SEG09R27-5891 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 49 | 24431 | 5698 | 0.23323 | 0.0020056 | 215 | 25004 | 2011/2012 | February-2012 | 2 | 2012
27069 | REPLACE HV FUSE AT TX 08J04 - MIRO ST | 2012-02-24 08:35 | 2012-02-24 | 2012-02-24 09:14 | Calculated | TF8J4 | TF8J4 - Transformer Fuse: TF8J4 |  | No Segment | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 46 | 24431 | 1802 | 0.07376 | 0.0018829 | 100 | 3918 | 2011/2012 | February-2012 | 2 | 2012
27070 | FUSE PULLED APART - PUKEATUA RD | 2012-02-24 09:17 | 2012-02-24 | 2012-02-24 10:36 | Calculated | TF12H07 | TF12H07 - Transformer Fuse: TF12H07 |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 78 | 1 | 24431 | 78 | 0.00319 | 4.0932e-05 | 15 | 1172 | 2011/2012 | February-2012 | 2 | 2012
27072 | REPLACEING POLES AND XARMS - MOKAU FEEDER | 2012-02-24 09:37 | 2012-02-24 | 2012-02-24 14:10 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 273 | 27 | 24431 | 7374 | 0.30183 | 0.0011052 | 165 | 45066 | 2011/2012 | February-2012 | 2 | 2012
27073 | LV LINE DOWN - NEWMAN RD | 2012-02-24 18:00 | 2012-02-24 | 2012-02-24 19:10 | Calculated | TF697 | TF697 - Transformer Fuse: TF697 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 3 | 24431 | 210 | 0.0086 | 0.00012279 | 30 | 2106 | 2011/2012 | February-2012 | 2 | 2012
27074 | TRIPPING ON OVER CURRENT - HANGATIKI | 2012-02-25 15:52 | 2012-02-25 | 2012-02-25 15:55 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24431 |  | 0 | 0 |  |  | 2011/2012 | February-2012 | 2 | 2012
27075 | REPLACE HV FUSE AT TX 7J17 - WAITUHI RD | 2012-02-26 08:46 | 2012-02-26 | 2012-02-26 10:05 | Calculated | TF7J17 | TF7J17 - Transformer Fuse: TF7J17 |  | 402SEG5596-5930 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 79 | 1 | 24431 | 79 | 0.00323 | 4.0932e-05 | 15 | 1187 | 2011/2012 | February-2012 | 2 | 2012
27076 | BROKEN BINDER AT POLE 8 - POIHIPI RD | 2012-02-26 09:16 | 2012-02-26 | 2012-02-26 10:09 | Calculated | 433 | 433 - Fused Link 433 |  | 124SEG433 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 17 | 24431 | 903 | 0.03696 | 0.00069584 | 125 | 6641 | 2011/2012 | February-2012 | 2 | 2012
27077 | JUMPER OFF AT TX 1042 - OLD TE KUITI RD | 2012-02-26 16:28 | 2012-02-26 | 2012-02-26 17:25 | Calculated | TF1042 | TF1042 - Transformer Fuse: TF1042 |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 3 | 24431 | 171 | 0.007 | 0.00012279 | 50 | 2857 | 2011/2012 | February-2012 | 2 | 2012
27080 | RECLOSER 5455 TRIPPED - TATU SUB | 2012-02-27 07:47 | 2012-02-27 | 2012-02-27 13:01 | Calculated | 5455 | 5455 - Recloser with Bypass & Links 5455 |  | 413SEG5454-5455 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 314 | 24 | 24431 | 7539 | 0.30858 | 0.00098236 | 153 | 48064 | 2011/2012 | February-2012 | 2 | 2012
27081 | TREE CUTTING - CAVES FEEDER | 2012-02-27 09:07 | 2012-02-27 | 2012-02-27 15:25 | Calculated | 552 | 552 - Air Break Switch 552 |  | 101SEG552-290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 378 | 13 | 24431 | 4916 | 0.20122 | 0.00053211 | 95 | 35927 | 2011/2012 | February-2012 | 2 | 2012
27082 | TIROHANGA FEEDER RENEWAL PROJECT - TIROHANGA FEEDER | 2012-02-27 09:13 | 2012-02-27 | 2012-02-27 15:18 | Calculated | 301 | 301 - Fused Link 301 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 364 | 13 | 24431 | 4741 | 0.19406 | 0.00053211 | 360 | 131316 | 2011/2012 | February-2012 | 2 | 2012
27089 | MAGPIE AT TX 10R17 - HIRANGI SUB | 2012-02-28 07:10 | 2012-02-28 | 2012-02-28 18:48 | Calculated | 5519 | 5519 - Circuit Breaker with Bypass & Links 5519 |  | No Segment | Lake Taupo 606-01 | Urban A | Lake Taupo 33 | Direct from Tokaanu Supply |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 399 | 22 | 24431 | 8763 | 0.35868 | 0.0009005 | 87.5 | 34854 | 2011/2012 | February-2012 | 2 | 2012
27091 | REPLACE ROTTEN POLE 1131086 - MAHOENUI FEEDER | 2012-02-28 08:35 | 2012-02-28 | 2012-02-28 15:41 | Calculated | 1766 | 1766 - Solid Link 1766 |  | 113SEG1548-1526 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 385 | 149 | 24431 | 4109 | 0.16819 | 0.0060988 | 970.5 | 28437 | 2011/2012 | February-2012 | 2 | 2012
27090 | FEEDER UPGRADE - OHURA | 2012-02-28 08:49 | 2012-02-28 | 2012-02-28 18:06 | Calculated | 5298 | 5298 - Air Break Switch 5298 |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 490 | 84 | 24431 | 4068 | 0.16651 | 0.0034383 | 613 | 55978 | 2011/2012 | February-2012 | 2 | 2012
27092 | TIROHANGA FEEDER RENEWAL PROJECT - TIROHANGA FEEDER | 2012-02-28 09:02 | 2012-02-28 | 2012-02-28 15:37 | Calculated | 301 | 301 - Fused Link 301 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 394 | 13 | 24431 | 5131 | 0.21002 | 0.00053211 | 360 | 142116 | 2011/2012 | February-2012 | 2 | 2012
27093 | LV WRAPPED - AHUROA RD | 2012-02-28 09:26 | 2012-02-28 | 2012-02-28 11:52 | Calculated | TF5 | TF5 - Transformer Fuse: TF5 |  | No Segment | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 5 | 24431 | 731 | 0.02992 | 0.00020466 | 30 | 4386 | 2011/2012 | February-2012 | 2 | 2012
27094 | LV WRAPPED - OTEWA | 2012-02-28 12:01 | 2012-02-28 | 2012-02-28 14:43 | Calculated | TF643 | TF643 - Transformer Fuse: TF643 |  | No Segment | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 3 | 24431 | 486 | 0.01989 | 0.00012279 | 25 | 4055 | 2011/2012 | February-2012 | 2 | 2012
27095 | REPLACE FUSE LINK 438 - OKAMA RD - FOR OKAMA BLOCK | 2012-02-28 17:24 | 2012-02-28 | 2012-02-29 12:22 | Calculated | 438 | 438 - Fused Link 438 |  | 129SEG438 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1138 | 6 | 24431 | 6829 | 0.27952 | 0.00024559 | 60 | 68292 | 2011/2012 | February-2012 | 2 | 2012
27096 | FEEDER UPGRADE - OHURA FEEDER | 2012-02-29 08:11 | 2012-02-29 | 2012-02-29 16:07 | Calculated | 5298 | 5298 - Air Break Switch 5298 |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 410 | 84 | 24431 | 1856 | 0.07597 | 0.0034383 | 613 | 37946 | 2011/2012 | February-2012 | 2 | 2012
27097 | MAGPIE - PAPAROA RD | 2012-02-29 12:01 | 2012-02-29 | 2012-02-29 12:29 | Calculated | TF9H4 | TF9H4 - Transformer Fuse: TF9H4 |  | No Segment | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 28 | 2 | 24431 | 56 | 0.00229 | 8.1863e-05 | 15 | 422 | 2011/2012 | February-2012 | 2 | 2012
27098 | WIND - OCB 796 AND 242 TRIPPED ON | 2012-03-01 08:08 | 2012-03-01 | 2012-03-01 08:11 | Calculated | 796 | 796 - Circuit Breaker 796 |  | 301SEG1418-796 | Taharoa A 301-02 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24586 |  | 0 | 0 |  |  | 2011/2012 | March-2012 | 3 | 2012
27099 | REPLACE POLES AND XARMS - WHAREPAPA | 2012-03-01 09:08 | 2012-03-01 | 2012-03-01 15:11 | Calculated | 379 | 379 - Air Break Switch 379 |  | 122SEG379 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 362 | 9 | 24586 | 3259 | 0.13256 | 0.00036606 | 60 | 21729 | 2011/2012 | March-2012 | 3 | 2012
27100 | TIROHANGA FEEDER RENEWAL PROJECT - TIROHANGA FEEDER | 2012-03-01 09:12 | 2012-03-01 | 2012-03-01 15:21 | Calculated | 1788 | 1788 - Fused Link 1788 |  | 129SEG1788-1780 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 368 | 6 | 24586 | 2211 | 0.08993 | 0.00024404 | 95 | 35017 | 2011/2012 | March-2012 | 3 | 2012
27101 | FAULTY TX 1265 - OTAKE RD | 2012-03-01 10:07 | 2012-03-01 | 2012-03-01 12:00 | Calculated | TF1265 | TF1265 - Transformer Fuse: TF1265 |  | 123SEG467 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 3 | 24586 | 339 | 0.01379 | 0.00012202 | 5 | 565 | 2011/2012 | March-2012 | 3 | 2012
27103 | WIND - OMARU RD - FOR OMARU RD | 2012-03-01 13:45 | 2012-03-01 | 2012-03-01 14:48 | Calculated | 1729 | 1729 - Fused Link 1729 |  | 117SEG1729 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 63 | 10 | 24586 | 631 | 0.02567 | 0.00040674 | 65 | 4105 | 2011/2012 | March-2012 | 3 | 2012
27104 | WIND - WAITOMO VALLEY RD | 2012-03-01 15:00 | 2012-03-01 | 2012-03-01 15:53 | Calculated | TF526 | TF526 - Transformer Fuse: TF526 |  | 112SEG331-355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 2 | 24586 | 106 | 0.00431 | 8.1347e-05 | 25 | 1328 | 2011/2012 | March-2012 | 3 | 2012
27105 | BROKEN XARM AT POLE 70/30 - ONGARUE BACK RD | 2012-03-01 16:05 | 2012-03-01 | 2012-03-01 18:04 | Calculated | 5446 | 5446 - Sectionaliser with Bypass & Links 5446 |  | 402SEG5343-5446 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 88 | 40 | 24586 | 1883 | 0.07659 | 0.0016269 | 280.5 | 13132 | 2011/2012 | March-2012 | 3 | 2012
27106 | JUMPER OFF ABS 253 - HANGATIKI - IN FRONT OF CAVE | 2012-03-01 18:33 | 2012-03-01 | 2012-03-01 18:44 | Calculated | 253 | 253 - Air Break Switch 253 |  | 101SEG253-295 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 44 | 24586 | 447 | 0.01818 | 0.0017896 | 300 | 3049 | 2011/2012 | March-2012 | 3 | 2012
27107 | BRANCH ON LINE - HAUTU VILLAGE | 2012-03-01 21:33 | 2012-03-01 | 2012-03-01 23:45 | Calculated | 6337 | 6337 - Circuit Breaker Waiotaka 11kV 6337 |  | 427SEG6337-6549 | 511-01 Waiotaka | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 14 | 24586 | 1228 | 0.04995 | 0.00056943 | 180 | 19977 | 2011/2012 | March-2012 | 3 | 2012
27108 | JUMPER OFF LINK 1617 - PIOI STATION - SPUR BY ESTUARY | 2012-03-01 22:11 | 2012-03-01 | 2012-03-01 22:58 | Calculated | 1617 | 1617 - Fused Link 1617 |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 2 | 24586 | 93 | 0.00378 | 8.1347e-05 | 30 | 1404 | 2011/2012 | March-2012 | 3 | 2012
27146 | REPLACE ABS 425 - ALSO REPLACE XARMS AT POLES 1210109 n 1210110 - HUIRIMU FEEDER | 2012-03-02 07:27 | 2012-03-02 | 2012-03-02 14:04 | Calculated | 748 | 748 - Air Break Switch 748 |  | 121SEG748-418 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 16 | 24586 | 4210 | 0.17124 | 0.00065078 | 85 | 22367 | 2011/2012 | March-2012 | 3 | 2012
27144 | FEEDER UPGRADE - OHURA FEEDER | 2012-03-02 08:05 | 2012-03-02 | 2012-03-02 15:43 | Calculated | 5298 | 5298 - Air Break Switch 5298 |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 360 | 84 | 24586 | 1713 | 0.06967 | 0.0034166 | 613 | 33768 | 2011/2012 | March-2012 | 3 | 2012
27109 | TIROHANGA FEEDER RENEWAL PROJECT - TIROHANGA FEEDER | 2012-03-02 09:05 | 2012-03-02 | 2012-03-02 12:54 | Calculated | 1788 | 1788 - Fused Link 1788 |  | 129SEG1788-1780 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 228 | 6 | 24586 | 1371 | 0.05576 | 0.00024404 | 95 | 21717 | 2011/2012 | March-2012 | 3 | 2012
27110 | LOWER TAP AT TX 3345 - NGAKEPE RD | 2012-03-02 11:18 | 2012-03-02 | 2012-03-02 11:35 | Calculated | TF3345 | TF3345 - Transformer Fusa 3345 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 1 | 24586 | 17 | 0.00069 | 4.0674e-05 | 75 | 1310 | 2011/2012 | March-2012 | 3 | 2012
27145 | BROKEN SUSPENSION INSULATOR - PUNGA VALLEY RD | 2012-03-02 16:14 | 2012-03-02 | 2012-03-02 21:50 | Calculated | 5218 | 5218 - Recloser with Bypass 5218 |  | 408SEG5275-5218 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 335 | 73 | 24586 | 17134 | 0.6969 | 0.0029692 | 488 | 116663 | 2011/2012 | March-2012 | 3 | 2012
27111 | WIND - KIKUMUTU RD | 2012-03-02 16:17 | 2012-03-02 | 2012-03-02 21:09 | Calculated | TF9I5 | TF9I5 - Transformer Fuse: TF9I5 |  | No Segment | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 292 | 1 | 24586 | 292 | 0.01188 | 4.0674e-05 | 15 | 4385 | 2011/2012 | March-2012 | 3 | 2012
27112 | WIND - Waikawau Rd - Onetai Station | 2012-03-02 17:21 | 2012-03-02 | 2012-03-02 19:56 | Calculated | 1612 | 1612 - Sectionaliser with Bypass & Links 1612 |  | 128SEG1611-1612 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 155 | 41 | 24586 | 6359 | 0.25864 | 0.0016676 | 310 | 48086 | 2011/2012 | March-2012 | 3 | 2012
27114 | EXTREME WIND - RATA ST | 2012-03-02 23:20 | 2012-03-02 | 2012-03-03 06:37 | Calculated | TF644 | TF644 - Transformer Fuse: TF644 |  | 108SEG501-211 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 437 | 39 | 24586 | 17064 | 0.69405 | 0.0015863 | 200 | 87509 | 2011/2012 | March-2012 | 3 | 2012
27113 | WIND - OC Y AND B - Mangaorongo Rd - By King's | 2012-03-02 23:37 | 2012-03-02 | 2012-03-02 23:39 | Calculated | 127 | 127 - Circuit Breaker 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 601 | 24586 | 1312 | 0.05336 | 0.024445 | 6274.75 | 13699 | 2011/2012 | March-2012 | 3 | 2012
27224 | WIRE OFF INSULATOR | 2012-03-03 00:01 | 2012-03-03 | 2012-03-04 13:31 | Calculated | 1335 | 1335 - Sectionaliser 1335 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1292 | 17 | 24586 | 5467 | 0.22236 | 0.00069145 | 148 | 41650 | 2011/2012 | March-2012 | 3 | 2012
27186 | LINE DOWN POLE 148-149 -SCOWNS RD | 2012-03-03 00:21 | 2012-03-03 | 2012-03-03 07:43 | Calculated | 127 | 127 - Circuit Breaker 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 442 | 601 | 24586 | 53600 | 2.1801 | 0.024445 | 6274.75 | 543745 | 2011/2012 | March-2012 | 3 | 2012
27187 | LINE DOWN AT POLE 91 - SH 49 OHUTU | 2012-03-03 03:05 | 2012-03-03 | 2012-03-03 08:56 | Calculated | 5677 | 5677 - Recloser with Bypass 5677 |  | 416SEG5677-5681 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 351 | 220 | 24586 | 76908 | 3.1281 | 0.0089482 | 2129 | 745109 | 2011/2012 | March-2012 | 3 | 2012
27188 | JUMPER OFF ABS 5648 AND POLE DOWN AT TX 8I2- BOROUGH SUB | 2012-03-03 03:14 | 2012-03-03 | 2012-03-03 08:01 | Calculated | 5955 | 5955 - Circuit Breaker Northern 5955 |  | No Segment | 508-01 Borough | Rural B | Northern | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 286 | 1241 | 24586 | 113195 | 4.604 | 0.050476 | 7773.108 | 721825 | 2011/2012 | March-2012 | 3 | 2012
27216 | EXTREME WIND - LINE DOWN - RANGITOTO | 2012-03-03 03:29 | 2012-03-03 | 2012-03-04 16:22 | Calculated | 104 | 104 - Circuit Breaker Rangitoto 104 |  | No Segment | 206-01 Waitete | Urban A | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 614 | 740 | 24586 | 70228 | 2.8564 | 0.030098 | 5644.5 | 436410 | 2011/2012 | March-2012 | 3 | 2012
27190 | EXTREME WIND - WHAKAMARU RD | 2012-03-03 04:22 | 2012-03-03 | 2012-03-03 05:14 | Calculated | 507 | 507 - Fused Link 507 |  | 120SEG507-530 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 2 | 24586 | 104 | 0.00423 | 8.1347e-05 | 300 | 15645 | 2011/2012 | March-2012 | 3 | 2012
27191 | EXTREME WIND - RIVER RD - TOKIRIMA | 2012-03-03 06:05 | 2012-03-03 | 2012-03-03 08:52 | Calculated | TF4059 | TF4059 - Transformer Fuse: TF4059 |  | No Segment | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 167 | 2 | 24586 | 334 | 0.01358 | 8.1347e-05 | 65 | 10865 | 2011/2012 | March-2012 | 3 | 2012
27192 | POLE DOWN - PARAHEKA RD - NEAR ARIA TOWNSHIP | 2012-03-03 06:30 | 2012-03-03 | 2012-03-03 10:07 | Calculated | 1108 | 1108 - Recloser with Bypass 1108 |  | 114SEG1108-1102 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 61 | 24586 | 13249 | 0.53888 | 0.0024811 | 403 | 87531 | 2011/2012 | March-2012 | 3 | 2012
27193 | EXTREME WIND - TE KUMI RD | 2012-03-03 06:58 | 2012-03-03 | 2012-03-03 08:37 | Calculated | TF441 | TF441 - Transformer Fuse: TF441 |  | No Segment | Oparure 107-03 | Rural C | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 8 | 24586 | 786 | 0.03197 | 0.00032539 | 50 | 4913 | 2011/2012 | March-2012 | 3 | 2012
27119 | EXTREME WIND - TREES - FAULTY TX - BLUCKS RD | 2012-03-03 07:34 | 2012-03-03 | 2012-03-03 20:11 | Calculated | TF228 | TF228 - Transformer Fuse: TF228 |  | No Segment | Maihiihi 111-02 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 757 | 8 | 24586 | 6058 | 0.2464 | 0.00032539 | 50 | 37863 | 2011/2012 | March-2012 | 3 | 2012
27203 | EXTREME WIND - BLUCKS RD | 2012-03-03 07:35 | 2012-03-03 | 2012-03-03 15:20 | Calculated | 325 | 325 - Fused Link 325 |  | 111SEG325 | Maihiihi 111-02 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 465 | 28 | 24586 | 13026 | 0.52981 | 0.0011389 | 130 | 60480 | 2011/2012 | March-2012 | 3 | 2012
27204 | EXTREME WIND - PAEWHENUA RD | 2012-03-03 08:24 | 2012-03-03 | 2012-03-03 16:21 | Calculated | TF282 | TF282 - Transformer Fuse: TF282 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 477 | 4 | 24586 | 1908 | 0.07761 | 0.00016269 | 30 | 14314 | 2011/2012 | March-2012 | 3 | 2012
27120 | EXTREME WIND - REPLACE LINK 471 - Poihipi Rd - Corner Wereta Rd | 2012-03-03 08:38 | 2012-03-03 | 2012-03-03 10:47 | Calculated | 471 | 471 - Fused Link 471 |  | 123SEG471 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 10 | 24586 | 1292 | 0.05255 | 0.00040674 | 85 | 10983 | 2011/2012 | March-2012 | 3 | 2012
27195 | REPLACE LINK 471 - POIHIPI RD - CORNER WERETA | 2012-03-03 08:38 | 2012-03-03 | 2012-03-03 10:46 | Calculated | 471 | 471 - Fused Link 471 |  | 123SEG471 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 10 | 24586 | 1281 | 0.0521 | 0.00040674 | 85 | 10895 | 2011/2012 | March-2012 | 3 | 2012
27196 | EXTREME WIND EF - KURATAU SUB | 2012-03-03 08:41 | 2012-03-03 | 2012-03-03 12:42 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 241 | 4 | 24586 | 965 | 0.03925 | 0.00016269 | 450 | 108562 | 2011/2012 | March-2012 | 3 | 2012
27205 | EXTREME WIND - SH 3 - BODDIE'S HILL | 2012-03-03 08:42 | 2012-03-03 | 2012-03-03 13:31 | Calculated | 1538 | 1538 - Fused Link 1538 |  | 113SEG1538 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 289 | 2 | 24586 | 578 | 0.02351 | 8.1347e-05 | 30 | 8675 | 2011/2012 | March-2012 | 3 | 2012
27122 | OCB 796 AND 242 TRIPPED - EXTREME WIND - TAHAROA A | 2012-03-03 08:58 | 2012-03-03 | 2012-03-03 08:59 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24586 |  | 0 | 0 |  |  | 2011/2012 | March-2012 | 3 | 2012
27206 | EXTREME WIND - WAITOMO CAVES RD | 2012-03-03 09:12 | 2012-03-03 | 2012-03-03 14:55 | Calculated | TF85 | TF85 - Transformer Fuse: TF85 |  | 101SEG679-267 | Caves 101-06 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 343 | 9 | 24586 | 3088 | 0.1256 | 0.00036606 | 30 | 10296 | 2011/2012 | March-2012 | 3 | 2012
27217 | EXTREME WIND - LINE DOWN - RAURIMU FEEDER | 2012-03-03 09:38 | 2012-03-03 | 2012-03-04 15:32 | Calculated | 5490 | 5490 - Recloser with Bypass 5490 |  | 410SEG5490-5438 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1793 | 73 | 24586 | 34159 | 1.3894 | 0.0029692 | 433 | 178088 | 2011/2012 | March-2012 | 3 | 2012
27214 | EXTREME WIND - MANGAHAUHAU VALLEY RD | 2012-03-03 09:42 | 2012-03-03 | 2012-03-03 20:19 | Calculated | 5676 | 5676 - Fused Link 5676 |  | 416SEG5676 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 637 | 5 | 24586 | 3186 | 0.12959 | 0.00020337 | 55 | 35046 | 2011/2012 | March-2012 | 3 | 2012
27198 | FAULTY TX 69 - GADSBY RD | 2012-03-03 09:54 | 2012-03-03 | 2012-03-03 13:39 | Calculated | TF69 | TF69 - Transformer Fuse: TF69 |  | No Segment | Oparure 107-01 | Urban A | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 224 | 8 | 24586 | 1793 | 0.07293 | 0.00032539 | 30 | 6724 | 2011/2012 | March-2012 | 3 | 2012
27207 | EXTREME WIND - SH 3 - PASTORAL HOLDINGS | 2012-03-03 10:08 | 2012-03-03 | 2012-03-03 12:51 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 8 | 24586 | 1305 | 0.05308 | 0.00032539 | 95 | 15503 | 2011/2012 | March-2012 | 3 | 2012
27199 | JUMPER OFF AT TX 2619 - HAUTURU NORTH RD - BY SCOTT'S | 2012-03-03 10:15 | 2012-03-03 | 2012-03-03 11:19 | Calculated | 290 | 290 - Air Break Switch 290 |  | 101SEG290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 8 | 24586 | 513 | 0.02087 | 0.00032539 | 65 | 4169 | 2011/2012 | March-2012 | 3 | 2012
27219 | LINE DOWN - ONGARUE RD | 2012-03-03 10:30 | 2012-03-03 | 2012-03-03 14:32 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 242 | 30 | 24586 | 4025 | 0.16371 | 0.0012202 | 232.5 | 31467 | 2011/2012 | March-2012 | 3 | 2012
27225 | TREE THROUGH LINE AT TX 15J02 | 2012-03-03 10:32 | 2012-03-03 | 2012-03-04 13:19 | Calculated | 5806 | 5806 - Recloser with Bypass 5806 |  | 410SEG5806-5793 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1589 | 68 | 24586 | 52920 | 2.1524 | 0.0027658 | 399 | 302344 | 2011/2012 | March-2012 | 3 | 2012
27124 | EXTREME WIND - LV DOWN - PUKETAPU CRES | 2012-03-03 10:47 | 2012-03-03 | 2012-03-03 14:25 | Calculated | TF8I3 | TF8I3 - Transformer Fuse: TF8I3 |  | 402SEGA4.6-5351 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 70 | 24586 | 15220 | 0.61905 | 0.0028471 | 295.7746 | 64311 | 2011/2012 | March-2012 | 3 | 2012
27179 | EXTREME WIND - MANGAHAUHAU VALLEY RD | 2012-03-03 10:53 | 2012-03-03 | 2012-03-04 10:15 | Calculated | 5717 | 5717 - Fused Link 5717 |  | 416SEG5717 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1402 | 5 | 24586 | 7011 | 0.28516 | 0.00020337 | 45 | 63099 | 2011/2012 | March-2012 | 3 | 2012
27220 | EXTREME WIND - LINE DOWN AND POLE DOWN - TANGIWIA FEEDER | 2012-03-03 10:59 | 2012-03-03 | 2012-03-04 12:33 | Calculated | 5684 | 5684 - Recloser 5684 |  | 416SEG5721-5684 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1534 | 66 | 24586 | 27115 | 1.1029 | 0.0026845 | 632.5 | 231526 | 2011/2012 | March-2012 | 3 | 2012
27201 | EXTREME WIND - WAITUHI RD | 2012-03-03 11:07 | 2012-03-03 | 2012-03-03 11:48 | Calculated | 5485 | 5485 - Fused Link 5485 |  | 408SEG5485-5791 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 20 | 24586 | 802 | 0.03262 | 0.00081347 | 160 | 6418 | 2011/2012 | March-2012 | 3 | 2012
27202 | LINE DOWN - MANGATEITEI RD | 2012-03-03 11:30 | 2012-03-03 | 2012-03-03 12:59 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 27 | 24586 | 2406 | 0.09786 | 0.0010982 | 281.4286 | 25079 | 2011/2012 | March-2012 | 3 | 2012
27208 | EXTREME WIND - MAROKOPA RD | 2012-03-03 12:08 | 2012-03-03 | 2012-03-03 12:26 | Calculated | TF696 | TF696 - Transformer Fuse: TF696 |  | No Segment | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 3 | 24586 | 54 | 0.0022 | 0.00012202 | 30 | 547 | 2011/2012 | March-2012 | 3 | 2012
27222 | JUMMPER OFF AT ABS 342 - MANGAORONGO RD | 2012-03-03 12:22 | 2012-03-03 | 2012-03-03 14:06 | Calculated | 127 | 127 - Circuit Breaker 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 121 | 24586 | 7157 | 0.2911 | 0.0049215 | 1182.5 | 69944 | 2011/2012 | March-2012 | 3 | 2012
27209 | LINE DOWN - OMARU RD | 2012-03-03 12:29 | 2012-03-03 | 2012-03-03 13:17 | Calculated | 1729 | 1729 - Fused Link 1729 |  | 117SEG1729 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 48 | 10 | 24586 | 482 | 0.0196 | 0.00040674 | 65 | 3135 | 2011/2012 | March-2012 | 3 | 2012
27210 | EXTREME WIND - KAHOREKAU RD | 2012-03-03 13:07 | 2012-03-03 | 2012-03-03 16:48 | Calculated | TF870 | TF870 - Transformer Fuse: TF870 |  | No Segment | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 4 | 24586 | 884 | 0.03596 | 0.00016269 | 25 | 5528 | 2011/2012 | March-2012 | 3 | 2012
27221 | LINE DOWN - TIHOI FEEDER | 2012-03-03 14:16 | 2012-03-03 | 2012-03-03 17:53 | Calculated | CB2 | CB2 - Circuit Breaker Tihoi Feeder CB2 |  | No Segment | 212-01 Marotiri | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 200 | 209 | 24586 | 33813 | 1.3753 | 0.0085008 | 2165.5 | 351669 | 2011/2012 | March-2012 | 3 | 2012
27223 | JUMPER OFF AT LINK 1538 - SH 3 AT MURPHY'S | 2012-03-03 14:29 | 2012-03-03 | 2012-03-03 16:15 | Calculated | 1339 | 1339 - Air Break Switch 1339 |  | 113SEG1339-1511 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 72 | 24586 | 770 | 0.03132 | 0.0029285 | 538 | 8837 | 2011/2012 | March-2012 | 3 | 2012
27211 | EXTREME WIND - LV FAULT - MANGAORONGO RD | 2012-03-03 14:44 | 2012-03-03 | 2012-03-03 22:25 | Calculated | TF1860 | TF1860 - Transformer Fuse: TF1860 |  | No Segment | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 461 | 2 | 24586 | 922 | 0.0375 | 8.1347e-05 | 15 | 6917 | 2011/2012 | March-2012 | 3 | 2012
27212 | EXTREME WIND - LV FAULT - FAULTY TX - WAITOMO VALLEY RD | 2012-03-03 16:03 | 2012-03-03 | 2012-03-03 21:05 | Calculated | TF214 | TF214 - Transformer Fuse: TF214 |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 302 | 5 | 24586 | 1510 | 0.06142 | 0.00020337 | 30 | 9065 | 2011/2012 | March-2012 | 3 | 2012
27213 | EXTREME WIND - LINE DOWN - MANGAORONGO RD | 2012-03-03 16:08 | 2012-03-03 | 2012-03-03 18:05 | Calculated | 1347 | 1347 - Sectionaliser 1347 |  | 113SEG1347 | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 117 | 11 | 24586 | 1294 | 0.05263 | 0.00044741 | 58 | 6824 | 2011/2012 | March-2012 | 3 | 2012
27215 | LV LINE DOWN - WHATAURI RD | 2012-03-03 17:43 | 2012-03-03 | 2012-03-03 19:17 | Calculated | TF882 | TF882 - Transformer Fuse: TF882 |  | No Segment | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 5 | 24586 | 470 | 0.01912 | 0.00020337 | 30 | 2825 | 2011/2012 | March-2012 | 3 | 2012
27180 | EXTREME WIND - MAROTIRI RD | 2012-03-04 08:01 | 2012-03-04 | 2012-03-04 09:06 | Calculated | TF750 | TF750 - Transformer Fuse: TF750 |  | 123SEG1266-441 | Mokai 123-00 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 3 | 24586 | 195 | 0.00793 | 0.00012202 | 30 | 1953 | 2011/2012 | March-2012 | 3 | 2012
27181 | EXTREME WIND - SH 3 - PAEMAKO | 2012-03-04 08:14 | 2012-03-04 | 2012-03-04 10:20 | Calculated | TF2358 | TF2358 - Transformer Fuse: TF2358 |  | No Segment | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 1 | 24586 | 126 | 0.00512 | 4.0674e-05 | 15 | 1892 | 2011/2012 | March-2012 | 3 | 2012
27182 | XARM VERTICAL - TIROHANGA RD | 2012-03-04 12:31 | 2012-03-04 | 2012-03-04 13:11 | Calculated | 460 | 460 - Load Break Switch 460 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 17 | 24586 | 683 | 0.02778 | 0.00069145 | 243 | 9764 | 2011/2012 | March-2012 | 3 | 2012
27183 | LV FAULT - TAUMATAMAIRE RD | 2012-03-04 16:25 | 2012-03-04 | 2012-03-04 19:13 | Calculated | TF1363 | TF1363 - Transformer Fuse: TF1363 |  | 128SEG1602-1603 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 167 | 1 | 24586 | 167 | 0.00679 | 4.0674e-05 | 10 | 1672 | 2011/2012 | March-2012 | 3 | 2012
27127 | LV LINE DOWN - HENDERSON RD | 2012-03-05 07:40 | 2012-03-05 | 2012-03-05 10:19 | Calculated | TF728 | TF728 - Transformer Fuse: TF728 |  | 120SEG416-479 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 2 | 24586 | 318 | 0.01293 | 8.1347e-05 | 25 | 3982 | 2011/2012 | March-2012 | 3 | 2012
27128 | LV REPAIRS - MANGAORONGO RD | 2012-03-05 10:25 | 2012-03-05 | 2012-03-05 17:00 | Calculated | TF1860 | TF1860 - Transformer Fuse: TF1860 |  | No Segment | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 395 | 2 | 24586 | 790 | 0.03213 | 8.1347e-05 | 15 | 5929 | 2011/2012 | March-2012 | 3 | 2012
27130 | SECTIONALISER 5536 TRIPPED - HINGARAE RD | 2012-03-05 11:07 | 2012-03-05 | 2012-03-05 13:19 | Calculated | 5536 | 5536 - Sectionaliser 5536 |  | 124SEG5536 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 12 | 24586 | 1586 | 0.06451 | 0.00048808 | 77.5 | 10245 | 2011/2012 | March-2012 | 3 | 2012
27131 | LV LINE DOWN - PAERATA RD | 2012-03-05 11:20 | 2012-03-05 | 2012-03-05 12:46 | Calculated | TF776 | TF776 - Transformer Fuse: TF776 |  | 129SEG402-725 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 4 | 24586 | 341 | 0.01387 | 0.00016269 | 25 | 2132 | 2011/2012 | March-2012 | 3 | 2012
27132 | LINE DOWN - SH 49 | 2012-03-05 12:39 | 2012-03-05 | 2012-03-05 14:04 | Calculated | TF21N13 | TF21N13 - Transformer Fuse: TF21N13 |  | 416SEG5700-5709 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 2 | 24586 | 170 | 0.00691 | 8.1347e-05 | 10 | 852 | 2011/2012 | March-2012 | 3 | 2012
27133 | TREE ON LV LINE - MOHAKATINO RD | 2012-03-05 12:43 | 2012-03-05 | 2012-03-05 13:38 | Calculated | TF2162 | TF2162 - Transformer Fuse: TF2162 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 55 | 1 | 24586 | 55 | 0.00224 | 4.0674e-05 | 10 | 551 | 2011/2012 | March-2012 | 3 | 2012
27135 | REPLACE HV FUSE AT TX 1962 - KUMARA RD | 2012-03-05 17:24 | 2012-03-05 | 2012-03-05 18:00 | Calculated | TF1962 | TF1962 - Transformer Fuse: TF1962 |  | 114SEG1108-1102 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 4 | 24586 | 144 | 0.00586 | 0.00016269 | 10 | 361 | 2011/2012 | March-2012 | 3 | 2012
27147 | CHANGE POLES AND XARMS - COAST FEEDER | 2012-03-06 09:43 | 2012-03-06 | 2012-03-06 14:12 | Calculated | 298 | 298 - Fused Link 298 |  | 125SEG298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 9 | 24586 | 2424 | 0.09859 | 0.00036606 | 45 | 12119 | 2011/2012 | March-2012 | 3 | 2012
27136 | BURNING LV RACK - RANFURLY ST | 2012-03-06 11:06 | 2012-03-06 | 2012-03-06 14:03 | Calculated | TF1257 | TF1257 - Transformer Fuse: TF1257 |  | 112SEG300-646 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 1 | 24586 | 177 | 0.0072 | 4.0674e-05 | 300 | 53140 | 2011/2012 | March-2012 | 3 | 2012
27137 | FUSE PULLED APART - OKAUAKA RD | 2012-03-06 12:54 | 2012-03-06 | 2012-03-06 13:43 | Calculated | TF2L1 | TF2L1 - Transformer Fuse: TF2L1 |  | No Segment | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 49 | 3 | 24586 | 147 | 0.00598 | 0.00012202 | 15 | 736 | 2011/2012 | March-2012 | 3 | 2012
27138 | BROKEN LV XARM - HANGATIKI EAST RD | 2012-03-06 16:36 | 2012-03-06 | 2012-03-06 17:56 | Calculated | TF72 | TF72 - Transformer Fuse: TF72 |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 4 | 24586 | 320 | 0.01302 | 0.00016269 | 30 | 2404 | 2011/2012 | March-2012 | 3 | 2012
27148 | REPLACE HV FUSE AT TX 4237 - MILL RD | 2012-03-07 05:33 | 2012-03-07 | 2012-03-07 06:49 | Calculated | TF4237 | TF4237 - Transformer Fuse: TF4237 |  | No Segment | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 76 | 1 | 24586 | 76 | 0.00309 | 4.0674e-05 | 50 | 3808 | 2011/2012 | March-2012 | 3 | 2012
27149 | REPLACE POLES AND XARMS - COAST FEEDER | 2012-03-07 09:11 | 2012-03-07 | 2012-03-07 15:47 | Calculated | 125TempABS2 | 125TempABS2 - Temp ABS2 125-03 |  | 125SEG125TempABS2-281RET | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 350 | 36 | 24586 | 5736 | 0.2333 | 0.0014642 | 390 | 39659 | 2011/2012 | March-2012 | 3 | 2012
27150 | LINE RENEWAL PROJECT - RANGIPO/HAUTU FEEDER | 2012-03-07 09:38 | 2012-03-07 | 2012-03-07 15:06 | Calculated | TF11S10 | TF11S10 - Transformer Fuse: TF11S10 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 13 | 24586 | 4253 | 0.17298 | 0.00052876 | 1537.5 | 503095 | 2011/2012 | March-2012 | 3 | 2012
27167 | FAULTY DDO AT TX 2601- HANGATIKI EAST RD | 2012-03-07 13:38 | 2012-03-07 | 2012-03-07 15:43 | Calculated | TF2601 | TF2601 - Transformer Fuse: TF2601 |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 5 | 24586 | 626 | 0.02546 | 0.00020337 | 50 | 6260 | 2011/2012 | March-2012 | 3 | 2012
27168 | DUCKS - HANGATIKI EAST RD | 2012-03-07 14:32 | 2012-03-07 | 2012-03-07 17:20 | Calculated | TF2488 | TF2488 - Transformer Fuse: TF2488 |  | 102SEG521-505 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 1 | 24586 | 168 | 0.00683 | 4.0674e-05 | 15 | 2522 | 2011/2012 | March-2012 | 3 | 2012
27170 | LV LINE DOWN - OLD TE KUITI RD | 2012-03-07 17:05 | 2012-03-07 | 2012-03-07 18:41 | Calculated | TF206 | TF206 - Transformer Fuse: TF206 |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 14 | 24586 | 1331 | 0.05414 | 0.00056943 | 50 | 4756 | 2011/2012 | March-2012 | 3 | 2012
27152 | WIND/LV LINE DOWN - WHAKAMARU RD | 2012-03-08 07:52 | 2012-03-08 | 2012-03-08 10:50 | Calculated | TF991 | TF991 - Transformer Fuse: TF991 |  | No Segment | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 178 | 5 | 24586 | 890 | 0.0362 | 0.00020337 | 15 | 2672 | 2011/2012 | March-2012 | 3 | 2012
27153 | REPLACE POLES AND XARMS - COAST FEEDER | 2012-03-08 08:51 | 2012-03-08 | 2012-03-08 15:47 | Calculated | 125TempABS2 | 125TempABS2 - Temp ABS2 125-03 |  | 125SEG125TempABS2-281RET | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 374 | 36 | 24586 | 6096 | 0.24795 | 0.0014642 | 390 | 40559 | 2011/2012 | March-2012 | 3 | 2012
27155 | R/Y/B PHASE TRIP - MT RUAPEHU - BY WATER TOWER | 2012-03-08 12:20 | 2012-03-08 | 2012-03-08 12:22 | Calculated | 5773 | 5773 - Circuit Breaker 5773 |  | 419SEG5773-5998 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 39 | 24586 | 67 | 0.00273 | 0.0015863 | 1640 | 2842 | 2011/2012 | March-2012 | 3 | 2012
27156 | TREE FELLED THROUGH LINE - FAUCHELLE RD | 2012-03-08 13:51 | 2012-03-08 | 2012-03-08 16:42 | Calculated | 5277 | 5277 - Sectionaliser with Bypass & Links5277 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 170 | 16 | 24586 | 2722 | 0.11071 | 0.00065078 | 135 | 22974 | 2011/2012 | March-2012 | 3 | 2012
27157 | WIND - WAIPAPA RD | 2012-03-08 15:37 | 2012-03-08 | 2012-03-08 17:57 | Calculated | TF1497 | TF1497 - Transformer Fuse: TF1497 |  | 122SEG595 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 2 | 24586 | 278 | 0.01131 | 8.1347e-05 | 25 | 3480 | 2011/2012 | March-2012 | 3 | 2012
27158 | WIND / LV CLASH - MCDONALD RD | 2012-03-08 15:54 | 2012-03-08 | 2012-03-08 16:51 | Calculated | TF2589 | TF2589 - Transformer Fuse: TF2589 |  | 120SEG465-410 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 3 | 24586 | 171 | 0.00696 | 0.00012202 | 25 | 1428 | 2011/2012 | March-2012 | 3 | 2012
27159 | WIND - MAROTIRI RD | 2012-03-08 18:23 | 2012-03-08 | 2012-03-08 20:21 | Calculated | TF1203 | TF1203 - Transformer Fuse: TF1203 |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 3 | 24586 | 354 | 0.0144 | 0.00012202 | 15 | 1772 | 2011/2012 | March-2012 | 3 | 2012
27160 | POLE AND XARM CHANGES - RANGIPO/HAUTU FEEDER | 2012-03-09 07:24 | 2012-03-09 | 2012-03-09 15:01 | Calculated | 5963 | 5963 - Recloser with Bypass & Links 5963 |  | 424SEG5963 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 293 | 23 | 24586 | 6728 | 0.27365 | 0.00093549 | 1997.5 | 584368 | 2011/2012 | March-2012 | 3 | 2012
27161 | RECLOSER 5661 TRIPPED - WAITUHI SUB | 2012-03-09 08:01 | 2012-03-09 | 2012-03-09 10:03 | Calculated | 5661 | 5661 - Recloser with Bypass 5661 |  | 408SEG5664-5661 | Manunui 408-03 | Rural B | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 121 | 15 | 24586 | 1817 | 0.0739 | 0.0006101 | 86.3889 | 10466 | 2011/2012 | March-2012 | 3 | 2012
27163 | REPLACE POLES AND XARMS - COAST FEEDER | 2012-03-09 08:52 | 2012-03-09 | 2012-03-09 13:48 | Calculated | 125TempABS2 | 125TempABS2 - Temp ABS2 125-03 |  | 125SEG125TempABS2-281RET | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 275 | 36 | 24586 | 4512 | 0.18352 | 0.0014642 | 390 | 31649 | 2011/2012 | March-2012 | 3 | 2012
27164 | REPLACE POLES AND XARMS - ALSO INSTALL TEMP LINKS AT POLE 196 FOR FUTURE SHUTDOWN - WHAREPAPA FEEDER | 2012-03-09 09:21 | 2012-03-09 | 2012-03-09 16:00 | Calculated | 380 | 380 - Air Break Switch 380 |  | 122SEG398-380 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 398 | 15 | 24586 | 5982 | 0.24331 | 0.0006101 | 160 | 63813 | 2011/2012 | March-2012 | 3 | 2012
27165 | FAULTY PIN INSULATOR - WAITUHI SUB | 2012-03-11 07:50 | 2012-03-11 | 2012-03-11 13:11 | Calculated | 5661 | 5661 - Recloser with Bypass 5661 |  | 408SEG5664-5661 | Manunui 408-03 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 320 | 15 | 24586 | 4801 | 0.19527 | 0.0006101 | 86.3889 | 27654 | 2011/2012 | March-2012 | 3 | 2012
27166 | BARK ON LINE - KARANGAHAPE RD | 2012-03-11 13:51 | 2012-03-11 | 2012-03-11 14:57 | Calculated | 6150 | 6150 - Fused Link 6150 |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 5 | 24586 | 330 | 0.01342 | 0.00020337 | 15 | 991 | 2011/2012 | March-2012 | 3 | 2012
27171 | FAULTY LA AT POLE 28 - TE WAIREKA RD | 2012-03-12 00:02 | 2012-03-12 | 2012-03-12 02:28 | Calculated | 123 | 123 - Circuit Breaker 123 |  | No Segment | 203-01 Te Waireka Road | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 1171 | 24586 | 68874 | 2.8013 | 0.047629 | 7513.1587 | 421898 | 2011/2012 | March-2012 | 3 | 2012
27172 | ISOLATE FOR PRIVATE LINE TREE WORK - WESTERN | 2012-03-12 09:15 | 2012-03-12 | 2012-03-12 15:46 | Calculated | 5368 | 5368 - Sectionaliser with Bypass & Links 5368 |  | 403SEG5622-5368 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 391 | 12 | 24586 | 4698 | 0.19108 | 0.00048808 | 55 | 21536 | 2011/2012 | March-2012 | 3 | 2012
27174 | REPLACE POLES AND XARMS - ALSO REMOVE TEMP LINKS AT POLE 196 LIVE LINE - WHAREPAPA FEEDER | 2012-03-13 08:51 | 2012-03-13 | 2012-03-13 15:28 | Calculated | 398 | 398 - Air Break Switch 398 |  | 122SEG366-398 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 374 | 21 | 24586 | 7837 | 0.31876 | 0.00085414 | 185 | 69048 | 2011/2012 | March-2012 | 3 | 2012
27175 | BURNT OUT FUSE CARRIER - NGAHAPE RD | 2012-03-13 09:15 | 2012-03-13 | 2012-03-13 10:45 | Calculated | TF424 | TF424 - Transformer Fuse: TF424 |  | No Segment | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 5 | 24586 | 450 | 0.0183 | 0.00020337 | 100 | 9018 | 2011/2012 | March-2012 | 3 | 2012
27177 | LV FAULT - FUSE BOX - SANDEL RD | 2012-03-13 14:11 | 2012-03-13 | 2012-03-13 14:51 | Calculated | TF2571 | TF2571 - Transformer Fuse: TF2571 |  | No Segment | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 1 | 24586 | 40 | 0.00163 | 4.0674e-05 | 30 | 1204 | 2011/2012 | March-2012 | 3 | 2012
27178 | FUSE PULLED APART AT TX 21N09 - WATER INTAKE PUMPS | 2012-03-13 14:17 | 2012-03-13 | 2012-03-13 15:30 | Calculated | TF21N09 | TF21N09 - Transformer Fuse: TF21N09 |  | 428SEG6111 | Winstones 428-01 | Remote Rural F | Winstones | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24586 |  | 0 | 0 |  |  | 2011/2012 | March-2012 | 3 | 2012
27233 | CONVERT OH TX 11S05 TO GM TX RELOCATED IN NGAUMU ST | 2012-03-14 08:01 | 2012-03-14 | 2012-03-14 20:23 | Calculated | 5207 | 5207 - Air Break Switch 5207 |  | 424SEG5200-6650 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 259 | 49 | 24586 | 12097 | 0.49203 | 0.001993 | 500 | 121474 | 2011/2012 | March-2012 | 3 | 2012
27236 | REPLACE POLES AND XARMS - WHAREPAPA FEEDER | 2012-03-14 09:02 | 2012-03-14 | 2012-03-14 16:35 | Calculated | 5381 | 5381 - Fused Link 5381 |  | 403SEG5766-5460RET | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 452 | 1 | 24586 | 452 | 0.01838 | 4.0674e-05 | 15 | 6786 | 2011/2012 | March-2012 | 3 | 2012
27237 | RAISE PLATFORM FOR SWER ISO SUB TX 1948 - ARIA FEEDER | 2012-03-14 09:04 | 2012-03-14 | 2012-03-14 15:44 | Calculated | 1102 | 1102 - Air Break Switch 1102 |  | 114SEG1102-1126RET | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 400 | 55 | 24586 | 22011 | 0.89527 | 0.002237 | 383 | 153282 | 2011/2012 | March-2012 | 3 | 2012
27229 | REPLACE POLES 1111277,279,280,297 AND 302 - MAIHIIHI FEEDER | 2012-03-14 09:09 | 2012-03-14 | 2012-03-14 15:08 | Calculated | 574 | 574 - Air Break Switch 574 |  | 111SEG574-357 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 358 | 71 | 24586 | 25428 | 1.0342 | 0.0028878 | 900 | 322334 | 2011/2012 | March-2012 | 3 | 2012
27230 | UPGRADE LV FUSING - SANDEL RD | 2012-03-14 09:34 | 2012-03-14 | 2012-03-14 10:54 | Calculated | TF2571 | TF2571 - Transformer Fuse: TF2571 |  | No Segment | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 80 | 1 | 24586 | 80 | 0.00325 | 4.0674e-05 | 30 | 2407 | 2011/2012 | March-2012 | 3 | 2012
27232 | REPAIR BROKEN EARTH BANK - MCLEAN RD | 2012-03-14 13:16 | 2012-03-14 | 2012-03-14 15:35 | Calculated | TF2436 | TF2436 - Transformer Fuse: TF2436 |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBJ | Underground Cable Joint Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 1 | 24586 | 139 | 0.00565 | 4.0674e-05 | 50 | 6960 | 2011/2012 | March-2012 | 3 | 2012
27235 | RECLOSER 5218 TRIPPED - NGAPUKE SUB | 2012-03-15 05:08 | 2012-03-15 | 2012-03-15 05:39 | Calculated | 5218 | 5218 - Recloser with Bypass 5218 |  | 408SEG5275-5218 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 31 | 73 | 24586 | 2275 | 0.09253 | 0.0029692 | 488 | 15209 | 2011/2012 | March-2012 | 3 | 2012
27238 | T1 OIL TEMP TRIP - WAITETE 33KV INCOMER T1 | 2012-03-15 22:09 | 2012-03-15 | 2012-03-15 23:30 | Calculated | 1411 | 1411 - Circuit Breaker Incomer (T1) 1411 |  | No Segment | Waitete 306-01 | Urban A | Waitete 33 | Direct from Hangatiki Supply |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24586 |  | 0 | 0 |  |  | 2011/2012 | March-2012 | 3 | 2012
27239 | REPLACE COMPLETE STRUCTURE TX 2193 - WHAREPAPA FEEDER | 2012-03-16 09:10 | 2012-03-16 | 2012-03-16 14:56 | Calculated | TF1061 | TF1061 - Transformer Fuse: TF1061 |  | 122SEG366-398 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 346 | 5 | 24586 | 1731 | 0.07041 | 0.00020337 | 25 | 8655 | 2011/2012 | March-2012 | 3 | 2012
27241 | TRUCK VS LINE - WHAREPAPA | 2012-03-16 10:11 | 2012-03-16 | 2012-03-16 13:28 | Calculated | 378 | 378 - Recloser 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 311 | 24586 | 12322 | 0.50118 | 0.012649 | 2763 | 115706 | 2011/2012 | March-2012 | 3 | 2012
27243 | REPLACE HV FUSE AT TX 1480 - MAIN NTH RD - OTOROHANGA | 2012-03-17 05:56 | 2012-03-17 | 2012-03-17 07:01 | Calculated | TF1480 | TF1480 - Transformer Fuse: TF1480 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 3 | 24586 | 195 | 0.00793 | 0.00012202 | 15 | 976 | 2011/2012 | March-2012 | 3 | 2012
27267 | Replace HV Tx Fuse | 2012-03-19 11:01 | 2012-03-19 | 2012-03-19 13:20 | Calculated | TF1098 | TF1098 - Transformer Fuse: TF1098 |  | 111SEG665 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 3 | 24586 | 417 | 0.01696 | 0.00012202 | 15 | 2087 | 2011/2012 | March-2012 | 3 | 2012
27268 | Replace H/V Tx Fuse | 2012-03-19 13:24 | 2012-03-19 | 2012-03-19 16:17 | Calculated | TF4163 | TF4163 - Transformer Fuse: TF4163 |  | No Segment | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 1 | 24586 | 172 | 0.007 | 4.0674e-05 | 30 | 5164 | 2011/2012 | March-2012 | 3 | 2012
27269 | Replace H/V Link | 2012-03-19 14:27 | 2012-03-19 | 2012-03-19 16:12 | Calculated | 578 | 578 - Fused Link 578 |  | 126SEG578 | Rural 126-01 | Rural D | Rural | Taharoa Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 4 | 24586 | 420 | 0.01708 | 0.00016269 | 45 | 4731 | 2011/2012 | March-2012 | 3 | 2012
27272 | Line Down at Pole 49 | 2012-03-19 20:03 | 2012-03-19 | 2012-03-20 00:38 | Calculated | 117 | 117 - Circuit Breaker 117 |  | 111SEG647-117RET | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 275 | 228 | 24586 | 18598 | 0.75645 | 0.0092736 | 2261.25 | 221900 | 2011/2012 | March-2012 | 3 | 2012
27274 | Replace H/V Tx Fuse | 2012-03-19 21:15 | 2012-03-19 | 2012-03-19 21:34 | Calculated | TF20L5 | TF20L5 - Transformer Fuse: TF20L5 |  | No Segment | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 44 | 24586 | 842 | 0.03425 | 0.0017896 | 200 | 3829 | 2011/2012 | March-2012 | 3 | 2012
27277 | Trees Through Line | 2012-03-19 21:55 | 2012-03-19 | 2012-03-23 18:51 | Calculated | 6007 | 6007 - Recloser 6007 |  | No Segment | 513-01 Tawhai | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 5550 | 111 | 24586 | 164989 | 6.7107 | 0.0045148 | 1036 | 1704813 | 2011/2012 | March-2012 | 3 | 2012
27278 | Lines Down | 2012-03-19 23:44 | 2012-03-19 | 2012-03-20 10:01 | Calculated | 5144 | 5144 - Circuit Breaker with Bypass 5144 |  | 411SEG5144-5769 | 501-01 National Park | Rural D | National Park | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 617 | 370 | 24586 | 35026 | 1.4246 | 0.015049 | 3204.7759 | 362828 | 2011/2012 | March-2012 | 3 | 2012
27321 | EXTREME WIND - TREES | 2012-03-20 02:52 | 2012-03-20 | 2012-03-22 16:38 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 486 | 4 | 24586 | 1940 | 0.07891 | 0.00016269 | 450 | 218317 | 2011/2012 | March-2012 | 3 | 2012
27322 | EXTREME WIND - POLES DOWN | 2012-03-20 03:54 | 2012-03-20 | 2012-03-22 17:21 | Calculated | 6135 | 6135 - Circuit Breaker with Bypass 6135 |  | 417SEG5297-5245 | 518-01 Kiko Road | Rural D | Oruatua | Kiko Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3676 | 374 | 24586 | 184595 | 7.5081 | 0.015212 | 2155 | 1006686 | 2011/2012 | March-2012 | 3 | 2012
27323 | EXTREME WIND - POLES DOWN | 2012-03-20 04:53 | 2012-03-20 | 2012-03-26 13:16 | Calculated | 116 | 116 - Recloser with Bypass 116 |  | 109SEG541-116 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9142 | 44 | 24586 | 64682 | 2.6309 | 0.0017896 | 370.5 | 816218 | 2011/2012 | March-2012 | 3 | 2012
27326 | EXTREME WIND | 2012-03-20 05:13 | 2012-03-20 | 2012-03-20 09:11 | Calculated | TF1320 | TF1320 - Transformer Fuse: TF1320 |  | 122SEG702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 237 | 5 | 24586 | 1186 | 0.04824 | 0.00020337 | 25 | 5932 | 2011/2012 | March-2012 | 3 | 2012
27327 | EXTREME WIND | 2012-03-20 05:50 | 2012-03-20 | 2012-03-20 09:27 | Calculated | 127 | 127 - Circuit Breaker 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 602 | 24586 | 84861 | 3.4516 | 0.024485 | 6254.75 | 890756 | 2011/2012 | March-2012 | 3 | 2012
27361 | EXTREME WIND | 2012-03-20 05:57 | 2012-03-20 | 2012-03-20 17:48 | Calculated | TF2589 | TF2589 - Transformer Fuse: TF2589 |  | 120SEG465-410 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 711 | 3 | 24586 | 2133 | 0.08676 | 0.00012202 | 25 | 17778 | 2011/2012 | March-2012 | 3 | 2012
27337 | EXTREME WIND | 2012-03-20 05:57 | 2012-03-20 | 2012-03-20 15:13 | Calculated | TF1248 | TF1248 - Transformer Fuse: TF1248 |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 556 | 1 | 24586 | 556 | 0.02261 | 4.0674e-05 | 5 | 2781 | 2011/2012 | March-2012 | 3 | 2012
27329 | LV LINE DOWN | 2012-03-20 06:05 | 2012-03-20 | 2012-03-20 11:12 | Calculated | TF271 | TF271 - Transformer Fuse: TF271 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 307 | 3 | 24586 | 921 | 0.03746 | 0.00012202 | 30 | 9214 | 2011/2012 | March-2012 | 3 | 2012
27330 | EXTREME WIND | 2012-03-20 06:20 | 2012-03-20 | 2012-03-20 08:31 | Calculated | TF807 | TF807 - Transformer Fuse: TF807 |  | 119SEG417-423 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 4 | 24586 | 525 | 0.02135 | 0.00016269 | 50 | 6572 | 2011/2012 | March-2012 | 3 | 2012
27331 | EXTREME WIND | 2012-03-20 06:48 | 2012-03-20 | 2012-03-21 11:36 | Calculated | 5218 | 5218 - Recloser with Bypass 5218 |  | 408SEG5275-5218 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1611 | 73 | 24586 | 24698 | 1.0046 | 0.0029692 | 488 | 151313 | 2011/2012 | March-2012 | 3 | 2012
27338 | EXTREME WIND | 2012-03-20 08:03 | 2012-03-20 | 2012-03-20 14:06 | Calculated | 565 | 565 - Fused Link 565 |  | 121SEG565 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 363 | 6 | 24586 | 2179 | 0.08863 | 0.00024404 | 40 | 14528 | 2011/2012 | March-2012 | 3 | 2012
27339 | EXTREME WIND | 2012-03-20 08:12 | 2012-03-20 | 2012-03-20 15:23 | Calculated | 377 | 377 - Fused Link 377 |  | 122SEG392-568 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 355 | 18 | 24586 | 6379 | 0.25946 | 0.00073212 | 145 | 51388 | 2011/2012 | March-2012 | 3 | 2012
27340 | EXTREME WIND | 2012-03-20 08:17 | 2012-03-20 | 2012-03-20 11:06 | Calculated | 1335 | 1335 - Sectionaliser 1335 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 169 | 17 | 24586 | 2876 | 0.11698 | 0.00069145 | 148 | 25041 | 2011/2012 | March-2012 | 3 | 2012
27332 | TIROHANGA FEEDER RENEWAL PROJECT | 2012-03-20 08:28 | 2012-03-20 | 2012-03-20 18:12 | Calculated | 635 | 635 - Air Break Switch 635 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 374 | 29 | 24586 | 10836 | 0.44074 | 0.0011795 | 325 | 121447 | 2011/2012 | March-2012 | 3 | 2012
27341 | EXTREME WIND | 2012-03-20 08:42 | 2012-03-20 | 2012-03-20 12:24 | Calculated | TF2357 | TF2357 - Transformer Fuse: TF2357 |  | 119SEG432-653 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 222 | 1 | 24586 | 222 | 0.00903 | 4.0674e-05 | 10 | 2222 | 2011/2012 | March-2012 | 3 | 2012
27333 | EXTREME WIND - LINE DOWN | 2012-03-20 09:39 | 2012-03-20 | 2012-03-20 11:13 | Calculated | 379 | 379 - Air Break Switch 379 |  | 122SEG379 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 12 | 24586 | 1130 | 0.04596 | 0.00048808 | 90 | 8478 | 2011/2012 | March-2012 | 3 | 2012
27342 | EXTREME WIND | 2012-03-20 10:03 | 2012-03-20 | 2012-03-20 11:23 | Calculated | 355 | 355 - Fused Link 355 |  | 112SEG355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 10 | 24586 | 802 | 0.03262 | 0.00040674 | 105 | 8421 | 2011/2012 | March-2012 | 3 | 2012
27343 | EXTREME WIND | 2012-03-20 10:04 | 2012-03-20 | 2012-03-20 15:12 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 308 | 103 | 24586 | 31744 | 1.2911 | 0.0041894 | 988 | 304501 | 2011/2012 | March-2012 | 3 | 2012
27335 | EXTREME WIND - TREES IN LV | 2012-03-20 10:07 | 2012-03-20 | 2012-03-20 11:02 | Calculated | TF1139 | TF1139 - Transformer Fuse: TF1139 |  | 129SEG477 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 3 | 24586 | 165 | 0.00671 | 0.00012202 | 15 | 828 | 2011/2012 | March-2012 | 3 | 2012
27344 | EXTREME WIND | 2012-03-20 10:14 | 2012-03-20 | 2012-03-20 13:34 | Calculated | 5494 | 5494 - Recloser with Bypass 5494 |  | 410SEG5494-5493 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 200 | 43 | 24586 | 6194 | 0.25193 | 0.001749 | 273.3333 | 39929 | 2011/2012 | March-2012 | 3 | 2012
27362 | EXTREME WIND | 2012-03-20 10:16 | 2012-03-20 | 2012-03-20 17:07 | Calculated | TF1004 | TF1004 - Transformer Fuse: TF1004 |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 411 | 4 | 24586 | 1644 | 0.06687 | 0.00016269 | 30 | 12334 | 2011/2012 | March-2012 | 3 | 2012
27336 | EXTREME WIND - LINE DOWN | 2012-03-20 10:17 | 2012-03-20 | 2012-03-20 13:22 | Calculated | 399 | 399 - Air Break Switch 399 |  | 111SEG707-399 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 32 | 24586 | 5926 | 0.24103 | 0.0013016 | 455 | 84265 | 2011/2012 | March-2012 | 3 | 2012
27346 | EXTREME WIND | 2012-03-20 10:22 | 2012-03-20 | 2012-03-20 12:13 | Calculated | TF2982 | TF2982 - Transformer Fuse: TF2982 |  | No Segment | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 1 | 24586 | 111 | 0.00451 | 4.0674e-05 | 30 | 3336 | 2011/2012 | March-2012 | 3 | 2012
27347 | EXTREME WIND | 2012-03-20 10:40 | 2012-03-20 | 2012-03-20 12:23 | Calculated | TF2638 | TF2638 - Transformer Fuse: TF2638 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 1 | 24586 | 103 | 0.00419 | 4.0674e-05 | 25 | 2580 | 2011/2012 | March-2012 | 3 | 2012
27348 | EXTREME WIND | 2012-03-20 10:40 | 2012-03-20 | 2012-03-20 12:23 | Calculated | TF416 | TF416 - Transformer Fuse: TF416 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 3 | 24586 | 309 | 0.01257 | 0.00012202 | 30 | 3096 | 2011/2012 | March-2012 | 3 | 2012
27349 | EXTREME WIND | 2012-03-20 10:44 | 2012-03-20 | 2012-03-20 15:21 | Calculated | 431 | 431 - Fused Link 431 |  | 122SEG431 | Wharepapa 122-01 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 277 | 8 | 24586 | 2217 | 0.09017 | 0.00032539 | 55 | 15246 | 2011/2012 | March-2012 | 3 | 2012
27350 | EXTREME WIND | 2012-03-20 10:46 | 2012-03-20 | 2012-03-20 15:39 | Calculated | TF2312 | TF2312 - Transformer Fuse: TF2312 |  | No Segment | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 293 | 3 | 24586 | 879 | 0.03575 | 0.00012202 | 15 | 4398 | 2011/2012 | March-2012 | 3 | 2012
27351 | EXTREME WIND | 2012-03-20 10:47 | 2012-03-20 | 2012-03-20 16:00 | Calculated | TF1188 | TF1188 - Transformer Fuse: TF1188 |  | 122SEG702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 313 | 2 | 24586 | 626 | 0.02546 | 8.1347e-05 | 15 | 4698 | 2011/2012 | March-2012 | 3 | 2012
27363 | EXTREME WIND | 2012-03-20 10:56 | 2012-03-20 | 2012-03-20 16:32 | Calculated | 5829 | 5829 - Fused Link 5829 |  | 410SEG5829-5545 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 336 | 23 | 24586 | 7731 | 0.31445 | 0.00093549 | 130 | 43699 | 2011/2012 | March-2012 | 3 | 2012
27364 | EXTREME WIND | 2012-03-20 10:57 | 2012-03-20 | 2012-03-20 16:46 | Calculated | TF2296 | TF2296 - Transformer Fuse: TF2296 |  | No Segment | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 349 | 3 | 24586 | 1047 | 0.04259 | 0.00012202 | 50 | 17457 | 2011/2012 | March-2012 | 3 | 2012
27365 | EXTREME WIND | 2012-03-20 10:57 | 2012-03-20 | 2012-03-20 16:46 | Calculated | TF920 | TF920 - Transformer Fuse: TF920 |  | No Segment | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 349 | 5 | 24586 | 1745 | 0.07098 | 0.00020337 | 100 | 34915 | 2011/2012 | March-2012 | 3 | 2012
27355 | EXTREME WIND - LINE DOWN | 2012-03-20 11:11 | 2012-03-20 | 2012-03-20 19:04 | Calculated | 5782 | 5782 - Fused Link 5782 |  | 402SEG5782 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 473 | 40 | 24586 | 3082 | 0.12536 | 0.0016269 | 280.5 | 27635 | 2011/2012 | March-2012 | 3 | 2012
27352 | EXTREME WIND - LV LINE DOWN | 2012-03-20 11:36 | 2012-03-20 | 2012-03-20 12:17 | Calculated | TF273 | TF273 - Transformer Fuse: TF273 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 2 | 24586 | 82 | 0.00334 | 8.1347e-05 | 15 | 618 | 2011/2012 | March-2012 | 3 | 2012
27366 | EXTREME WIND | 2012-03-20 11:41 | 2012-03-20 | 2012-03-20 16:40 | Calculated | TF193 | TF193 - Transformer Fuse: TF193 |  | No Segment | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 299 | 4 | 24586 | 1196 | 0.04865 | 0.00016269 | 15 | 4487 | 2011/2012 | March-2012 | 3 | 2012
27354 | EXTREME WIND | 2012-03-20 11:46 | 2012-03-20 | 2012-03-20 15:10 | Calculated | TF952 | TF952 - Transformer Fuse: TF952 |  | No Segment | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 204 | 6 | 24586 | 1225 | 0.04983 | 0.00024404 | 25 | 5104 | 2011/2012 | March-2012 | 3 | 2012
27356 | EXTREME WIND - LINE DOWN | 2012-03-20 12:30 | 2012-03-20 | 2012-03-20 13:26 | Calculated | 362 | 362 - Fused Link 362 |  | 111SEG362 | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 17 | 24586 | 954 | 0.0388 | 0.00069145 | 115 | 6457 | 2011/2012 | March-2012 | 3 | 2012
27367 | EXTREME WIND | 2012-03-20 12:32 | 2012-03-20 | 2012-03-20 16:25 | Calculated | 562 | 562 - Fused Link 562 |  | 122SEG562 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 233 | 14 | 24586 | 3264 | 0.13276 | 0.00056943 | 200 | 46629 | 2011/2012 | March-2012 | 3 | 2012
27368 | EXTREME WIND | 2012-03-20 12:37 | 2012-03-20 | 2012-03-20 17:06 | Calculated | TF1590 | TF1590 - Transformer Fuse: TF1590 |  | 122SEG619-REG35 | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 269 | 2 | 24586 | 538 | 0.02188 | 8.1347e-05 | 25 | 6728 | 2011/2012 | March-2012 | 3 | 2012
27357 | EXTREME WIND - POLE DOWN | 2012-03-20 12:55 | 2012-03-20 | 2012-03-20 14:58 | Calculated | 638 | 638 - Fused Link 638 |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 28 | 24586 | 3448 | 0.14024 | 0.0011389 | 365 | 44949 | 2011/2012 | March-2012 | 3 | 2012
27358 | EXTREME WIND | 2012-03-20 12:56 | 2012-03-20 | 2012-03-20 14:44 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 26 | 24586 | 2811 | 0.11433 | 0.0010575 | 300 | 32445 | 2011/2012 | March-2012 | 3 | 2012
27359 | LV LINE DOWN | 2012-03-20 13:19 | 2012-03-20 | 2012-03-20 14:47 | Calculated | TF1205 | TF1205 - Transformer Fuse: TF1205 |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 27 | 24586 | 2380 | 0.0968 | 0.0010982 | 100 | 8814 | 2011/2012 | March-2012 | 3 | 2012
27360 | EXTREME WIND | 2012-03-20 13:22 | 2012-03-20 | 2012-03-20 14:34 | Calculated | 5806 | 5806 - Recloser with Bypass 5806 |  | 410SEG5806-5793 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 72 | 68 | 24586 | 4906 | 0.19954 | 0.0027658 | 399 | 28787 | 2011/2012 | March-2012 | 3 | 2012
27369 | EXTREME WIND | 2012-03-20 13:36 | 2012-03-20 | 2012-03-20 16:53 | Calculated | TF1320 | TF1320 - Transformer Fuse: TF1320 |  | 122SEG702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 197 | 5 | 24586 | 985 | 0.04006 | 0.00020337 | 25 | 4928 | 2011/2012 | March-2012 | 3 | 2012
27370 | EXTREME WIND | 2012-03-20 15:23 | 2012-03-20 | 2012-03-20 17:12 | Calculated | 5407 | 5407 - Sectionaliser with Bypass 5407 |  | 410SEG5407-5433 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 109 | 46 | 24586 | 5020 | 0.20418 | 0.001871 | 267.5 | 29197 | 2011/2012 | March-2012 | 3 | 2012
27371 | EXTREME WIND | 2012-03-20 15:44 | 2012-03-20 | 2012-03-20 17:47 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 103 | 24586 | 12684 | 0.5159 | 0.0041894 | 988 | 121672 | 2011/2012 | March-2012 | 3 | 2012
27374 | EXTREME WIND - LINE DOWN | 2012-03-20 16:48 | 2012-03-20 | 2012-03-21 00:38 | Calculated | 5132 | 5132 - Circuit Breaker Manunui SF6 5132 |  | No Segment | 510-01 Manunui | Rural B | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 470 | 953 | 24586 | 142609 | 5.8004 | 0.038762 | 6298 | 956559 | 2011/2012 | March-2012 | 3 | 2012
27372 | EXTREME WIND - LV FAULT | 2012-03-20 17:13 | 2012-03-20 | 2012-03-20 18:01 | Calculated | TF413 | TF413 - Transformer Fuse: TF413 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 2 | 24586 | 96 | 0.0039 | 8.1347e-05 | 15 | 722 | 2011/2012 | March-2012 | 3 | 2012
27373 | EXTREME WIND - LINE DOWN | 2012-03-20 18:21 | 2012-03-20 | 2012-03-20 18:22 | Calculated | 5142 | 5142 - Circuit Breaker with Bypass 5142 |  | 410SEG6766-5141 | 501-01 National Park | Rural D | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 316 | 24586 | 363 | 0.01476 | 0.012853 | 2082.8333 | 2395 | 2011/2012 | March-2012 | 3 | 2012
27393 | EXTREME WIND - LINE DOWN | 2012-03-21 02:56 | 2012-03-21 | 2012-03-21 10:28 | Calculated | 446 | 446 - Recloser 446 |  | 402SEG5343-5446 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 452 | 184 | 24586 | 25035 | 1.0183 | 0.0074839 | 1634.1667 | 206994 | 2011/2012 | March-2012 | 3 | 2012
27378 | CONVERT TX 08R17 TO AN RTE TYPE | 2012-03-21 08:33 | 2012-03-21 | 2012-03-21 17:03 | Calculated | TF8R17 | TF8R17 - Transformer Fuse: TF8R17 |  | 406SEG6670 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 509 | 127 | 24586 | 63470 | 2.5816 | 0.0051655 | 400 | 199686 | 2011/2012 | March-2012 | 3 | 2012
27381 | TIROHANGA FEEDER RENEWAL PROJECT | 2012-03-21 08:50 | 2012-03-21 | 2012-03-21 14:35 | Calculated | 635 | 635 - Air Break Switch 635 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 29 | 24586 | 8169 | 0.33226 | 0.0011795 | 325 | 91529 | 2011/2012 | March-2012 | 3 | 2012
27380 | REPLACE POLES AND XARMS - WHAREPAPA | 2012-03-21 09:04 | 2012-03-21 | 2012-03-21 14:58 | Calculated | 372 | 372 - Fused Link 372 |  | 122SEG372 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 354 | 24 | 24586 | 8500 | 0.34573 | 0.00097617 | 148 | 52419 | 2011/2012 | March-2012 | 3 | 2012
27382 | EXTREME WIND | 2012-03-21 12:18 | 2012-03-21 | 2012-03-21 14:18 | Calculated | 745 | 745 - Fused Link 745 |  | 120SEG580-745 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 5 | 24586 | 601 | 0.02444 | 0.00020337 | 85 | 10221 | 2011/2012 | March-2012 | 3 | 2012
27383 | EXTREME WIND - 33KV XARM DOWN ON 11KV XARM | 2012-03-21 12:44 | 2012-03-21 | 2012-03-21 13:45 | Calculated | 5158 | 5158 - Air Break Switch 5158 |  | 609SEG5158-5159 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 61 | 19 | 24586 | 1043 | 0.04242 | 0.0007728 | 270 | 14387 | 2011/2012 | March-2012 | 3 | 2012
27385 | EXTREME WIND - BROKEN XARM | 2012-03-21 13:58 | 2012-03-21 | 2012-03-21 15:19 | Calculated | 5373 | 5373 - Fused Link 5373 |  | 411SEG5373-5387 | National Park 411-02 | Rural D | National Park | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 8 | 24586 | 649 | 0.0264 | 0.00032539 | 100 | 8120 | 2011/2012 | March-2012 | 3 | 2012
27386 | EXTREME WIND | 2012-03-21 14:37 | 2012-03-21 | 2012-03-21 15:53 | Calculated | TF8K4 | TF8K4 - Transformer Fuse: TF8K4 |  | No Segment | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 76 | 4 | 24586 | 304 | 0.01236 | 0.00016269 | 15 | 1143 | 2011/2012 | March-2012 | 3 | 2012
27387 | EXTREME WIND | 2012-03-21 14:43 | 2012-03-21 | 2012-03-21 16:11 | Calculated | TF12O03 | TF12O03 - Transformer Fuse: TF12O03 |  | 418SEG5836-5589 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 88 | 4 | 24586 | 352 | 0.01432 | 0.00016269 | 160 | 14112 | 2011/2012 | March-2012 | 3 | 2012
27388 | EXTREME WIND - FUSE PULLED APART | 2012-03-21 15:23 | 2012-03-21 | 2012-03-21 16:22 | Calculated | TF21M12 | TF21M12 - Transformer Fuse: TF21M12 |  | 416SEG5684-5747 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 2 | 24586 | 118 | 0.0048 | 8.1347e-05 | 15 | 888 | 2011/2012 | March-2012 | 3 | 2012
27389 | EXTREME WIND - BROKEN XARM | 2012-03-21 17:55 | 2012-03-21 | 2012-03-21 21:05 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 190 | 103 | 24586 | 7886 | 0.32075 | 0.0041894 | 988 | 70478 | 2011/2012 | March-2012 | 3 | 2012
27390 | EXTREME WIND - LINE DOWN | 2012-03-21 19:42 | 2012-03-21 | 2012-03-21 21:10 | Calculated | 522 | 522 - Air Break Switch 522 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 56 | 24586 | 4939 | 0.20089 | 0.0022777 | 555 | 48950 | 2011/2012 | March-2012 | 3 | 2012
27392 | EXTREME WIND | 2012-03-21 21:06 | 2012-03-21 | 2012-03-21 21:21 | Calculated | 2102 | 2102 - Circuit Breaker Mareatai 11 kV 2102 |  | No Segment | 210-01 Maraetai | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 605 | 24586 | 8235 | 0.33495 | 0.024608 | 4598.5936 | 62616 | 2011/2012 | March-2012 | 3 | 2012
27391 | EXTREME WIND | 2012-03-21 23:01 | 2012-03-21 | 2012-03-21 23:12 | Calculated | 1072 | 1072 - Circuit Breaker 1072 Huirimu |  | 121SEG1072-753 | 211-01 Arohena | Rural D | Huirimu | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 159 | 24586 | 1780 | 0.0724 | 0.0064671 | 1668.1667 | 18683 | 2011/2012 | March-2012 | 3 | 2012
27394 | EXTREME WIND | 2012-03-22 05:22 | 2012-03-22 | 2012-03-22 08:11 | Calculated | 5407 | 5407 - Sectionaliser with Bypass 5407 |  | 410SEG5407-5433 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 169 | 46 | 24586 | 7785 | 0.31664 | 0.001871 | 267.5 | 45274 | 2011/2012 | March-2012 | 3 | 2012
27396 | EXTREME WIND | 2012-03-22 09:07 | 2012-03-22 | 2012-03-22 11:53 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 1 | 24586 | 166 | 0.00675 | 4.0674e-05 | 5 | 831 | 2011/2012 | March-2012 | 3 | 2012
27404 | EXTREME WIND | 2012-03-22 09:35 | 2012-03-22 | 2012-03-22 11:04 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 26 | 24586 | 2319 | 0.09432 | 0.0010575 | 300 | 26765 | 2011/2012 | March-2012 | 3 | 2012
27397 | REPLACE POLES AND XARMS - ALSO REMOVE TEMP LINKS AT POLE 196 AND 197 LIVE LINE - WHAREPAPA FEEDER | 2012-03-22 09:35 | 2012-03-22 | 2012-03-22 14:56 | Calculated | 398 | 398 - Air Break Switch 398 |  | 122SEG366-398 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 21 | 24586 | 5698 | 0.23176 | 0.00085414 | 185 | 50202 | 2011/2012 | March-2012 | 3 | 2012
27405 | EXTREME WIND | 2012-03-22 10:15 | 2012-03-22 | 2012-03-22 11:33 | Calculated | TF901 | TF901 - Transformer Fuse: TF901 |  | 120SEG416-479 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 1 | 24586 | 78 | 0.00317 | 4.0674e-05 | 25 | 1955 | 2011/2012 | March-2012 | 3 | 2012
27406 | EXTREME WIND | 2012-03-22 10:26 | 2012-03-22 | 2012-03-22 11:10 | Calculated | TF3255 | TF3255 - Transformer Fuse: TF3255 |  | 123SEG450-469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 2 | 24586 | 88 | 0.00358 | 8.1347e-05 | 75 | 3316 | 2011/2012 | March-2012 | 3 | 2012
27409 | EXTREME WIND - JUMPER OFF TX 1287 | 2012-03-22 11:20 | 2012-03-22 | 2012-03-22 12:34 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 17 | 24586 | 1251 | 0.05088 | 0.00069145 | 113 | 8318 | 2011/2012 | March-2012 | 3 | 2012
27410 | EXTREME WIND | 2012-03-22 12:42 | 2012-03-22 | 2012-03-22 15:10 | Calculated | TF12K7 | TF12K7 - Transformer Fuse: TF12K7 |  | 410SEG5161-5235 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 1 | 24586 | 148 | 0.00602 | 4.0674e-05 | 10 | 1481 | 2011/2012 | March-2012 | 3 | 2012
27412 | FUSE PULLED APART | 2012-03-23 09:02 | 2012-03-23 | 2012-03-23 09:58 | Calculated | TF20L2 | TF20L2 - Transformer Fuse: TF20L2 |  | 414SEG5715-5925RET | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 45 | 24586 | 2528 | 0.10282 | 0.0018303 | 293.4783 | 16488 | 2011/2012 | March-2012 | 3 | 2012
27413 | BROKEN DDO AT TX 8R3 | 2012-03-23 10:55 | 2012-03-23 | 2012-03-23 11:50 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 24586 | 55 | 0.00224 | 4.0674e-05 | 5 | 275 | 2011/2012 | March-2012 | 3 | 2012
27411 | WIND | 2012-03-23 19:40 | 2012-03-23 | 2012-03-24 10:14 | Calculated | TF08R03 | TF08R03 - Transformer Fuse: TF8R3 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 874 | 1 | 24586 | 874 | 0.03555 | 4.0674e-05 | 5 | 4370 | 2011/2012 | March-2012 | 3 | 2012
27261 | COOKED UP LV FUSE BOX | 2012-03-24 20:59 | 2012-03-24 | 2012-03-24 21:50 | Calculated | TF2686 | TF2686 - Transformer Fuse: TF2686 |  | No Segment | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 1 | 24586 | 51 | 0.00207 | 4.0674e-05 | 30 | 1534 | 2011/2012 | March-2012 | 3 | 2012
27262 | RECLOSER 5266 TRIPPED | 2012-03-25 08:39 | 2012-03-25 | 2012-03-25 10:30 | Calculated | 5266 | 5266 - Recloser 5266 |  | 413SEG5260-5266 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 111 | 19 | 24586 | 2111 | 0.08586 | 0.0007728 | 110 | 12224 | 2011/2012 | March-2012 | 3 | 2012
27263 | FAULTY CONNECTION AT POLE 1210118 | 2012-03-25 17:32 | 2012-03-25 | 2012-03-26 | Calculated | 748 | 748 - Air Break Switch 748 |  | 121SEG748-418 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 87 | 24586 | 87 | 0.00354 | 0.0035386 | 801.5 | 801 | 2011/2012 | March-2012 | 3 | 2012
27264 | FUSE PULLED APART | 2012-03-25 21:38 | 2012-03-25 | 2012-03-25 22:52 | Calculated | 5589 | 5589 - Fused Link 5589 |  | 418SEG5589-5584 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 73 | 74 | 24586 | 5414 | 0.22021 | 0.0030098 | 346 | 25315 | 2011/2012 | March-2012 | 3 | 2012
27283 | REPLACE ABS 5648 AND ASSOCIATED EQUP - ALSO MEGGER CABLE AND RECONNECT TX 8I19 - NORTHER FEEDER | 2012-03-26 09:06 | 2012-03-26 | 2012-03-26 16:16 | Calculated | 5483 | 5483 - Fused Link 5483 |  | 402SEG5483-5648 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 64 | 102 | 24586 | 2436 | 0.09908 | 0.0041487 | 445.8333 | 11450 | 2011/2012 | March-2012 | 3 | 2012
27289 | LOWERING TAPS | 2012-03-26 10:16 | 2012-03-26 | 2012-03-26 12:01 | Calculated | TF3345 | TF3345 - Transformer Fusa 3345 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 49 | 4 | 24586 | 58 | 0.00236 | 0.00016269 | 155 | 2331 | 2011/2012 | March-2012 | 3 | 2012
27301 | BROKEN CONNECTION AT 1210118 AND JUMPER AT ABS 748 | 2012-03-26 11:58 | 2012-03-26 | 2012-03-26 16:16 | Calculated | 425 | 425 - Air Break Switch 425 |  | 121SEG425-748 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 251 | 33 | 24586 | 5061 | 0.20585 | 0.0013422 | 275 | 33089 | 2011/2012 | March-2012 | 3 | 2012
27290 | TREES IN LV | 2012-03-26 14:37 | 2012-03-26 | 2012-03-26 15:28 | Calculated | TF2087 | TF2087 - Transformer Fuse: TF2087 |  | 117SEG1259-1722 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 51 | 2 | 24586 | 102 | 0.00415 | 8.1347e-05 | 10 | 511 | 2011/2012 | March-2012 | 3 | 2012
27294 | RANGITOTO FEEDER RENEWAL PROJECT | 2012-03-27 08:36 | 2012-03-27 | 2012-03-27 15:13 | Calculated | 659 | 659 - Air Break Switch 659 |  | 106SEG659-194 | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 351 | 32 | 24586 | 11207 | 0.45583 | 0.0013016 | 240.5 | 84231 | 2011/2012 | March-2012 | 3 | 2012
27292 | REPLACE HV FUSE AT TX 05F18 | 2012-03-27 08:49 | 2012-03-27 | 2012-03-27 11:10 | Calculated | TF5F18 | TF5F18 - Transformer Fuse: TF5F18 |  | No Segment | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 1 | 24586 | 141 | 0.00573 | 4.0674e-05 | 3 | 423 | 2011/2012 | March-2012 | 3 | 2012
27293 | FUSE PULLED APART | 2012-03-27 08:55 | 2012-03-27 | 2012-03-27 17:50 | Calculated | TF901 | TF901 - Transformer Fuse: TF901 |  | 120SEG416-479 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 535 | 1 | 24586 | 535 | 0.02176 | 4.0674e-05 | 25 | 13378 | 2011/2012 | March-2012 | 3 | 2012
27304 | RANGITOTO FEEDER RENEWAL PROJECT | 2012-03-28 09:02 | 2012-03-28 | 2012-03-28 14:27 | Calculated | 659 | 659 - Air Break Switch 659 |  | 106SEG659-194 | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 325 | 32 | 24586 | 10409 | 0.42337 | 0.0013016 | 240.5 | 78230 | 2011/2012 | March-2012 | 3 | 2012
27305 | BROKEN DDO AT TX 8E2 | 2012-03-28 09:31 | 2012-03-28 | 2012-03-28 10:06 | Calculated | 5579 | 5579 - Fused Link 5579 |  | 413SEG5579-5571 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 35 | 24 | 24586 | 844 | 0.03433 | 0.00097617 | 175 | 6157 | 2011/2012 | March-2012 | 3 | 2012
27306 | FUSE PULLED APART AT TX 901 | 2012-03-28 12:43 | 2012-03-28 | 2012-03-28 13:59 | Calculated | TF901 | TF901 - Transformer Fuse: TF901 |  | 120SEG416-479 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 1 | 24586 | 76 | 0.00309 | 4.0674e-05 | 25 | 1903 | 2011/2012 | March-2012 | 3 | 2012
27307 | LOWER TAP AT TX 2060 | 2012-03-28 13:10 | 2012-03-28 | 2012-03-28 13:20 | Calculated | TF2060 | TF2060 - Transformer Fuse: TF2060 |  | 115SEG1717-1723 | Mokauiti 115-05 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 10 | 2 | 24586 | 20 | 0.00081 | 8.1347e-05 | 15 | 152 | 2011/2012 | March-2012 | 3 | 2012
27303 | LV JUMPER AND BROKEN DDO - TE KAWA ST | 2012-03-28 14:22 | 2012-03-28 | 2012-03-29 10:08 | Calculated | TF699 | TF699 - Transformer Fuse: TF699 |  | 112SEG311 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1186 | 1 | 24586 | 1186 | 0.04824 | 4.0674e-05 | 300 | 355850 | 2011/2012 | March-2012 | 3 | 2012
27310 | REPLACE POLES AND XARMS - WHAREPAPA FEEDER | 2012-03-29 08:11 | 2012-03-29 | 2012-03-29 15:22 | Calculated | 398 | 398 - Air Break Switch 398 |  | 122SEG366-398 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 372 | 41 | 24586 | 15207 | 0.61852 | 0.0016676 | 293 | 108566 | 2011/2012 | March-2012 | 3 | 2012
27308 | REPLACE HV FUSE AT TX 191 | 2012-03-29 08:16 | 2012-03-29 | 2012-03-29 11:58 | Calculated | TF191 | TF191 - Transformer Fuse: TF191 |  | No Segment | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 222 | 5 | 24586 | 1110 | 0.04515 | 0.00020337 | 15 | 3331 | 2011/2012 | March-2012 | 3 | 2012
27309 | RANGITOTO FEEDER RENEWAL PROJECT | 2012-03-29 08:21 | 2012-03-29 | 2012-03-29 15:53 | Calculated | 195 | 195 - Air Break Switch 195 |  | 106SEG195-659 | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 377 | 25 | 24586 | 9403 | 0.38245 | 0.0010168 | 210.5 | 79179 | 2011/2012 | March-2012 | 3 | 2012
27313 | REPLACE LINK 5829 | 2012-03-29 17:03 | 2012-03-29 | 2012-03-29 17:48 | Calculated | 5829 | 5829 - Fused Link 5829 |  | 410SEG5829-5545 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 23 | 24586 | 1041 | 0.04234 | 0.00093549 | 130 | 5884 | 2011/2012 | March-2012 | 3 | 2012
27314 | REPLACE HV FUSE AT TX 1686 | 2012-03-29 19:52 | 2012-03-29 | 2012-03-29 20:45 | Calculated | TF1686 | TF1686 - Transformer Fuse: TF1686 |  | 116SEG1354-1334 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 1 | 24586 | 52 | 0.00212 | 4.0674e-05 | 10 | 523 | 2011/2012 | March-2012 | 3 | 2012
27317 | CHANGE TX STRUCTURE | 2012-03-30 09:37 | 2012-03-30 | 2012-03-30 15:07 | Calculated | TF1404 | TF1404 - Transformer Fuse: TF1404 |  | 126SEG504-578 | Rural 126-01 | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 330 | 5 | 24586 | 1650 | 0.06711 | 0.00020337 | 50 | 16508 | 2011/2012 | March-2012 | 3 | 2012
27318 | CHANGE TX STRUCTURE | 2012-03-30 09:48 | 2012-03-30 | 2012-03-30 15:53 | Calculated | TF1405 | TF1405 - Transformer Fuse: TF1405 |  | 126SEG609-2121 | Rural 126-03 | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 364 | 1 | 24586 | 364 | 0.01481 | 4.0674e-05 | 15 | 5463 | 2011/2012 | March-2012 | 3 | 2012
27418 | Replace Faulty Transformer | 2012-04-02 10:13 | 2012-04-02 | 2012-04-02 11:30 | Calculated | TF7A1 | TF7A1 - Transformer Fuse: TF7A1 |  | 413SEG5734 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 77 | 4 | 24590 | 309 | 0.01257 | 0.00016267 | 0 | 0 | 2012/2013 | April-2012 | 4 | 2012
27421 | Replace Poles & Xarms | 2012-04-03 09:03 | 2012-04-03 | 2012-04-03 14:34 | Calculated | 366 | 366 - Air Break Switch 366 |  | 122SEG366-549RET | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 331 | 17 | 24590 | 5629 | 0.22891 | 0.00069134 | 145 | 48019 | 2012/2013 | April-2012 | 4 | 2012
27419 | Branch on Line - Line Down | 2012-04-03 14:30 | 2012-04-03 | 2012-04-03 16:53 | Calculated | 5623 | 5623 - Sectionaliser with Bypass 5623 |  | 409SEG5411-5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 15 | 24590 | 2148 | 0.08735 | 0.00061 | 71.5 | 10239 | 2012/2013 | April-2012 | 4 | 2012
27420 | Tree Through Line | 2012-04-04 17:18 | 2012-04-04 | 2012-04-04 18:38 | Calculated | 6003 | 6003 - Fault Thrower Switch Isolator 6003 |  | 424SEG6003-6559 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 118 | 24590 | 9465 | 0.38491 | 0.0047987 | 505 | 40509 | 2012/2013 | April-2012 | 4 | 2012
27422 | Replace Poles & Xarms | 2012-04-05 09:05 | 2012-04-05 | 2012-04-05 13:53 | Calculated | 366 | 366 - Air Break Switch 366 |  | 122SEG366-549RET | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 288 | 17 | 24590 | 4899 | 0.19923 | 0.00069134 | 145 | 41786 | 2012/2013 | April-2012 | 4 | 2012
27423 | Replace Pole 100/5 | 2012-04-05 09:37 | 2012-04-05 | 2012-04-05 16:32 | Calculated | 5426 | 5426 - Fused Link 5426 |  | 409SEG5426-5846 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 415 | 42 | 24590 | 6517 | 0.26503 | 0.001708 | 377.6667 | 57786 | 2012/2013 | April-2012 | 4 | 2012
27424 | Isolation for L/V Maintenance inside Tx | 2012-04-05 10:07 | 2012-04-05 | 2012-04-05 11:08 | Calculated | 5670 | 5670 - Fused Link 5670 |  | 415SEG5670 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 61 | 10 | 24590 | 613 | 0.02493 | 0.00040667 | 60 | 3679 | 2012/2013 | April-2012 | 4 | 2012
27425 | Replace Faulty Tx | 2012-04-05 15:38 | 2012-04-05 | 2012-04-06 11:43 | Calculated | TF860 | TF860 - Transformer Fuse: TF860 |  | No Segment | Wharepapa 122-01 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1205 | 3 | 24590 | 3615 | 0.14701 | 0.000122 | 10 | 12051 | 2012/2013 | April-2012 | 4 | 2012
27428 | Burnt Out DDO Fuse Holder | 2012-04-06 10:09 | 2012-04-06 | 2012-04-06 12:29 | Calculated | TF826 | TF826 - Transformer Fuse: TF826 |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 1 | 24590 | 140 | 0.00569 | 4.0667e-05 | 5 | 700 | 2012/2013 | April-2012 | 4 | 2012
27429 | Sloppy L/V Xarm - Faulty Tx | 2012-04-07 10:11 | 2012-04-07 | 2012-04-07 13:21 | Calculated | TF860 | TF860 - Transformer Fuse: TF860 |  | No Segment | Wharepapa 122-01 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 190 | 3 | 24590 | 570 | 0.02318 | 0.000122 | 10 | 1901 | 2012/2013 | April-2012 | 4 | 2012
27430 | Fuse Pulled Apart | 2012-04-07 13:31 | 2012-04-07 | 2012-04-07 14:30 | Calculated | TF7H3 | TF7H3 - Transformer Fuse: TF7H3 |  | 402SEG5781 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 1 | 24590 | 59 | 0.0024 | 4.0667e-05 | 15 | 887 | 2012/2013 | April-2012 | 4 | 2012
27431 | Fuse Pulled Apart | 2012-04-08 14:27 | 2012-04-08 | 2012-04-08 15:32 | Calculated | TF5K04 | TF5K04 - Transformer Fuse: TF5K04 |  | 402SEG5360-5267 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 64 | 5 | 24590 | 320 | 0.01301 | 0.00020333 | 30 | 1925 | 2012/2013 | April-2012 | 4 | 2012
27432 | Faulty Tx | 2012-04-09 05:41 | 2012-04-09 | 2012-04-09 12:47 | Calculated | TF901 | TF901 - Transformer Fuse: TF901 |  | 120SEG416-479 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 425 | 1 | 24590 | 425 | 0.01728 | 4.0667e-05 | 25 | 10631 | 2012/2013 | April-2012 | 4 | 2012
27433 | Fuse Pulled Apart | 2012-04-09 09:45 | 2012-04-09 | 2012-04-09 10:07 | Calculated | TF20L31 | TF20L31 - Transformer Fuse: TF20L31 |  | 415SEGREG28-6788 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 4 | 24590 | 88 | 0.00358 | 0.00016267 | 200 | 4430 | 2012/2013 | April-2012 | 4 | 2012
27434 | L/V Fault | 2012-04-10 12:00 | 2012-04-10 | 2012-04-10 13:24 | Calculated | TF216 | TF216 - Transformer Fuse: TF216 |  | 112SEG331-355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 2 | 24590 | 168 | 0.00683 | 8.1334e-05 | 15 | 1262 | 2012/2013 | April-2012 | 4 | 2012
27435 | Fuse Pulled Apart | 2012-04-10 12:05 | 2012-04-10 | 2012-04-10 13:58 | Calculated | TF9D6 | TF9D6 - Transformer Fuse: TF9D6 |  | No Segment | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 113 | 1 | 24590 | 113 | 0.0046 | 4.0667e-05 | 5 | 565 | 2012/2013 | April-2012 | 4 | 2012
27436 | Replace Tx Pole | 2012-04-11 09:02 | 2012-04-11 | 2012-04-11 13:37 | Calculated | TF1246 | TF1246 - Transformer Fuse: TF1246 |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 275 | 6 | 24590 | 1651 | 0.06714 | 0.000244 | 30 | 8255 | 2012/2013 | April-2012 | 4 | 2012
27437 | Tx Upgrade | 2012-04-12 09:35 | 2012-04-12 | 2012-04-13 16:52 | Calculated | 5788 | 5788 - Air Break Switch 5788 |  | 414SEG5925-5964 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 72 | 82 | 24590 | 5841 | 0.23754 | 0.0033347 | 388.2353 | 27655 | 2012/2013 | April-2012 | 4 | 2012
27438 | Line Down - Found Next Day | 2012-04-12 21:06 | 2012-04-12 | 2012-04-12 21:50 | Calculated | 341 | 341 - Fused Link 341 |  | 109SEG341-587 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 40 | 24590 | 14613 | 0.59427 | 0.0016267 | 355 | 129693 | 2012/2013 | April-2012 | 4 | 2012
27439 | Line Down | 2012-04-13 07:14 | 2012-04-13 | 2012-04-13 12:36 | Calculated | 341 | 341 - Fused Link 341 |  | 109SEG341-587 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 322 | 40 | 24590 | 12885 | 0.52399 | 0.0016267 | 355 | 114363 | 2012/2013 | April-2012 | 4 | 2012
27440 | Replace Pole | 2012-04-13 09:02 | 2012-04-13 | 2012-04-13 14:52 | Calculated | TF1246 | TF1246 - Transformer Fuse: TF1246 |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 350 | 6 | 24590 | 2100 | 0.0854 | 0.000244 | 30 | 10504 | 2012/2013 | April-2012 | 4 | 2012
27441 | Raise Platform for SWER Iso Sub Tx2166 | 2012-04-13 09:33 | 2012-04-13 | 2012-04-13 15:15 | Calculated | 1605 | 1605 - Fused Link 1605 |  | 128SEG1605-1607 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 59 | 24590 | 20185 | 0.82086 | 0.0023993 | 440.5 | 150709 | 2012/2013 | April-2012 | 4 | 2012
27442 | Broken Xarm - Temp Repair | 2012-04-13 12:25 | 2012-04-13 | 2012-04-13 14:41 | Calculated | TF545 | TF545 - Transformer Fuse: TF545 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 2 | 24590 | 272 | 0.01106 | 8.1334e-05 | 25 | 3403 | 2012/2013 | April-2012 | 4 | 2012
27443 | Rotten Xarm @ Pole 79/46/7 | 2012-04-13 16:29 | 2012-04-13 | 2012-04-13 17:07 | Calculated | 1313 | 1313 - Air Break Switch 1313 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 28 | 24590 | 1067 | 0.04339 | 0.0011387 | 250 | 9533 | 2012/2013 | April-2012 | 4 | 2012
27444 | Unknown | 2012-04-14 16:12 | 2012-04-14 | 2012-04-14 17:40 | Calculated | 5277 | 5277 - Sectionaliser with Bypass & Links5277 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 88 | 16 | 24590 | 1410 | 0.05734 | 0.00065067 | 135 | 11898 | 2012/2013 | April-2012 | 4 | 2012
27445 | Replace Pole & Xarms | 2012-04-16 09:12 | 2012-04-16 | 2012-04-16 14:43 | Calculated | 398 | 398 - Air Break Switch 398 |  | 122SEG366-398 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 331 | 34 | 24590 | 11259 | 0.45787 | 0.0013827 | 233 | 77161 | 2012/2013 | April-2012 | 4 | 2012
27447 | Fit T/O Fuses for Tx 1362 | 2012-04-16 10:02 | 2012-04-16 | 2012-04-16 12:30 | Calculated | 399 | 399 - Air Break Switch 399 |  | 111SEG707-399 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 32 | 24590 | 4741 | 0.1928 | 0.0013013 | 455 | 67415 | 2012/2013 | April-2012 | 4 | 2012
27448 | Broken Xarms | 2012-04-16 10:49 | 2012-04-16 | 2012-04-16 17:44 | Calculated | TF545 | TF545 - Transformer Fuse: TF545 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 415 | 2 | 24590 | 830 | 0.03375 | 8.1334e-05 | 25 | 10378 | 2012/2013 | April-2012 | 4 | 2012
27449 | Unknown | 2012-04-16 18:00 | 2012-04-16 | 2012-04-16 18:10 | Calculated | TF175 | TF175 - Transformer Fuse: TF175 |  | 110SEG644-759 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 2 | 24590 | 20 | 0.00081 | 8.1334e-05 | 15 | 152 | 2012/2013 | April-2012 | 4 | 2012
27450 | Fit New Xarms & Fuses for new Extension | 2012-04-17 09:03 | 2012-04-17 | 2012-04-17 13:51 | Calculated | 349 | 349 - Air Break Switch 349 |  | 109SEG348-522 | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 243 | 40 | 24590 | 9687 | 0.39394 | 0.0016267 | 340 | 82342 | 2012/2013 | April-2012 | 4 | 2012
27452 | Fit New T/O Fuses fot Tx 1245 | 2012-04-17 09:24 | 2012-04-17 | 2012-04-17 14:45 | Calculated | 413 | 413 - Air Break Switch 413 |  | 120SEG465-410 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 260 | 15 | 24590 | 3888 | 0.15811 | 0.00061 | 153 | 39660 | 2012/2013 | April-2012 | 4 | 2012
27451 | Install PTF, Restrain Line & Fit T/O Fuse for Tx 1M5 | 2012-04-17 09:41 | 2012-04-17 | 2012-04-17 13:25 | Calculated | 5933 | 5933 - Earth Working Link 5933 |  | 421SEG5933 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 224 | 9 | 24590 | 2017 | 0.08203 | 0.000366 | 60 | 13449 | 2012/2013 | April-2012 | 4 | 2012
27453 | Connect Private Line T/O Fuses | 2012-04-17 10:36 | 2012-04-17 | 2012-04-17 15:09 | Calculated | 1781 | 1781 - Load Break Switch |  | 113SEG1319-1781 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 41 | 22 | 24590 | 884 | 0.03595 | 0.00089467 | 235 | 9443 | 2012/2013 | April-2012 | 4 | 2012
27454 | Unknown | 2012-04-17 18:16 | 2012-04-17 | 2012-04-17 18:27 | Calculated | 727 | 727 - Circuit Breaker 727 |  | 305SEG657-126 | Gadsby Road 305-02 | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 11 | 5 | 24590 | 55 | 0.00224 | 0.00020333 | 800 | 8893 | 2012/2013 | April-2012 | 4 | 2012
27455 | MAgpie | 2012-04-18 01:44 | 2012-04-18 | 2012-04-18 08:53 | Calculated | TF8I63 | TF8I63 - Transformer Fuse: TF8I63 |  | No Segment | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 429 | 1 | 24590 | 429 | 0.01745 | 4.0667e-05 | 3 | 1287 | 2012/2013 | April-2012 | 4 | 2012
27456 | unknown | 2012-04-18 01:59 | 2012-04-18 | 2012-04-18 02:11 | Calculated | 6005 | 6005 - Circuit Breaker 6005 |  | 610SEG6005-6004 | 516-01 Transpower National Park | Rural D | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 1541 | 24590 | 18804 | 0.7647 | 0.062668 | 8618.9713 | 105601 | 2012/2013 | April-2012 | 4 | 2012
27457 | Till Box Blow Up | 2012-04-18 08:34 | 2012-04-18 | 2012-04-18 20:30 | Calculated | TF8R18 | TF8R18 - Transformer Fuse: TF8R18 |  | 406SEG6599-6430 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBT | Underground Cable Termination Failure - Other | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 716 | 268 | 24590 | 125178 | 5.0906 | 0.010899 | 1115 | 479217 | 2012/2013 | April-2012 | 4 | 2012
27458 | Feeder Renewal Project | 2012-04-18 09:07 | 2012-04-18 | 2012-04-18 15:25 | Calculated | TF1379 | TF1379 - Transformer Fuse: TF1379 |  | 103SEG107-REG7 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 378 | 2 | 24590 | 756 | 0.03074 | 8.1334e-05 | 15 | 5672 | 2012/2013 | April-2012 | 4 | 2012
27459 | Replace Pole Number 56 | 2012-04-18 09:24 | 2012-04-18 | 2012-04-18 14:58 | Calculated | TF1A28 | TF1A28 - Transformer Fuse: TF1A28 |  | No Segment | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 334 | 47 | 24590 | 15704 | 0.63863 | 0.0019113 | 200 | 66826 | 2012/2013 | April-2012 | 4 | 2012
27461 | Faulty L/V Fuse Box | 2012-04-18 16:43 | 2012-04-18 | 2012-04-18 17:11 | Calculated | TF2938 | TF2938 - Transformer Fuse: TF2938 |  | No Segment | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 1 | 24590 | 28 | 0.00114 | 4.0667e-05 | 50 | 1406 | 2012/2013 | April-2012 | 4 | 2012
27462 | Replace Poles & Xarms | 2012-04-19 09:13 | 2012-04-19 | 2012-04-19 14:51 | Calculated | TF3125 | TF3125 - Transformer Fuse: TF3125 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 338 | 18 | 24590 | 6087 | 0.24754 | 0.000732 | 160 | 54114 | 2012/2013 | April-2012 | 4 | 2012
27464 | Replace Poles & Xarms | 2012-04-20 09:08 | 2012-04-20 | 2012-04-20 12:55 | Calculated | 359 | 359 - Fused Link 359 |  | 111SEG359RET | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 227 | 19 | 24590 | 4316 | 0.17552 | 0.00077267 | 235 | 53384 | 2012/2013 | April-2012 | 4 | 2012
27466 | Replace Rusty 11kv Pothead Bracket | 2012-04-20 09:56 | 2012-04-20 | 2012-04-20 14:51 | Calculated | 609 | 609 - Circuit Breaker 609 (Rural Feeder) 609 |  | No Segment | 201-01 Taharoa | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 166 | 12 | 24590 | 1983 | 0.08064 | 0.000488 | 183 | 30243 | 2012/2013 | April-2012 | 4 | 2012
27467 | Loose Neutral Connection | 2012-04-20 14:30 | 2012-04-20 | 2012-04-20 15:04 | Calculated | TF161 | TF161 - Transformer Fuse: TF161 |  | 101SEG1272-257 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 2 | 24590 | 68 | 0.00277 | 8.1334e-05 | 15 | 512 | 2012/2013 | April-2012 | 4 | 2012
27468 | Reconnect H/V Cables & Disconnect Generators | 2012-04-20 15:07 | 2012-04-20 | 2012-04-20 16:55 | Calculated | TF8R18 | TF8R18 - Transformer Fuse: TF8R18 |  | 406SEG6599-6430 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 90 | 211 | 24590 | 10233 | 0.41614 | 0.0085807 | 800 | 38813 | 2012/2013 | April-2012 | 4 | 2012
27469 | Fuse Pulled Apart | 2012-04-22 15:40 | 2012-04-22 | 2012-04-22 16:51 | Calculated | TF1J3 | TF1J3 - Transformer Fuse: TF1J3 |  | No Segment | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 71 | 1 | 24590 | 71 | 0.00289 | 4.0667e-05 | 15 | 1068 | 2012/2013 | April-2012 | 4 | 2012
27470 | Replace Fuse | 2012-04-23 06:59 | 2012-04-23 | 2012-04-23 08:35 | Calculated | TF4F5 | TF4F5 - Transformer Fuse: TF4F5 |  | No Segment | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 96 | 1 | 24590 | 96 | 0.0039 | 4.0667e-05 | 15 | 1443 | 2012/2013 | April-2012 | 4 | 2012
27472 | Unknown | 2012-04-23 08:33 | 2012-04-23 | 2012-04-23 12:15 | Calculated | TF09P02 | TF09P02 - Transformer Fuse: TF09P02 |  | 609SEG5839-5163 | National Park / Kuratau 609-01 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 222 | 1 | 24590 | 222 | 0.00903 | 4.0667e-05 | 100 | 22215 | 2012/2013 | April-2012 | 4 | 2012
27473 | Tirohanga Feeder Renewal Project | 2012-04-23 08:37 | 2012-04-23 | 2012-04-23 10:53 | Calculated | 787 | 787 - Air Break Switch 787 |  | 123SEG460-787 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 55 | 24590 | 3146 | 0.12794 | 0.0022367 | 850 | 48634 | 2012/2013 | April-2012 | 4 | 2012
27475 | Replace H/V Fuse | 2012-04-24 08:11 | 2012-04-24 | 2012-04-24 09:43 | Calculated | TF08R03 | TF08R03 - Transformer Fuse: TF8R3 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 1 | 24590 | 92 | 0.00374 | 4.0667e-05 | 5 | 460 | 2012/2013 | April-2012 | 4 | 2012
27474 | Changing Poles | 2012-04-24 09:06 | 2012-04-24 | 2012-04-24 11:38 | Calculated | 369 | 369 - Fused Link 369 |  | 122SEG369-678 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 151 | 15 | 24590 | 2267 | 0.09219 | 0.00061 | 195 | 29480 | 2012/2013 | April-2012 | 4 | 2012
27476 | Broken DDO | 2012-04-25 10:46 | 2012-04-25 | 2012-04-25 14:27 | Calculated | TF6Q5 | TF6Q5 - Transformer Fuse: TF6Q5 |  | No Segment | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 12 | 24590 | 683 | 0.02778 | 0.000488 | 95 | 5250 | 2012/2013 | April-2012 | 4 | 2012
27477 | Replace Pole Tx 23 | 2012-04-26 09:05 | 2012-04-26 | 2012-04-26 14:21 | Calculated | 282 | 282 - Air Break Switch 282 |  | 103SEG236-731 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 315 | 18 | 24590 | 5673 | 0.2307 | 0.000732 | 90 | 28368 | 2012/2013 | April-2012 | 4 | 2012
27478 | Resag Line - Rework | 2012-04-26 09:32 | 2012-04-26 | 2012-04-26 10:47 | Calculated | TF162 | TF162 - Transformer Fuse: TF162 |  | 106SEG1790 | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 75 | 4 | 24590 | 300 | 0.0122 | 0.00016267 | 40 | 3006 | 2012/2013 | April-2012 | 4 | 2012
27479 | Replace H/V Fuse | 2012-04-26 17:36 | 2012-04-26 | 2012-04-26 18:40 | Calculated | TF07R10 | TF07R10 - Transformer Fuse: TF7R10 |  | 426SEG5110-5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 2 | 24590 | 128 | 0.00521 | 8.1334e-05 | 7.5 | 481 | 2012/2013 | April-2012 | 4 | 2012
27489 | Install Prop Pole Between Poles 1031051 & 052 | 2012-04-27 11:03 | 2012-04-27 | 2012-04-27 12:35 | Calculated | 556 | 556 - Air Break Switch 556 |  | No Segment | No Asset Group | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 92 | 5 | 24590 | 461 | 0.01875 | 0.00020333 | 25 | 2306 | 2012/2013 | April-2012 | 4 | 2012
27490 | Wire Burning o Xarm | 2012-04-27 11:40 | 2012-04-27 | 2012-04-27 15:30 | Calculated | 662 | 662 - Fused Link 662 |  | 111SEG662 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 230 | 3 | 24590 | 690 | 0.02806 | 0.000122 | 40 | 9207 | 2012/2013 | April-2012 | 4 | 2012
27491 | Insulator Come Adrift | 2012-04-27 13:30 | 2012-04-27 | 2012-04-27 14:53 | Calculated | TF2380 | TF2380 - Transformer Fuse: TF2380 |  | No Segment | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 1 | 24590 | 82 | 0.00333 | 4.0667e-05 | 10 | 821 | 2012/2013 | April-2012 | 4 | 2012
27492 | Replace Link | 2012-04-28 10:16 | 2012-04-28 | 2012-04-28 11:55 | Calculated | 1528 | 1528 - Fused Link 1528 |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 12 | 24590 | 1189 | 0.04835 | 0.000488 | 58 | 5749 | 2012/2013 | April-2012 | 4 | 2012
27493 | Replace H/V Fuse | 2012-04-29 14:06 | 2012-04-29 | 2012-04-29 15:10 | Calculated | TF7I46 | TF7I46 - Transformer Fuse: TF7I46 |  | 402SEG5923-5103 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 6 | 24590 | 385 | 0.01566 | 0.000244 | 60 | 3849 | 2012/2013 | April-2012 | 4 | 2012
27494 | Replace H/V Fuse | 2012-04-29 16:14 | 2012-04-29 | 2012-04-29 17:31 | Calculated | TF4F9 | TF4F9 - Transformer Fuse: TF4F9 |  | No Segment | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 77 | 2 | 24590 | 154 | 0.00626 | 8.1334e-05 | 15 | 1157 | 2012/2013 | April-2012 | 4 | 2012
27495 | Replace Link | 2012-04-30 08:57 | 2012-04-30 | 2012-04-30 09:58 | Calculated | 1121 | 1121 - Fused Link 1121 |  | 114SEG1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 5 | 24590 | 305 | 0.0124 | 0.00020333 | 25 | 1529 | 2012/2013 | April-2012 | 4 | 2012
27496 | Replace Pole 1031473 for Clearance Issues | 2012-04-30 10:06 | 2012-04-30 | 2012-04-30 14:15 | Calculated | 459 | 459 - Air Break Switch 459 |  | 103SEG459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 6 | 24590 | 1489 | 0.06055 | 0.000244 | 65 | 16134 | 2012/2013 | April-2012 | 4 | 2012
27499 | Replace Tx Structure | 2012-05-01 09:06 | 2012-05-01 | 2012-05-01 15:12 | Calculated | TF2193 | TF2193 - Transformer Fuse: TF2193 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 366 | 27 | 24610 | 9886 | 0.40171 | 0.0010971 | 100 | 36618 | 2012/2013 | May-2012 | 5 | 2012
27500 | Install New Tx 3353 on Pole 58 | 2012-05-01 11:00 | 2012-05-01 | 2012-05-01 13:31 | Calculated | 127 | 127 - Circuit Breaker 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 121 | 24610 | 14068 | 0.57164 | 0.0049167 | 1197.5 | 139229 | 2012/2013 | May-2012 | 5 | 2012
27501 | Jumper Off Incoming Link Sect 313 | 2012-05-01 16:50 | 2012-05-01 | 2012-05-01 19:24 | Calculated | 5313 | 5313 - Sectionaliser with Bypass 5313 |  | 403SEG5879-5367 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 154 | 20 | 24610 | 3082 | 0.12523 | 0.00081268 | 120 | 18496 | 2012/2013 | May-2012 | 5 | 2012
27510 | Close CB 796 | 2012-05-02 08:32 | 2012-05-02 | 2012-05-02 16:01 | Calculated | 788 | 788 - Circuit Breaker 788 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 114 | 24610 | 134 | 0.00544 | 0.0046323 | 3280.8571 | 3882 | 2012/2013 | May-2012 | 5 | 2012
27506 | Replace Pole 225 to Prevent Further Slipping | 2012-05-02 09:09 | 2012-05-02 | 2012-05-02 15:46 | Calculated | 2096 | 2096 - Fused Link 2096 |  | 128SEG REG3-1635RET | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 202 | 24610 | 404 | 0.01642 | 0.008208 | 1371 | 2741 | 2012/2013 | May-2012 | 5 | 2012
27507 | Replace Pole 3020284 | 2012-05-02 09:18 | 2012-05-02 | 2012-05-02 15:50 | Calculated | TF680 | TF680 - Transformer Fuse: TF680 |  | 126SEG525 | Rural 126-01 | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 392 | 1 | 24610 | 392 | 0.01593 | 4.0634e-05 | 30 | 11766 | 2012/2013 | May-2012 | 5 | 2012
27509 | Replace H/V Fuse | 2012-05-02 10:51 | 2012-05-02 | 2012-05-02 13:02 | Calculated | TF4025 | TF4025 - Transformer Fuse: TF4025 |  | 402SEG5645-5471 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 1 | 24610 | 131 | 0.00532 | 4.0634e-05 | 200 | 26226 | 2012/2013 | May-2012 | 5 | 2012
27511 | Jumper Off Sect 313 | 2012-05-02 15:49 | 2012-05-02 | 2012-05-02 16:17 | Calculated | 5313 | 5313 - Sectionaliser with Bypass 5313 |  | 403SEG5879-5367 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 28 | 65 | 24610 | 1558 | 0.06331 | 0.0026412 | 383 | 9197 | 2012/2013 | May-2012 | 5 | 2012
27513 | Move Existing Pole Away From Slip | 2012-05-03 08:58 | 2012-05-03 | 2012-05-03 15:32 | Calculated | 2096 | 2096 - Fused Link 2096 |  | 128SEG REG3-1635RET | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 322 | 624 | 24610 | 2543 | 0.10333 | 0.025356 | 3611.5 | 21209 | 2012/2013 | May-2012 | 5 | 2012
27512 | Replace Xarm Pole Top | 2012-05-03 10:04 | 2012-05-03 | 2012-05-03 12:40 | Calculated | 1301 | 1301 - Fused Link 1301 |  | 103SEG1301-1307 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 156 | 1 | 24610 | 156 | 0.00634 | 4.0634e-05 | 3 | 468 | 2012/2013 | May-2012 | 5 | 2012
27514 | Suspect High Load vs Line | 2012-05-04 06:03 | 2012-05-04 | 2012-05-07 07:43 | Calculated | TF1505 | TF1505 - Transformer Fuse: TF1505 |  | 121SEG753-439 | Huirimu 121-01 | Rural D | Huirimu | Arohena Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 2 | 24610 | 200 | 0.00813 | 8.1268e-05 | 16.6667 | 1668 | 2012/2013 | May-2012 | 5 | 2012
27515 | L/V Line Down | 2012-05-04 06:50 | 2012-05-04 | 2012-05-04 10:10 | Calculated | TF858 | TF858 - Transformer Fuse: TF858 |  | No Segment | Wharepapa 122-01 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 200 | 8 | 24610 | 1601 | 0.06505 | 0.00032507 | 50 | 10007 | 2012/2013 | May-2012 | 5 | 2012
27516 | Renew Matiere SWER Sub | 2012-05-04 09:08 | 2012-05-04 | 2012-05-04 16:04 | Calculated | 5017R | 5017R - Recloser with Bypass 5107R |  | No Segment | No Asset Group | Remote Rural F | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 416 | 64 | 24610 | 3485 | 0.14161 | 0.0026006 | 454 | 25700 | 2012/2013 | May-2012 | 5 | 2012
27517 | Replace Red Tagged Pole 1231429 | 2012-05-04 09:37 | 2012-05-04 | 2012-05-04 13:33 | Calculated | 402 | 402 - Fused Link 402 |  | 129SEG402-725 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 236 | 43 | 24610 | 10155 | 0.41264 | 0.0017473 | 615 | 145242 | 2012/2013 | May-2012 | 5 | 2012
27518 | Replace Red Tagged Pole 1281495 | 2012-05-04 10:02 | 2012-05-04 | 2012-05-04 14:32 | Calculated | 1632 | 1632 - Sectionaliser with Incoming Link1632 |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 270 | 11 | 24610 | 2971 | 0.12072 | 0.00044697 | 95 | 25662 | 2012/2013 | May-2012 | 5 | 2012
27519 | Replace Pole 89 & Install New Pole | 2012-05-04 12:04 | 2012-05-04 | 2012-05-04 13:21 | Calculated | 1612 | 1612 - Sectionaliser with Bypass & Links 1612 |  | 128SEG1611-1612 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 77 | 41 | 24610 | 3172 | 0.12889 | 0.001666 | 310 | 23983 | 2012/2013 | May-2012 | 5 | 2012
27520 | Replace H/V Fuse | 2012-05-04 12:37 | 2012-05-04 | 2012-05-04 14:07 | Calculated | TF2142 | TF2142 - Transformer Fuse: TF2142 |  | 128SEG1617RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 1 | 24610 | 89 | 0.00362 | 4.0634e-05 | 15 | 1337 | 2012/2013 | May-2012 | 5 | 2012
27521 | Replace H/V Fuse | 2012-05-04 19:36 | 2012-05-04 | 2012-05-04 20:50 | Calculated | TF9R28 | TF9R28 - Transformer Fuse: TF9R28 |  | 406SEG5896 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 3 | 24610 | 222 | 0.00902 | 0.0001219 | 200 | 14826 | 2012/2013 | May-2012 | 5 | 2012
27523 | Digger vs Line @ Tx 1609 | 2012-05-05 16:15 | 2012-05-05 | 2012-05-05 19:21 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 18 | 24610 | 3350 | 0.13612 | 0.00073141 | 140 | 26061 | 2012/2013 | May-2012 | 5 | 2012
27524 | Bulls in Paddock | 2012-05-06 18:35 | 2012-05-06 | 2012-05-06 19:38 | Calculated | 5690 | 5690 - Fused Link 5690 |  | 416SEG5690 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Animals | BANI:ANIM:AFAR | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 9 | 24610 | 568 | 0.02308 | 0.0003657 | 50 | 3158 | 2012/2013 | May-2012 | 5 | 2012
27525 | Replace Cracked Pole 27 | 2012-05-07 09:20 | 2012-05-07 | 2012-05-07 15:07 | Calculated | 5715 | 5715 - Air Break Switch 5715 |  | 414SEG5999-5715 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 243 | 2 | 24610 | 484 | 0.01967 | 8.1268e-05 | 7.5 | 1816 | 2012/2013 | May-2012 | 5 | 2012
27528 | Replace Poles & Xarms | 2012-05-08 09:26 | 2012-05-08 | 2012-05-08 15:55 | Calculated | 531 | 531 - Air Break Switch 531 |  | 121SEG487-531 | Huirimu 121-04 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 359 | 130 | 24610 | 9671 | 0.39297 | 0.0052824 | 1366.5 | 171943 | 2012/2013 | May-2012 | 5 | 2012
27527 | Replace Pole 269 & Xarm on Pole 268 | 2012-05-08 09:35 | 2012-05-08 | 2012-05-08 15:13 | Calculated | 1725 | 1725 - Fused Link 1725 |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 338 | 6 | 24610 | 2029 | 0.08245 | 0.0002438 | 60 | 20296 | 2012/2013 | May-2012 | 5 | 2012
27529 | Replace H/V Fuse | 2012-05-09 05:45 | 2012-05-09 | 2012-05-09 07:15 | Calculated | TF7D24 | TF7D24 - Transformer Fuse: TF7D24 |  | 413SEG6543-5996 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 29 | 24610 | 2614 | 0.10622 | 0.0011784 | 467.7419 | 42174 | 2012/2013 | May-2012 | 5 | 2012
27530 | Replace Poles & Xarms | 2012-05-09 08:33 | 2012-05-09 | 2012-05-09 15:13 | Calculated | 531 | 531 - Air Break Switch 531 |  | 121SEG487-531 | Huirimu 121-04 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 323 | 33 | 24610 | 10640 | 0.43234 | 0.0013409 | 280 | 90285 | 2012/2013 | May-2012 | 5 | 2012
27531 | Cable Blown Up | 2012-05-09 09:26 | 2012-05-09 | 2012-05-09 13:10 | Calculated | 701 | 701 - Air Break Switch 701 |  | 107SEG213-242 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 224 | 88 | 24610 | 18082 | 0.73474 | 0.0035758 | 400 | 82519 | 2012/2013 | May-2012 | 5 | 2012
27532 | Replace H/V Fuse | 2012-05-09 10:01 | 2012-05-09 | 2012-05-09 12:32 | Calculated | TF12H07 | TF12H07 - Transformer Fuse: TF12H07 |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 151 | 1 | 24610 | 151 | 0.00614 | 4.0634e-05 | 15 | 2268 | 2012/2013 | May-2012 | 5 | 2012
27533 | Replace Links 676 & 717 | 2012-05-10 10:05 | 2012-05-10 | 2012-05-10 13:21 | Calculated | 5675 | 5675 - Air Break Switch 5675 |  | 416SEG5675-5730 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 195 | 14 | 24610 | 2733 | 0.11105 | 0.00056887 | 130 | 25378 | 2012/2013 | May-2012 | 5 | 2012
27534 | Replace Rotten Xarms @ Pole 11620741 | 2012-05-10 10:35 | 2012-05-10 | 2012-05-10 13:06 | Calculated | 1313 | 1313 - Air Break Switch 1313 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 151 | 28 | 24610 | 4232 | 0.17196 | 0.0011377 | 250 | 37787 | 2012/2013 | May-2012 | 5 | 2012
27535 | Replace Stay Wire | 2012-05-10 10:47 | 2012-05-10 | 2012-05-13 12:23 | Calculated | TF34 | TF34 - Transformer Fuse: TF34 |  | 103SEG636-238 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 97 | 2 | 24610 | 192 | 0.0078 | 8.1268e-05 | 15 | 1443 | 2012/2013 | May-2012 | 5 | 2012
27536 | L/V Maintenance | 2012-05-10 11:13 | 2012-05-10 | 2012-05-10 11:44 | Calculated | TF797 | TF797 - Transformer Fuse: TF797 |  | 120SEG497-REG31 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 31 | 3 | 24610 | 93 | 0.00378 | 0.0001219 | 25 | 779 | 2012/2013 | May-2012 | 5 | 2012
27537 | Remove L/V Backfeed & Restore to Normal | 2012-05-10 13:30 | 2012-05-10 | 2012-05-10 14:01 | Calculated | 701 | 701 - Air Break Switch 701 |  | 107SEG213-242 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 30 | 88 | 24610 | 2659 | 0.10805 | 0.0035758 | 400 | 12086 | 2012/2013 | May-2012 | 5 | 2012
27538 | Fire @ Tx 15n3 | 2012-05-10 14:28 | 2012-05-10 | 2012-05-10 17:34 | Calculated | 5154 | 5154 - Circuit Breaker 5154 |  | No Segment | 513-01 Tawhai | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLA | Accidental Contact, Damage or Interference by TLC Staff | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 138 | 24610 | 25695 | 1.0441 | 0.0056075 | 12065 | 2246503 | 2012/2013 | May-2012 | 5 | 2012
27539 | Close CB | 2012-05-10 20:26 | 2012-05-10 | 2012-05-10 20:31 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24610 |  | 0 | 0 |  |  | 2012/2013 | May-2012 | 5 | 2012
27540 | Close CB | 2012-05-10 22:40 | 2012-05-10 | 2012-05-10 22:42 | Calculated | TPTokaanu CB1102 | TPTokaanu CB1102 - 33kV Minimum Oil Circuit Breaker TP1102 |  | No Segment | 515-01 Transpower Tokaanu | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 2765 | 24610 | 5898 | 0.23966 | 0.11235 | 14670.6959 | 31297 | 2012/2013 | May-2012 | 5 | 2012
27561 | OVERLOADED | 2012-05-11 07:47 | 2012-05-11 | 2012-05-11 09:12 | Calculated | TF1452 | TF1452 - Transformer Fuse: TF1452 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 3 | 24610 | 255 | 0.01036 | 0.0001219 | 50 | 4259 | 2012/2013 | May-2012 | 5 | 2012
27562 | FUSE PULLED APART | 2012-05-11 08:17 | 2012-05-11 | 2012-05-11 13:12 | Calculated | TF5E5 | TF5E5 - Transformer Fuse: TF5E5 |  | No Segment | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 295 | 2 | 24610 | 590 | 0.02397 | 8.1268e-05 | 15 | 4426 | 2012/2013 | May-2012 | 5 | 2012
27563 | POLE 901/85/44 ON FIRE | 2012-05-11 08:31 | 2012-05-11 | 2012-05-11 10:55 | Calculated | 5218 | 5218 - Recloser with Bypass 5218 |  | 408SEG5275-5218 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOF | Pole Top Fire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 144 | 73 | 24610 | 10524 | 0.42763 | 0.0029663 | 488 | 70353 | 2012/2013 | May-2012 | 5 | 2012
27565 | DUCKS | 2012-05-11 12:00 | 2012-05-11 | 2012-05-11 13:49 | Calculated | 231 | 231 - Fused Link 231 |  | 107SEG244-575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 2 | 24610 | 218 | 0.00886 | 8.1268e-05 | 65 | 7092 | 2012/2013 | May-2012 | 5 | 2012
27567 | SCHEDULED MAINTENANCE | 2012-05-12 09:10 | 2012-05-12 | 2012-05-12 12:10 | Calculated | TF2595 | TF2595 - Transformer Fuse: TF2595 |  | 111SEG346-REG6 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 180 | 1 | 24610 | 180 | 0.00731 | 4.0634e-05 | 50 | 9007 | 2012/2013 | May-2012 | 5 | 2012
27568 | BROKEN INSULATOR AT ABS 5156 | 2012-05-13 01:01 | 2012-05-13 | 2012-05-13 03:34 | Calculated | 5156 | 5156 - Circuit Breaker Incomer 5156 |  | No Segment | 513-01 Tawhai | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 138 | 24610 | 19754 | 0.80268 | 0.0056075 | 12065 | 1727104 | 2012/2013 | May-2012 | 5 | 2012
27569 | FUSE JUST FELL OUT | 2012-05-13 09:51 | 2012-05-13 | 2012-05-13 11:01 | Calculated | TF9L10 | TF9L10 - Transformer Fuse: TF9L10 |  | No Segment | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 70 | 1 | 24610 | 70 | 0.00284 | 4.0634e-05 | 30 | 2106 | 2012/2013 | May-2012 | 5 | 2012
27570 | LIGHTING - OHA ST | 2012-05-13 10:50 | 2012-05-13 | 2012-05-13 13:58 | Calculated | TF2152 | TF2152 - Transformer Fuse: TF2152 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 188 | 29 | 24610 | 5457 | 0.22174 | 0.0011784 | 100 | 18818 | 2012/2013 | May-2012 | 5 | 2012
27571 | CAR VS POLE | 2012-05-13 15:11 | 2012-05-13 | 2012-05-17 10:57 | Calculated | 103 | 103 - Circuit Breaker Te Kuiti South 103 |  | No Segment | 206-01 Waitete | Urban A | Te Kuiti South | Waitete Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 551 | 1203 | 24610 | 72038 | 2.9272 | 0.048883 | 8242.9167 | 613717 | 2012/2013 | May-2012 | 5 | 2012
27573 | LIGHTNING | 2012-05-14 06:23 | 2012-05-14 | 2012-05-14 10:10 | Calculated | 266 | 266 - Fused Link 266 |  | 107SEG266 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 226 | 6 | 24610 | 1315 | 0.05343 | 0.0002438 | 50 | 10779 | 2012/2013 | May-2012 | 5 | 2012
27574 | LIGHTING | 2012-05-14 07:09 | 2012-05-14 | 2012-05-14 11:22 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 252 | 8 | 24610 | 2019 | 0.08204 | 0.00032507 | 95 | 23977 | 2012/2013 | May-2012 | 5 | 2012
27576 | LIGHTNING | 2012-05-14 07:37 | 2012-05-14 | 2012-05-14 09:38 | Calculated | TF117 | TF117 - Transformer Fuse: TF117 |  | 107SEG243-113 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 3 | 24610 | 360 | 0.01463 | 0.0001219 | 15 | 1803 | 2012/2013 | May-2012 | 5 | 2012
27577 | LIGHTNING | 2012-05-14 08:03 | 2012-05-14 | 2012-05-14 13:39 | Calculated | TF2396 | TF2396 - Transformer Fuse: TF2396 |  | No Segment | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 336 | 1 | 24610 | 336 | 0.01365 | 4.0634e-05 | 10 | 3361 | 2012/2013 | May-2012 | 5 | 2012
27578 | POLE 901/119/9 DOWN | 2012-05-14 08:16 | 2012-05-14 | 2012-05-15 14:41 | Calculated | 5485 | 5485 - Fused Link 5485 |  | 408SEG5485-5791 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 555 | 20 | 24610 | 7642 | 0.31052 | 0.00081268 | 160 | 56707 | 2012/2013 | May-2012 | 5 | 2012
27583 | LIGHTNING | 2012-05-14 08:19 | 2012-05-14 | 2012-05-14 16:11 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 472 | 18 | 24610 | 8498 | 0.34531 | 0.00073141 | 140 | 66101 | 2012/2013 | May-2012 | 5 | 2012
27591 | LIGHTNING | 2012-05-14 08:19 | 2012-05-14 | 2012-05-14 16:11 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 472 | 18 | 24610 | 8498 | 0.34531 | 0.00073141 | 140 | 66101 | 2012/2013 | May-2012 | 5 | 2012
27585 | LIGHTNING | 2012-05-14 11:03 | 2012-05-14 | 2012-05-14 13:39 | Calculated | TF8I6 | TF8I6 - Transformer Fuse: TF8I6 |  | No Segment | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 156 | 3 | 24610 | 468 | 0.01902 | 0.0001219 | 15 | 2342 | 2012/2013 | May-2012 | 5 | 2012
27586 | FAULTY TX 2663 | 2012-05-14 11:06 | 2012-05-14 | 2012-05-14 13:50 | Calculated | TF2663 | TF2663 - Transformer Fuse: TF2663 |  | No Segment | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 4 | 24610 | 656 | 0.02666 | 0.00016254 | 50 | 8209 | 2012/2013 | May-2012 | 5 | 2012
27596 | FUSE PULLED APART | 2012-05-14 14:54 | 2012-05-14 | 2012-05-14 15:57 | Calculated | TF1A28 | TF1A28 - Transformer Fuse: TF1A28 |  | No Segment | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 47 | 24610 | 2973 | 0.1208 | 0.0019098 | 200 | 12653 | 2012/2013 | May-2012 | 5 | 2012
27597 | BIRD | 2012-05-14 15:44 | 2012-05-14 | 2012-05-14 16:36 | Calculated | TF9F5 | TF9F5 - Transformer Fuse: TF9F5 |  | No Segment | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 52 | 1 | 24610 | 52 | 0.00211 | 4.0634e-05 | 15 | 782 | 2012/2013 | May-2012 | 5 | 2012
27598 | LIGHTNING | 2012-05-14 17:00 | 2012-05-14 | 2012-05-14 18:13 | Calculated | 5266 | 5266 - Recloser 5266 |  | 413SEG5260-5266 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 73 | 19 | 24610 | 1389 | 0.05644 | 0.00077204 | 110 | 8044 | 2012/2013 | May-2012 | 5 | 2012
27599 | WIRE OFF INSULATOR AT POLE 149 | 2012-05-14 18:03 | 2012-05-14 | 2012-05-14 22:08 | Calculated | 5867 | 5867 - Recloser with Bypass 5867 |  | 409SEG5761-5867 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 245 | 499 | 24610 | 35543 | 1.4443 | 0.020276 | 3302.1667 | 250586 | 2012/2013 | May-2012 | 5 | 2012
27600 | LIGHTNING | 2012-05-14 18:17 | 2012-05-14 | 2012-05-14 20:04 | Calculated | TF2917 | TF2917 - Transformer Fuse: TF2917 |  | No Segment | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 1 | 24610 | 107 | 0.00435 | 4.0634e-05 | 10 | 1071 | 2012/2013 | May-2012 | 5 | 2012
27601 | LINE DOWN | 2012-05-14 18:34 | 2012-05-14 | 2012-05-15 13:28 | Calculated | 1624 | 1624 - Fused Link 1624 |  | 128SEG1615-1624 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1133 | 7 | 24610 | 7932 | 0.32231 | 0.00028444 | 60 | 67993 | 2012/2013 | May-2012 | 5 | 2012
27602 | FLOATING INSULATORS/ FAULTY SECTIONALISOR | 2012-05-14 19:12 | 2012-05-14 | 2012-05-15 12:21 | Calculated | 5534 | 5534 - Sectionaliser 5534 |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1029 | 15 | 24610 | 15438 | 0.62731 | 0.00060951 | 105 | 108073 | 2012/2013 | May-2012 | 5 | 2012
27603 | TREE ON LINE | 2012-05-15 09:03 | 2012-05-15 | 2012-05-15 09:12 | Calculated | 508 | 508 - Air Break Switch 508 |  | 107SEG508-1798 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 16 | 24610 | 147 | 0.00597 | 0.00065014 | 75 | 689 | 2012/2013 | May-2012 | 5 | 2012
27604 | LV LINE DOWN | 2012-05-15 15:52 | 2012-05-15 | 2012-05-15 16:45 | Calculated | TF85 | TF85 - Transformer Fuse: TF85 |  | 101SEG679-267 | Caves 101-06 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 9 | 24610 | 478 | 0.01942 | 0.0003657 | 30 | 1593 | 2012/2013 | May-2012 | 5 | 2012
27605 | RECLOSER 5107 TRIPPED | 2012-05-15 20:42 | 2012-05-15 | 2012-05-15 21:45 | Calculated | 5107 | 5107 - Recloser with Bypass & Links 5107 |  | 422SEG05F14-5107 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 63 | 64 | 24610 | 4059 | 0.16493 | 0.0026006 | 454 | 28798 | 2012/2013 | May-2012 | 5 | 2012
27606 | LINE DOWN | 2012-05-15 21:08 | 2012-05-15 | 2012-05-16 13:01 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 948 | 34 | 24610 | 9579 | 0.38923 | 0.0013816 | 208.5 | 69309 | 2012/2013 | May-2012 | 5 | 2012
27607 | RECLOSER 5266 TRIPPED | 2012-05-16 06:18 | 2012-05-16 | 2012-05-16 12:07 | Calculated | 5266 | 5266 - Recloser 5266 |  | 413SEG5260-5266 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 348 | 19 | 24610 | 3652 | 0.14839 | 0.00077204 | 110 | 20311 | 2012/2013 | May-2012 | 5 | 2012
27609 | REPLACE POLES AND XARMS | 2012-05-16 09:01 | 2012-05-16 | 2012-05-16 15:16 | Calculated | 425 | 425 - Air Break Switch 425 |  | 121SEG425-748 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 319 | 16 | 24610 | 5098 | 0.20715 | 0.00065014 | 90 | 28676 | 2012/2013 | May-2012 | 5 | 2012
27608 | LIGHTNING | 2012-05-16 09:32 | 2012-05-16 | 2012-05-16 13:39 | Calculated | TF3E2 | TF3E2 - Transformer Fuse: TF3E2 |  | No Segment | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 247 | 1 | 24610 | 247 | 0.01004 | 4.0634e-05 | 3 | 741 | 2012/2013 | May-2012 | 5 | 2012
27610 | BROKEN DDO AT TX 2806 | 2012-05-16 09:41 | 2012-05-16 | 2012-05-16 11:17 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 8 | 24610 | 770 | 0.03129 | 0.00032507 | 95 | 9150 | 2012/2013 | May-2012 | 5 | 2012
27611 | LIGHTNING | 2012-05-16 10:31 | 2012-05-16 | 2012-05-16 14:27 | Calculated | 5277 | 5277 - Sectionaliser with Bypass & Links5277 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 236 | 16 | 24610 | 3784 | 0.15376 | 0.00065014 | 135 | 31932 | 2012/2013 | May-2012 | 5 | 2012
27612 | NEW 11KV EXTENSION(CURRENTLY SUPPLIED OFF TX 3082) | 2012-05-16 10:50 | 2012-05-16 | 2012-05-16 12:11 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 81 | 26 | 24610 | 2109 | 0.0857 | 0.0010565 | 300 | 24345 | 2012/2013 | May-2012 | 5 | 2012
27613 | LIGHTNING | 2012-05-16 18:26 | 2012-05-16 | 2012-05-16 19:07 | Calculated | TF9J7 | TF9J7 - Transformer Fuse: TF9J7 |  | No Segment | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 41 | 1 | 24610 | 41 | 0.00167 | 4.0634e-05 | 15 | 621 | 2012/2013 | May-2012 | 5 | 2012
27614 | REPLACE ABS 5663, LV BOARD TO TX 15N03 AND TIDY UP AROUND RG 12 | 2012-05-17 08:41 | 2012-05-17 | 2012-05-17 16:38 | Calculated | 5148 | 5148 - Air Break Switch 5148 |  | 411SEG5148-5373 | 513-01 Tawhai | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 420 | 150 | 24610 | 62764 | 2.5503 | 0.0060951 | 12280 | 5146035 | 2012/2013 | May-2012 | 5 | 2012
27615 | FIT NEW XARM AND TO FOR TX 1817 | 2012-05-17 09:22 | 2012-05-17 | 2012-05-17 11:57 | Calculated | 1346 | 1346 - Sectionaliser 1346 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 134 | 7 | 24610 | 934 | 0.03795 | 0.00028444 | 57.5 | 7673 | 2012/2013 | May-2012 | 5 | 2012
27616 | LIGHTNING | 2012-05-17 11:11 | 2012-05-17 | 2012-05-17 12:43 | Calculated | TF2986 | TF2986 - Transformer Fuse: TF2986 |  | No Segment | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 1 | 24610 | 92 | 0.00374 | 4.0634e-05 | 10 | 922 | 2012/2013 | May-2012 | 5 | 2012
27617 | INSTALL NEW POLE FOR NEW TX BETWEEN POLE 89 AND 90 | 2012-05-17 12:01 | 2012-05-17 | 2012-05-17 15:33 | Calculated | 1612 | 1612 - Sectionaliser with Bypass & Links 1612 |  | 128SEG1611-1612 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 211 | 41 | 24610 | 8659 | 0.35185 | 0.001666 | 310 | 65477 | 2012/2013 | May-2012 | 5 | 2012
27618 | CT METERING WORK | 2012-05-17 13:00 | 2012-05-17 | 2012-05-17 13:30 | Calculated | 6586 | 6586 - Ring Main Unit 6586 |  | 415SEG6354-6586 | Turoa 415-03 | Rural B | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24610 |  | 0 | 0 |  |  | 2012/2013 | May-2012 | 5 | 2012
27620 | UNKNOWN HV FAULT - LV BACKFED | 2012-05-17 14:28 | 2012-05-17 | 2012-05-17 15:44 | Calculated | TF1A53 | TF1A53 - Transformer Fuse: TF1A53 |  | 402SEG5986 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 29 | 24610 | 2180 | 0.08858 | 0.0011784 | 250 | 18799 | 2012/2013 | May-2012 | 5 | 2012
27621 | SECTIONALISED UNKNOWN FAULT | 2012-05-17 14:53 | 2012-05-17 | 2012-05-17 23:59 | Calculated | 5266 | 5266 - Recloser 5266 |  | 413SEG5260-5266 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 231 | 19 | 24610 | 4266 | 0.17334 | 0.00077204 | 110 | 24795 | 2012/2013 | May-2012 | 5 | 2012
27624 | REPLACE RED TAGGED POLE AND ABS 434 | 2012-05-18 08:51 | 2012-05-18 | 2012-05-18 15:35 | Calculated | 634 | 634 - Air Break Switch 634 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 394 | 229 | 24610 | 9106 | 0.37001 | 0.0093052 | 2950 | 104741 | 2012/2013 | May-2012 | 5 | 2012
27629 | BURN OUT DDO | 2012-05-18 10:04 | 2012-05-18 | 2012-05-18 12:08 | Calculated | TF438 | TF438 - Transformer Fuse: TF438 |  | 112SEG645-307 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 63 | 24610 | 6703 | 0.27237 | 0.0025599 | 400 | 31073 | 2012/2013 | May-2012 | 5 | 2012
27630 | BIRD | 2012-05-18 11:01 | 2012-05-18 | 2012-05-18 13:19 | Calculated | TF8P6 | TF8P6 - Transformer Fuse: TF8P6 |  | 426SEG5892-5240 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 138 | 1 | 24610 | 138 | 0.00561 | 4.0634e-05 | 15 | 2072 | 2012/2013 | May-2012 | 5 | 2012
27631 | HV FUSE BLEW | 2012-05-18 12:01 | 2012-05-18 | 2012-05-18 13:38 | Calculated | TF1034 | TF1034 - Transformer Fuse: TF1034 |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 2 | 24610 | 194 | 0.00788 | 8.1268e-05 | 15 | 1458 | 2012/2013 | May-2012 | 5 | 2012
27632 | FAULTY INSULATOR | 2012-05-18 13:09 | 2012-05-18 | 2012-05-18 15:13 | Calculated | 5869 | 5869 - Earth Working Link 5869 |  | 413SEG5869 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 124 | 1 | 24610 | 124 | 0.00504 | 4.0634e-05 | 15 | 1863 | 2012/2013 | May-2012 | 5 | 2012
27634 | POSSUM | 2012-05-18 13:55 | 2012-05-18 | 2012-05-18 14:58 | Calculated | TF80 | TF80 - Transformer Fuse: TF80 |  | No Segment | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 2 | 24610 | 124 | 0.00504 | 8.1268e-05 | 15 | 932 | 2012/2013 | May-2012 | 5 | 2012
27635 | BURNT OUT LV FUSE BOXES | 2012-05-18 16:48 | 2012-05-18 | 2012-05-18 17:55 | Calculated | TF453 | TF453 - Transformer Fuse: TF453 |  | 111SEG358-707 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 3 | 24610 | 201 | 0.00817 | 0.0001219 | 30 | 2016 | 2012/2013 | May-2012 | 5 | 2012
27623 | INSTALL NEW TAP OFF AT POLE 1190092 | 2012-05-19 09:55 | 2012-05-19 | 2012-05-19 12:06 | Calculated | 406 | 406 - Air Break Switch 406 |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 55 | 23 | 24610 | 1247 | 0.05067 | 0.00093458 | 495 | 26845 | 2012/2013 | May-2012 | 5 | 2012
27636 | FUSE PULLED APART | 2012-05-20 09:29 | 2012-05-20 | 2012-05-20 11:32 | Calculated | TF2436 | TF2436 - Transformer Fuse: TF2436 |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 1 | 24610 | 122 | 0.00496 | 4.0634e-05 | 100 | 12211 | 2012/2013 | May-2012 | 5 | 2012
27637 | GOOSE LIE DOWN | 2012-05-20 15:11 | 2012-05-20 | 2012-05-20 17:52 | Calculated | 5876 | 5876 - Circuit Breaker Manunui SF6 5876 |  | No Segment | 510-01 Manunui | Rural B | Manunui / AFFCO Retired | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 589 | 24610 | 20027 | 0.81377 | 0.023933 | 4346.2585 | 123495 | 2012/2013 | May-2012 | 5 | 2012
27638 | PRIVATE LINE TREE WORK | 2012-05-21 08:58 | 2012-05-21 | 2012-05-21 09:54 | Calculated | TF345 | TF345 - Transformer Fuse: TF345 |  | No Segment | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 56 | 7 | 24610 | 393 | 0.01597 | 0.00028444 | 30 | 1685 | 2012/2013 | May-2012 | 5 | 2012
27639 | FUSE PULLED APART | 2012-05-21 09:24 | 2012-05-21 | 2012-05-21 09:58 | Calculated | TF20L62 | TF20L62 - Transformer Fuse: TF20L62 |  | 414SEG6644-5643 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 11 | 24610 | 375 | 0.01524 | 0.00044697 | 100 | 3411 | 2012/2013 | May-2012 | 5 | 2012
27640 | FUSE PULLED APART | 2012-05-21 13:00 | 2012-05-21 | 2012-05-21 16:05 | Calculated | TF2881 | TF2881 - Transformer Fuse: TF2881 |  | No Segment | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 184 | 1 | 24610 | 184 | 0.00748 | 4.0634e-05 | 10 | 1841 | 2012/2013 | May-2012 | 5 | 2012
27641 | TREE FELLED THROUGH LINE | 2012-05-21 14:03 | 2012-05-21 | 2012-05-21 15:30 | Calculated | 1322 | 1322 - Sectionaliser 1322 |  | 117SEG1322 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 87 | 27 | 24610 | 2353 | 0.09561 | 0.0010971 | 161 | 14033 | 2012/2013 | May-2012 | 5 | 2012
27642 | UPGARADE TX 2293 | 2012-05-21 14:12 | 2012-05-21 | 2012-05-21 16:23 | Calculated | TF2293 | TF2293 - Transformer Fuse: TF2293 |  | 114SEG1109-1110 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 130 | 3 | 24610 | 390 | 0.01585 | 0.0001219 | 30 | 3904 | 2012/2013 | May-2012 | 5 | 2012
27644 | REPAIR LV CONNECTION | 2012-05-22 11:48 | 2012-05-22 | 2012-05-22 12:19 | Calculated | TF1909 | TF1909 - Transformer Fuse: TF1909 |  | 116SEG1355-1327 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 2 | 24610 | 62 | 0.00252 | 8.1268e-05 | 10 | 311 | 2012/2013 | May-2012 | 5 | 2012
27645 | LIGHTNING | 2012-05-23 09:17 | 2012-05-23 | 2012-05-23 13:19 | Calculated | TF2908 | TF2908 - Transformer Fuse: TF2908 |  | No Segment | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 242 | 1 | 24610 | 242 | 0.00983 | 4.0634e-05 | 15 | 3631 | 2012/2013 | May-2012 | 5 | 2012
27646 | RENEWAL OF PUKAWA SWER SUB AND REPLACE H STRUCTURE 4060048 | 2012-05-23 09:40 | 2012-05-23 | 2012-05-23 17:29 | Calculated | 5896 | 5896 - Solid Link 5896 |  | 406SEG5896 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 449 | 370 | 24610 | 50800 | 2.0642 | 0.015035 | 2133.75 | 412718 | 2012/2013 | May-2012 | 5 | 2012
27648 | NEW 11KV EXTENSION | 2012-05-23 10:08 | 2012-05-23 | 2012-05-23 13:18 | Calculated | 451 | 451 - Air Break Switch 451 |  | 129SEG451-787 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 82 | 26 | 24610 | 2116 | 0.08598 | 0.0010565 | 260 | 21168 | 2012/2013 | May-2012 | 5 | 2012
27647 | UPGRADE TX 3277 | 2012-05-23 10:24 | 2012-05-23 | 2012-05-23 13:19 | Calculated | TF3277 | TF3277 - Transformer Fuse: TF3277 |  | 116SEG805 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 175 | 1 | 24610 | 175 | 0.00711 | 4.0634e-05 | 100 | 17520 | 2012/2013 | May-2012 | 5 | 2012
27649 | DUCKS | 2012-05-23 11:26 | 2012-05-23 | 2012-05-23 13:56 | Calculated | 5717 | 5717 - Fused Link 5717 |  | 416SEG5717 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 5 | 24610 | 750 | 0.03048 | 0.00020317 | 45 | 6757 | 2012/2013 | May-2012 | 5 | 2012
27651 | SHIFT POLE AND UPGRADE TX 1673 TO 75KVA | 2012-05-24 09:32 | 2012-05-24 | 2012-05-24 15:58 | Calculated | 655 | 655 - Fused Link 655 |  | 116SEG655 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 386 | 2 | 24610 | 772 | 0.03137 | 8.1268e-05 | 65 | 25100 | 2012/2013 | May-2012 | 5 | 2012
27652 | PRIVATE LINE MAINTENANCE | 2012-05-24 12:30 | 2012-05-24 | 2012-05-24 13:55 | Calculated | TF1900 | TF1900 - Transformer Fuse: TF1900 |  | 114SEG1128 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 85 | 2 | 24610 | 170 | 0.00691 | 8.1268e-05 | 10 | 852 | 2012/2013 | May-2012 | 5 | 2012
27653 | FAULTY LV CONNECTION | 2012-05-24 14:43 | 2012-05-24 | 2012-05-24 15:42 | Calculated | TF1957 | TF1957 - Transformer Fuse: TF1957 |  | 114SEG1125-2160 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 3 | 24610 | 177 | 0.00719 | 0.0001219 | 15 | 887 | 2012/2013 | May-2012 | 5 | 2012
27655 | FUSE PULLED APART | 2012-05-25 08:48 | 2012-05-25 | 2012-05-25 09:52 | Calculated | TF1807 | TF1807 - Transformer Fuse: TF1807 |  | 117SEG1292-1300 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 2 | 24610 | 128 | 0.0052 | 8.1268e-05 | 15 | 963 | 2012/2013 | May-2012 | 5 | 2012
27654 | BROKEN XARM | 2012-05-25 09:19 | 2012-05-25 | 2012-05-25 16:08 | Calculated | 634 | 634 - Air Break Switch 634 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 388 | 6 | 24610 | 2324 | 0.09443 | 0.0002438 | 45 | 17430 | 2012/2013 | May-2012 | 5 | 2012
27657 | MAGPIE | 2012-05-25 13:10 | 2012-05-25 | 2012-05-25 14:34 | Calculated | TF11K23 | TF11K23 - Transformer Fuse: TF11K23 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 3 | 24610 | 252 | 0.01024 | 0.0001219 | 15 | 1261 | 2012/2013 | May-2012 | 5 | 2012
27658 | MAGPIE | 2012-05-25 17:22 | 2012-05-25 | 2012-05-25 18:11 | Calculated | TF1216 | TF1216 - Transformer Fuse: TF1216 |  | 112SEG326-288 | Otorohanga 112-06 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 3 | 24610 | 147 | 0.00597 | 0.0001219 | 10 | 491 | 2012/2013 | May-2012 | 5 | 2012
27659 | BRANCH ON LINE | 2012-05-27 11:20 | 2012-05-27 | 2012-05-27 12:51 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 27 | 24610 | 2437 | 0.09902 | 0.0010971 | 281.4286 | 25403 | 2012/2013 | May-2012 | 5 | 2012
27661 | WIND | 2012-05-27 11:48 | 2012-05-27 | 2012-05-27 12:45 | Calculated | TF191 | TF191 - Transformer Fuse: TF191 |  | No Segment | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 5 | 24610 | 285 | 0.01158 | 0.00020317 | 15 | 857 | 2012/2013 | May-2012 | 5 | 2012
27664 | FAULTY TX 478 | 2012-05-28 13:02 | 2012-05-28 | 2012-05-28 15:45 | Calculated | TF478 | TF478 - Transformer Fuse: TF478 |  | No Segment | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 5 | 24610 | 815 | 0.03312 | 0.00020317 | 300 | 48935 | 2012/2013 | May-2012 | 5 | 2012
27665 | TO CONNECT IN NEW XIRIA SWITCHGEAR | 2012-05-29 06:01 | 2012-05-29 | 2012-05-29 14:40 | Calculated | TF20L2 | TF20L2 - Transformer Fuse: TF20L2 |  | 414SEG5715-5925RET | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 67 | 83 | 24610 | 5577 | 0.22662 | 0.0033726 | 793.4783 | 53321 | 2012/2013 | May-2012 | 5 | 2012
27666 | LV MAINTENANCE | 2012-05-29 11:33 | 2012-05-29 | 2012-05-29 12:22 | Calculated | TF2156 | TF2156 - Transformer Fuse: TF2156 |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 5 | 24610 | 245 | 0.00996 | 0.00020317 | 15 | 737 | 2012/2013 | May-2012 | 5 | 2012
27667 | FUSE BURNT UP | 2012-05-29 12:19 | 2012-05-29 | 2012-05-29 12:31 | Calculated | TF1447 | TF1447 - Transformer Fuse: TF1447 |  | 104SEG207-546 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 16 | 24610 | 194 | 0.00788 | 0.00065014 | 300 | 3640 | 2012/2013 | May-2012 | 5 | 2012
27668 | LV MAINTENANCE | 2012-05-29 12:33 | 2012-05-29 | 2012-05-29 13:40 | Calculated | TF8E2 | TF8E2 - Transformer Fuse: TF8E2 |  | 413SEG5579-5571 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 67 | 4 | 24610 | 268 | 0.01089 | 0.00016254 | 10 | 671 | 2012/2013 | May-2012 | 5 | 2012
27669 | POSSUM | 2012-05-30 00:10 | 2012-05-30 | 2012-05-30 01:17 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 103 | 24610 | 6832 | 0.27761 | 0.0041853 | 988 | 65537 | 2012/2013 | May-2012 | 5 | 2012
27671 | LINE DOWN | 2012-05-30 10:10 | 2012-05-30 | 2012-05-30 12:34 | Calculated | 1714 | 1714 - Fused Link 1714 |  | 115SEG1714 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 13 | 24610 | 1873 | 0.07611 | 0.00052824 | 95 | 13694 | 2012/2013 | May-2012 | 5 | 2012
27672 | HV FUSE BLEW | 2012-05-30 10:45 | 2012-05-30 | 2012-05-30 13:38 | Calculated | TF4163 | TF4163 - Transformer Fuse: TF4163 |  | No Segment | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 173 | 1 | 24610 | 173 | 0.00703 | 4.0634e-05 | 30 | 5194 | 2012/2013 | May-2012 | 5 | 2012
27673 | LV LINE DOWN | 2012-05-30 11:31 | 2012-05-30 | 2012-05-30 13:01 | Calculated | TF727 | TF727 - Transformer Fuse: TF727 |  | No Segment | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 3 | 24610 | 267 | 0.01085 | 0.0001219 | 25 | 2229 | 2012/2013 | May-2012 | 5 | 2012
27674 | FAULTY LA | 2012-05-30 15:58 | 2012-05-30 | 2012-05-30 17:29 | Calculated | 1780 | 1780 - Air Break Switch 1780 |  | 129SEG1780 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 1 | 24610 | 91 | 0.0037 | 4.0634e-05 | 50 | 4559 | 2012/2013 | May-2012 | 5 | 2012
27675 | RECLOSER 5440 TRIPPED | 2012-05-30 16:56 | 2012-05-30 | 2012-05-30 17:22 | Calculated | 5440 | 5440 - Recloser with Bypass & Links 5440 |  | 409SEG5439-5440 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 26 | 28 | 24610 | 730 | 0.02966 | 0.0011377 | 212.5 | 5546 | 2012/2013 | May-2012 | 5 | 2012
27688 | LV WARPPED | 2012-05-31 12:22 | 2012-05-31 | 2012-05-31 15:37 | Calculated | TF191 | TF191 - Transformer Fuse: TF191 |  | No Segment | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 195 | 5 | 24610 | 975 | 0.03962 | 0.00020317 | 15 | 2927 | 2012/2013 | May-2012 | 5 | 2012
27689 | REMOVE TERMINATION JOINTS AND CABLE UP POLE - INSTALL THRU JOINT AND BURY CABLE - PHASE OUT AT ABS 984 | 2012-06-01 09:06 | 2012-06-01 | 2012-06-01 17:55 | Calculated | 5955 | 5955 - Circuit Breaker Northern 5955 |  | No Segment | 508-01 Borough | Rural B | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 511 | 24559 | 30302 | 1.2338 | 0.020807 | 2355.7746 | 139697 | 2012/2013 | June-2012 | 6 | 2012
27690 | CAR VS LV POLE | 2012-06-02 02:16 | 2012-06-02 | 2012-06-02 09:28 | Calculated | TF7D30 | TF7D30 - Transformer Fuse: TF7D30 |  | 413SEG6543-5996 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 432 | 7 | 24559 | 3025 | 0.12317 | 0.00028503 | 50 | 21609 | 2012/2013 | June-2012 | 6 | 2012
27691 | JUMPER OFF AT ABS 920 | 2012-06-02 17:34 | 2012-06-02 | 2012-06-02 23:09 | Calculated | 5132 | 5132 - Circuit Breaker Manunui SF6 5132 |  | No Segment | 510-01 Manunui | Rural B | Southern | Manunui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 637 | 24559 | 11811 | 0.48092 | 0.025938 | 4215.1667 | 73190 | 2012/2013 | June-2012 | 6 | 2012
27692 | CT METERING WORK | 2012-06-03 09:08 | 2012-06-03 | 2012-06-03 11:25 | Calculated | 658 | 658 - Air Break Switch 658 |  | No Segment | 208-01 Oparure | Remote Rural E | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 136 | 1 | 24559 | 136 | 0.00554 | 4.0718e-05 | 160 | 21760 | 2012/2013 | June-2012 | 6 | 2012
27693 | DUCKS | 2012-06-03 12:14 | 2012-06-03 | 2012-06-03 13:16 | Calculated | 763 | 763 - Fused Link 763 |  | 108SEG763-2140 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 2 | 24559 | 124 | 0.00505 | 8.1437e-05 | 530 | 33054 | 2012/2013 | June-2012 | 6 | 2012
27694 | CT METERING WORK | 2012-06-03 12:49 | 2012-06-03 | 2012-06-03 14:33 | Calculated | TF1150A | TF1150A - Transformer Fuse: TF1150A |  | 106SEG227-586 | Rangitoto 106-02 | Urban A | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 104 | 2 | 24559 | 208 | 0.00847 | 8.1437e-05 | 750 | 78187 | 2012/2013 | June-2012 | 6 | 2012
27695 | REPLACE OH TX 20M07 WITH NEW GM TX | 2012-06-05 08:07 | 2012-06-05 | 2012-06-05 15:44 | Calculated | TF20M7 | TF20M7 - Transformer Fuse: TF20M7 |  | 414SEG5701-6420 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 457 | 63 | 24559 | 28799 | 1.1726 | 0.0025653 | 98.4375 | 44999 | 2012/2013 | June-2012 | 6 | 2012
27696 | SECTIONALISOR 5305 TRIPPED | 2012-06-05 18:15 | 2012-06-05 | 2012-06-06 17:00 | Calculated | 5305 | 5305 - Sectionaliser with Bypass & Links 5305 |  | 413SEG5305-5306 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 427 | 27 | 24559 | 11112 | 0.45246 | 0.0010994 | 130 | 53577 | 2012/2013 | June-2012 | 6 | 2012
27701 | REPLACE OH TX20M8 WITH NEW GM TX | 2012-06-06 08:39 | 2012-06-06 | 2012-06-06 14:30 | Calculated | TF20M8 | TF20M8 - Transformer Fuse: TF20M8 |  | No Segment | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 350 | 70 | 24559 | 24520 | 0.99841 | 0.0028503 | 200 | 70059 | 2012/2013 | June-2012 | 6 | 2012
27703 | DIGGER VS LINE | 2012-06-06 14:40 | 2012-06-06 | 2012-06-06 15:49 | Calculated | TF1214 | TF1214 - Transformer Fuse: TF1214 |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 5 | 24559 | 345 | 0.01405 | 0.00020359 | 105 | 7262 | 2012/2013 | June-2012 | 6 | 2012
27704 | SCHEDULED MAINTENANCE | 2012-06-07 09:31 | 2012-06-07 | 2012-06-07 14:12 | Calculated | TF2644 | TF2644 - Transformer Fuse: TF2644 |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 281 | 4 | 24559 | 1124 | 0.04577 | 0.00016287 | 40 | 11245 | 2012/2013 | June-2012 | 6 | 2012
27705 | REPLACE POLES AND HARDWARE | 2012-06-07 10:04 | 2012-06-07 | 2012-06-07 14:20 | Calculated | 665 | 665 - Fused Link 665 |  | 111SEG665 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 256 | 8 | 24559 | 2049 | 0.08343 | 0.00032575 | 60 | 15369 | 2012/2013 | June-2012 | 6 | 2012
27707 | UPGRADE TX 1168 | 2012-06-08 10:06 | 2012-06-08 | 2012-06-08 16:11 | Calculated | TF1168 | TF1168 - Transformer Fuse: TF1168 |  | 110SEG323-644 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 365 | 4 | 24559 | 1460 | 0.05945 | 0.00016287 | 15 | 5477 | 2012/2013 | June-2012 | 6 | 2012
27706 | PULL POLE STRAIGHT AND ATTACH NEW STAY | 2012-06-08 10:06 | 2012-06-08 | 2012-06-08 12:10 | Calculated | 374 | 374 - Fused Link 374 |  | 111SEG374-783 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 123 | 20 | 24559 | 2470 | 0.10057 | 0.00081437 | 335 | 41372 | 2012/2013 | June-2012 | 6 | 2012
27708 | REPIAR EARTH | 2012-06-08 10:32 | 2012-06-08 | 2012-06-08 16:11 | Calculated | TF8Q4 | TF8Q4 - Transformer Fuse: TF8Q4 |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 339 | 1 | 24559 | 339 | 0.0138 | 4.0718e-05 | 5 | 1696 | 2012/2013 | June-2012 | 6 | 2012
27709 | MAGPIE ACROSS CB 727 | 2012-06-08 15:42 | 2012-06-08 | 2012-06-08 15:47 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 1395 | 24559 | 1581 | 0.06438 | 0.056802 | 12657.5 | 14451 | 2012/2013 | June-2012 | 6 | 2012
27710 | SCHEDULED MAINTENANCE | 2012-06-11 09:25 | 2012-06-11 | 2012-06-11 09:57 | Calculated | TF1537 | TF1537 - Transformer Fuse: TF1537 |  | 111SEG359RET | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 32 | 3 | 24559 | 96 | 0.00391 | 0.00012215 | 15 | 482 | 2012/2013 | June-2012 | 6 | 2012
27713 | RESAG LINE TO TX 1505 | 2012-06-11 10:44 | 2012-06-11 | 2012-06-11 15:08 | Calculated | 439 | 439 - Air Break Switch 439 |  | 121SEG439-724 | Huirimu 121-01 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 191 | 9 | 24559 | 1711 | 0.06967 | 0.00036646 | 76.6667 | 14578 | 2012/2013 | June-2012 | 6 | 2012
27723 | REPLACE LA, DDOS AND DAMAGED CONDUCTOR | 2012-06-12 09:05 | 2012-06-12 | 2012-06-12 14:09 | Calculated | 1643 | 1643 - Fused Link 1643 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 304 | 9 | 24559 | 2737 | 0.11145 | 0.00036646 | 80 | 24329 | 2012/2013 | June-2012 | 6 | 2012
27724 | REPLACE POLES AND HARDWARE - ALSO REPLCE LINK | 2012-06-12 09:32 | 2012-06-12 | 2012-06-12 14:34 | Calculated | 648 | 648 - Fused Link 648 |  | 111SEG648 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 9 | 24559 | 2719 | 0.11071 | 0.00036646 | 70 | 21149 | 2012/2013 | June-2012 | 6 | 2012
27725 | REPLACE HV FUSE AT TX 2010 | 2012-06-12 14:31 | 2012-06-12 | 2012-06-12 17:29 | Calculated | TF2010 | TF2010 - Transformer Fuse: TF2010 |  | 111SEG1148 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 2 | 24559 | 355 | 0.01445 | 8.1437e-05 | 25 | 4447 | 2012/2013 | June-2012 | 6 | 2012
27726 | CHANGEING POLES AND XARMS | 2012-06-13 08:45 | 2012-06-13 | 2012-06-13 15:17 | Calculated | 361 | 361 - Air Break Switch 361 |  | 102SEG191-361 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 339 | 9 | 24559 | 3043 | 0.12391 | 0.00036646 | 75 | 25358 | 2012/2013 | June-2012 | 6 | 2012
27727 | HV FUSE BLEW | 2012-06-13 10:40 | 2012-06-13 | 2012-06-13 15:47 | Calculated | TF2561 | TF2561 - Transformer Fuse: TF2561 |  | No Segment | Rangitoto 106-02 | Urban A | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 307 | 3 | 24559 | 921 | 0.0375 | 0.00012215 | 25 | 7678 | 2012/2013 | June-2012 | 6 | 2012
27728 | CHANGING POLES AND XARMS | 2012-06-14 09:02 | 2012-06-14 | 2012-06-14 15:04 | Calculated | 340 | 340 - Air Break Switch 340 |  | 102SEG340-191 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 323 | 9 | 24559 | 2899 | 0.11804 | 0.00036646 | 75 | 24161 | 2012/2013 | June-2012 | 6 | 2012
27731 | REPLACE BLOWN HV FUSE AT TX 2638 | 2012-06-14 18:28 | 2012-06-14 | 2012-06-14 20:04 | Calculated | TF2638 | TF2638 - Transformer Fuse: TF2638 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 1 | 24559 | 95 | 0.00387 | 4.0718e-05 | 25 | 2378 | 2012/2013 | June-2012 | 6 | 2012
27732 | REPLACE POLES 4090147 AND 4090149 | 2012-06-15 09:33 | 2012-06-15 | 2012-06-15 14:14 | Calculated | 5138 | 5138 - Air Break Switch 5138 |  | 409SEG5138-5235 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 263 | 55 | 24559 | 14421 | 0.5872 | 0.0022395 | 436 | 114319 | 2012/2013 | June-2012 | 6 | 2012
27735 | SUSPECT STOCK RUBBING POLE | 2012-06-18 04:37 | 2012-06-18 | 2012-06-18 05:26 | Calculated | 120 | 120 - Circuit Breaker 120 |  | No Segment | 203-01 Te Waireka Road | Urban A | McDonalds | Te Waireka Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AFAR | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 469 | 24559 | 4377 | 0.17822 | 0.019097 | 5225.3077 | 48769 | 2012/2013 | June-2012 | 6 | 2012
27736 | DUCKS | 2012-06-18 07:01 | 2012-06-18 | 2012-06-18 09:51 | Calculated | TF2485 | TF2485 - Transformer Fuse: TF2485 |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 5 | 24559 | 850 | 0.03461 | 0.00020359 | 30 | 5105 | 2012/2013 | June-2012 | 6 | 2012
27741 | LIGHTNING | 2012-06-18 09:46 | 2012-06-18 | 2012-06-19 00:30 | Calculated | TF535 | TF535 - Transformer Fuse: TF535 |  | No Segment | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 884 | 3 | 24559 | 2652 | 0.10798 | 0.00012215 | 15 | 13262 | 2012/2013 | June-2012 | 6 | 2012
27737 | REMOVE TEMP TX 15N3 AND REPLACE WITH PERMENANT ONE | 2012-06-18 09:58 | 2012-06-18 | 2012-06-18 15:28 | Calculated | 6167 | 6167 - Fused Link 6167 |  | 419SEG6167 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 330 | 8 | 24559 | 2642 | 0.10758 | 0.00032575 | 100 | 33026 | 2012/2013 | June-2012 | 6 | 2012
27742 | LIGHTNING | 2012-06-18 09:59 | 2012-06-18 | 2012-06-19 01:30 | Calculated | TF536 | TF536 - Transformer Fuse: TF536 |  | No Segment | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 931 | 3 | 24559 | 2793 | 0.11373 | 0.00012215 | 25 | 23278 | 2012/2013 | June-2012 | 6 | 2012
27740 | COCKY VS POLE | 2012-06-18 12:47 | 2012-06-18 | 2012-06-18 15:28 | Calculated | 443 | 443 - Fused Link 443 |  | 122SEG443 | Wharepapa 122-01 | Rural D | Wharepapa | Arohena Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 18 | 24559 | 2902 | 0.11816 | 0.00073293 | 130 | 20960 | 2012/2013 | June-2012 | 6 | 2012
27743 | LIGHTNING | 2012-06-18 22:18 | 2012-06-18 | 2012-06-18 23:30 | Calculated | TF508 | TF508 - Transformer Fuse: TF508 |  | No Segment | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 3 | 24559 | 216 | 0.0088 | 0.00012215 | 15 | 1082 | 2012/2013 | June-2012 | 6 | 2012
27744 | LIGHTNING | 2012-06-19 00:11 | 2012-06-19 | 2012-06-19 07:37 | Calculated | TF419 | TF419 - Transformer Fuse: TF419 |  | No Segment | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 446 | 2 | 24559 | 892 | 0.03632 | 8.1437e-05 | 25 | 11152 | 2012/2013 | June-2012 | 6 | 2012
27745 | LIGHTNING | 2012-06-19 03:20 | 2012-06-19 | 2012-06-19 05:47 | Calculated | TF2416 | TF2416 - Transformer Fuse: TF2416 |  | 112SEG646-313 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 28 | 24559 | 4119 | 0.16772 | 0.0011401 | 200 | 29423 | 2012/2013 | June-2012 | 6 | 2012
27746 | LINE DOWN AT TX 439 - LIGHTNING MULTIPLE TXS | 2012-06-19 06:08 | 2012-06-19 | 2012-06-19 16:36 | Calculated | 260 | 260 - Circuit Breaker 260 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 627 | 23 | 24559 | 5826 | 0.23722 | 0.00093652 | 185.5 | 47740 | 2012/2013 | June-2012 | 6 | 2012
27747 | LIGHTNING | 2012-06-19 06:56 | 2012-06-19 | 2012-06-19 08:43 | Calculated | TF1192 | TF1192 - Transformer Fuse: TF1192 |  | 110SEG642-343 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 3 | 24559 | 321 | 0.01307 | 0.00012215 | 25 | 2678 | 2012/2013 | June-2012 | 6 | 2012
27748 | LIGHTNING | 2012-06-19 07:41 | 2012-06-19 | 2012-06-19 09:14 | Calculated | TF966 | TF966 - Transformer Fuse: TF966 |  | No Segment | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 2 | 24559 | 186 | 0.00757 | 8.1437e-05 | 10 | 931 | 2012/2013 | June-2012 | 6 | 2012
27749 | LIGHTNING | 2012-06-19 08:48 | 2012-06-19 | 2012-06-19 11:45 | Calculated | 280 | 280 - Fused Link 280 |  | 125SEG280-292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 12 | 24559 | 1729 | 0.0704 | 0.00048862 | 118 | 17193 | 2012/2013 | June-2012 | 6 | 2012
27750 | LIGHTNING | 2012-06-19 08:55 | 2012-06-19 | 2012-06-19 15:47 | Calculated | TF1547 | TF1547 - Transformer Fuse: TF1547 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 412 | 2 | 24559 | 824 | 0.03355 | 8.1437e-05 | 45 | 18546 | 2012/2013 | June-2012 | 6 | 2012
27751 | DEAD BIRD AT BASE OF THE POLE | 2012-06-19 08:56 | 2012-06-19 | 2012-06-19 10:49 | Calculated | TF08R03 | TF08R03 - Transformer Fuse: TF8R3 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 1 | 24559 | 113 | 0.0046 | 4.0718e-05 | 5 | 565 | 2012/2013 | June-2012 | 6 | 2012
27752 | LIGHTNING - FAULTY TX | 2012-06-19 09:09 | 2012-06-19 | 2012-06-19 14:23 | Calculated | TF3126 | TF3126 - Transformer Fuse: TF3126 |  | No Segment | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 314 | 1 | 24559 | 314 | 0.01279 | 4.0718e-05 | 15 | 4711 | 2012/2013 | June-2012 | 6 | 2012
27754 | INSTALL NEW PROP POLE FOR LOW LINES - POLE 1142100 | 2012-06-19 10:06 | 2012-06-19 | 2012-06-19 11:22 | Calculated | 1125 | 1125 - Fused Link 1125 |  | 114SEG1125-2160 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 76 | 15 | 24559 | 1144 | 0.04658 | 0.00061077 | 98 | 7475 | 2012/2013 | June-2012 | 6 | 2012
27756 | LIGHTNING | 2012-06-20 08:00 | 2012-06-20 | 2012-06-20 10:45 | Calculated | TF1835 | TF1835 - Transformer Fuse: TF1835 |  | 125SEG137 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 165 | 2 | 24559 | 330 | 0.01344 | 8.1437e-05 | 15 | 2477 | 2012/2013 | June-2012 | 6 | 2012
27758 | REPLACE COMPLETE STRUCTURE TX 1351 | 2012-06-20 09:34 | 2012-06-20 | 2012-06-20 14:55 | Calculated | 291 | 291 - Air Break Switch 291 |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 321 | 31 | 24559 | 9954 | 0.40531 | 0.0012623 | 248 | 79632 | 2012/2013 | June-2012 | 6 | 2012
27759 | EARTH TESTING | 2012-06-20 10:31 | 2012-06-20 | 2012-06-20 11:40 | Calculated | TF4291 | TF4291 - Transformer Fuse TF4291 |  | 421SEG5362-5933 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 0 | 0 | 24559 |  | 0 | 0 |  |  | 2012/2013 | June-2012 | 6 | 2012
27760 | LV LINE DOWN | 2012-06-20 20:23 | 2012-06-20 | 2012-06-20 21:24 | Calculated | TF636 | TF636 - Transformer Fuse: TF636 |  | No Segment | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 2 | 24559 | 122 | 0.00497 | 8.1437e-05 | 15 | 916 | 2012/2013 | June-2012 | 6 | 2012
27761 | FAULTY INSULATOR | 2012-06-21 05:40 | 2012-06-21 | 2012-06-21 13:47 | Calculated | 5720 | 5720 - Fused Link 5720 |  | 416SEG5720 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 487 | 4 | 24559 | 1949 | 0.07936 | 0.00016287 | 25 | 12182 | 2012/2013 | June-2012 | 6 | 2012
27762 | LIGHTNING | 2012-06-21 09:25 | 2012-06-21 | 2012-06-21 11:49 | Calculated | TF1109 | TF1109 - Transformer Fuse: TF1109 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 1 | 24559 | 143 | 0.00582 | 4.0718e-05 | 15 | 2147 | 2012/2013 | June-2012 | 6 | 2012
27763 | EARTH TEST | 2012-06-21 12:22 | 2012-06-21 | 2012-06-21 13:10 | Calculated | TF3372 | TF3372 - Transformer Fuse 3372 |  | 113SEG1508 | Mahoenui 113-07 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24559 |  | 0 | 0 |  |  | 2012/2013 | June-2012 | 6 | 2012
27767 | HV FUSE AT TX 1343 BLEW | 2012-06-22 08:00 | 2012-06-22 | 2012-06-22 09:40 | Calculated | TF1343 | TF1343 - Transformer Fuse: TF1343 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 1 | 24559 | 100 | 0.00407 | 4.0718e-05 | 10 | 1001 | 2012/2013 | June-2012 | 6 | 2012
27768 | HV FUSE AT TX 230 BLEW | 2012-06-22 09:01 | 2012-06-22 | 2012-06-22 10:31 | Calculated | TF230 | TF230 - Transformer Fuse: TF230 |  | No Segment | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 7 | 24559 | 631 | 0.02569 | 0.00028503 | 30 | 2705 | 2012/2013 | June-2012 | 6 | 2012
27769 | SLEEVE THROUGH AT POLE 74 AND REPLACE POLE 122 LIVE LINE | 2012-06-22 09:10 | 2012-06-22 | 2012-06-22 13:07 | Calculated | 282 | 282 - Air Break Switch 282 |  | 103SEG236-731 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 237 | 18 | 24559 | 4273 | 0.17399 | 0.00073293 | 90 | 21367 | 2012/2013 | June-2012 | 6 | 2012
27770 | REPLACE PILLAR BOX | 2012-06-22 10:10 | 2012-06-22 | 2012-06-22 15:42 | Calculated | TF4216 | TF4216 - Transformer Fuse: TF4216 |  | No Segment | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 331 | 4 | 24559 | 1325 | 0.05395 | 0.00016287 | 200 | 66260 | 2012/2013 | June-2012 | 6 | 2012
27771 | HV FUSE AT TX 1864 BLEW | 2012-06-22 18:21 | 2012-06-22 | 2012-06-22 19:50 | Calculated | TF1864 | TF1864 - Transformer Fuse: TF1864 |  | No Segment | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 89 | 2 | 24559 | 178 | 0.00725 | 8.1437e-05 | 15 | 1336 | 2012/2013 | June-2012 | 6 | 2012
27764 | JUMPER OFF AT TX 2543 | 2012-06-24 10:51 | 2012-06-24 | 2012-06-24 12:03 | Calculated | 334 | 334 - Circuit Breaker with Bypass & Links 334 |  | 109SEG303-334 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 22 | 24559 | 1343 | 0.05468 | 0.0008958 | 145 | 8854 | 2012/2013 | June-2012 | 6 | 2012
27765 | FUSE PULLED APART | 2012-06-24 11:50 | 2012-06-24 | 2012-06-24 13:15 | Calculated | TF20K17 | TF20K17 - Transformer Fuse: TF20K17 |  | 416SEG5672-5718 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 4 | 24559 | 340 | 0.01384 | 0.00016287 | 50 | 4259 | 2012/2013 | June-2012 | 6 | 2012
27766 | HV FUSE AT TX 4F8 BLEW | 2012-06-24 12:10 | 2012-06-24 | 2012-06-24 13:31 | Calculated | TF4F8 | TF4F8 - Transformer Fuse: TF4F8 |  | No Segment | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 81 | 6 | 24559 | 487 | 0.01983 | 0.00024431 | 15 | 1217 | 2012/2013 | June-2012 | 6 | 2012
27772 | LIGHTNING | 2012-06-25 13:49 | 2012-06-25 | 2012-06-25 15:37 | Calculated | TF1182 | TF1182 - Transformer Fuse: TF1182 |  | 103SEG230-197 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 4 | 24559 | 432 | 0.01759 | 0.00016287 | 10 | 1081 | 2012/2013 | June-2012 | 6 | 2012
27773 | LIGHTNING | 2012-06-25 13:52 | 2012-06-25 | 2012-06-25 15:14 | Calculated | TF1520 | TF1520 - Transformer Fuse: TF1520 |  | 103SEG197-177 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 2 | 24559 | 164 | 0.00668 | 8.1437e-05 | 10 | 821 | 2012/2013 | June-2012 | 6 | 2012
27785 | CHANGING POLES AND XARMS | 2012-06-26 08:58 | 2012-06-26 | 2012-06-26 15:27 | Calculated | 437 | 437 - Air Break Switch 437 |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 333 | 30 | 24559 | 9962 | 0.40564 | 0.0012215 | 395 | 131166 | 2012/2013 | June-2012 | 6 | 2012
27776 | LV LINE DOWN | 2012-06-26 11:32 | 2012-06-26 | 2012-06-26 13:33 | Calculated | TF1029 | TF1029 - Transformer Fuse: TF1029 |  | 101SEG519-232 | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 3 | 24559 | 363 | 0.01478 | 0.00012215 | 25 | 3029 | 2012/2013 | June-2012 | 6 | 2012
27777 | LIGHTNING | 2012-06-26 11:38 | 2012-06-26 | 2012-06-26 14:36 | Calculated | TF1011 | TF1011 - Transformer Fuse: TF1011 |  | 101SEG552-290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 3 | 24559 | 531 | 0.02162 | 0.00012215 | 10 | 1772 | 2012/2013 | June-2012 | 6 | 2012
27778 | LIGHTNING | 2012-06-26 15:27 | 2012-06-26 | 2012-06-26 17:10 | Calculated | TF4059 | TF4059 - Transformer Fuse: TF4059 |  | 413SEG6357 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 1 | 24559 | 103 | 0.00419 | 4.0718e-05 | 50 | 5156 | 2012/2013 | June-2012 | 6 | 2012
27780 | FAULTY LA | 2012-06-26 22:45 | 2012-06-26 | 2012-06-27 08:44 | Calculated | TF15L13 | TF15L13 - Transformer Fuse: TF15L13 |  | 411SEG5769-5147 | National Park 411-01 | Rural D | National Park | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 598 | 9 | 24559 | 5389 | 0.21943 | 0.00036646 | 200 | 119773 | 2012/2013 | June-2012 | 6 | 2012
27779 | OCB 242 AND 796 TRIPPED ON UNKNOWN OVER CURRENT | 2012-06-26 23:28 | 2012-06-26 | 2012-06-26 23:33 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24559 |  | 0 | 0 |  |  | 2012/2013 | June-2012 | 6 | 2012
27781 | TREES - LINE DOWN | 2012-06-27 06:50 | 2012-06-27 | 2012-06-27 15:58 | Calculated | 1519 | 1519 - Recloser 1519 |  | 113SEG1519-1541 | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 548 | 22 | 24559 | 12058 | 0.49098 | 0.0008958 | 138 | 75642 | 2012/2013 | June-2012 | 6 | 2012
27782 | HV FUSE AT TX 1910 BLEW | 2012-06-27 08:11 | 2012-06-27 | 2012-06-27 10:21 | Calculated | TF1910 | TF1910 - Transformer Fuse: TF1910 |  | 116SEG1355-1327 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 3 | 24559 | 390 | 0.01588 | 0.00012215 | 30 | 3907 | 2012/2013 | June-2012 | 6 | 2012
27784 | CHANGING POLES AND XARMS | 2012-06-27 08:54 | 2012-06-27 | 2012-06-27 15:47 | Calculated | 437 | 437 - Air Break Switch 437 |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 362 | 30 | 24559 | 10832 | 0.44106 | 0.0012215 | 395 | 142621 | 2012/2013 | June-2012 | 6 | 2012
27789 | CHANGING POLES AND XARMS | 2012-06-28 09:01 | 2012-06-28 | 2012-06-28 14:13 | Calculated | 437 | 437 - Air Break Switch 437 |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 265 | 30 | 24559 | 7921 | 0.32253 | 0.0012215 | 395 | 104306 | 2012/2013 | June-2012 | 6 | 2012
27791 | HV FUSE AT TX 2761 BLEW | 2012-06-28 12:17 | 2012-06-28 | 2012-06-28 14:29 | Calculated | TF2761 | TF2761 - Transformer Fuse: TF2761 |  | 129SEG477 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 4 | 24559 | 524 | 0.02134 | 0.00016287 | 30 | 3937 | 2012/2013 | June-2012 | 6 | 2012
27792 | FUSE LINK 2041 BLEW | 2012-06-28 13:49 | 2012-06-28 | 2012-06-28 16:48 | Calculated | 2041 | 2041 - Fused Link 2041 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 4 | 24559 | 716 | 0.02915 | 0.00016287 | 65 | 11646 | 2012/2013 | June-2012 | 6 | 2012
27795 | SUSPECT FAULTY SECTIONALISER | 2012-06-28 15:05 | 2012-06-28 | 2012-06-29 13:47 | Calculated | 5462 | 5462 - Sectionaliser with Bypass & Links 5462 |  | 421SEG6554-5462RET | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 478 | 121 | 24559 | 38732 | 1.5771 | 0.0049269 | 862.5 | 288382 | 2012/2013 | June-2012 | 6 | 2012
27793 | FUSE LINK 173 BLEW | 2012-06-28 17:03 | 2012-06-28 | 2012-06-28 18:54 | Calculated | 173 | 173 - Fused Link 173 |  | 106SEG173 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 7 | 24559 | 778 | 0.03168 | 0.00028503 | 115 | 12784 | 2012/2013 | June-2012 | 6 | 2012
27794 | JUMPER OFF AT TX 530 | 2012-06-28 17:18 | 2012-06-28 | 2012-06-28 19:00 | Calculated | 583 | 583 - Air Break Switch 583 |  | 125SEG296-583 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 149 | 24559 | 15078 | 0.61395 | 0.006067 | 972.1831 | 98384 | 2012/2013 | June-2012 | 6 | 2012
27796 | FUSE LINK 1344 BLEW | 2012-06-29 07:17 | 2012-06-29 | 2012-06-29 08:34 | Calculated | 1344 | 1344 - Fused Link 1344 |  | 110SEG1344 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 7 | 24559 | 540 | 0.02199 | 0.00028503 | 60 | 4631 | 2012/2013 | June-2012 | 6 | 2012
27797 | LV LINE DOWN | 2012-06-29 12:25 | 2012-06-29 | 2012-06-29 18:16 | Calculated | TF3Q5 | TF3Q5 - Transformer Fuse: TF3Q5 |  | No Segment | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 351 | 3 | 24559 | 1053 | 0.04288 | 0.00012215 | 10 | 3512 | 2012/2013 | June-2012 | 6 | 2012
27798 | FUSED LINK 2041 - DUCKS | 2012-06-29 22:41 | 2012-06-29 | 2012-06-29 23:40 | Calculated | 2041 | 2041 - Fused Link 2041 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 4 | 24559 | 236 | 0.00961 | 0.00016287 | 65 | 3846 | 2012/2013 | June-2012 | 6 | 2012
27799 | HV FUSE AT TX8J40 BLEW | 2012-07-02 07:35 | 2012-07-02 | 2012-07-02 08:50 | Calculated | TF8J40 | TF8J40 - Transformer Fuse: TF8J40 |  | No Segment | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 2 | 24612 | 150 | 0.00609 | 8.1261e-05 | 15 | 1128 | 2012/2013 | July-2012 | 7 | 2012
27800 | FUSE PULLED APART | 2012-07-02 12:45 | 2012-07-02 | 2012-07-02 16:12 | Calculated | TF3Q9 | TF3Q9 - Transformer Fuse: TF3Q9 |  | No Segment | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 207 | 1 | 24612 | 207 | 0.00841 | 4.0631e-05 | 15 | 3106 | 2012/2013 | July-2012 | 7 | 2012
27803 | FEEDER UPGRADE - STAGE 2 | 2012-07-02 14:35 | 2012-07-02 | 2012-07-03 15:53 | Calculated | 5364 | 5364 - Air Break Switch 5364 |  | 421SEG5364-5874 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 455 | 121 | 24612 | 8707 | 0.35377 | 0.0049163 | 862.5 | 43809 | 2012/2013 | July-2012 | 7 | 2012
27801 | LIGHTNING | 2012-07-02 20:00 | 2012-07-02 | 2012-07-02 20:56 | Calculated | TF1982 | TF1982 - Transformer Fuse: TF1982 |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 2 | 24612 | 112 | 0.00455 | 8.1261e-05 | 10 | 562 | 2012/2013 | July-2012 | 7 | 2012
27806 | FIT T/O FUSES FOR TX 2129 | 2012-07-03 10:00 | 2012-07-03 | 2012-07-03 11:31 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 90 | 26 | 24612 | 2346 | 0.09532 | 0.0010564 | 165 | 14888 | 2012/2013 | July-2012 | 7 | 2012
27807 | HV FUSE AT TX 7Q13 BLEW | 2012-07-03 16:04 | 2012-07-03 | 2012-07-03 17:59 | Calculated | TF7Q13 | TF7Q13 - Transformer Fuse: TF7Q13 |  | 426SEG5526-5359 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 1 | 24612 | 115 | 0.00467 | 4.0631e-05 | 10 | 1151 | 2012/2013 | July-2012 | 7 | 2012
27808 | BINDER OFF AT POLE 99 | 2012-07-04 03:50 | 2012-07-04 | 2012-07-04 08:17 | Calculated | 5142 | 5142 - Circuit Breaker with Bypass 5142 |  | 410SEG6766-5141 | 501-01 National Park | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 264 | 315 | 24612 | 25785 | 1.0477 | 0.012799 | 2067.8333 | 181001 | 2012/2013 | July-2012 | 7 | 2012
27809 | LV CONNECTIONS ON TX 2899 | 2012-07-04 08:01 | 2012-07-04 | 2012-07-04 08:45 | Calculated | TF2899 | TF2899 - Transformer Fuse: TF2899 |  | 111SEG399-374 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 1 | 24612 | 44 | 0.00179 | 4.0631e-05 | 10 | 442 | 2012/2013 | July-2012 | 7 | 2012
27813 | FEEDER UPGRADE - STAGE 2 | 2012-07-04 08:36 | 2012-07-04 | 2012-07-04 15:38 | Calculated | 5462W | 5462W - Bypass Switch 5462W |  | 421SEG6554-5462RET | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 402 | 121 | 24612 | 9386 | 0.38136 | 0.0049163 | 862.5 | 53899 | 2012/2013 | July-2012 | 7 | 2012
27815 | REPAIR OH LINE DAMAGED BY DIGGER | 2012-07-04 09:32 | 2012-07-04 | 2012-07-04 12:02 | Calculated | 1536 | 1536 - Sectionaliser 1536 |  | 125SEG564-1536 | Coast 125-06 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 96 | 10 | 24612 | 952 | 0.03868 | 0.00040631 | 65 | 6189 | 2012/2013 | July-2012 | 7 | 2012
27819 | LV FAULT | 2012-07-04 11:42 | 2012-07-04 | 2012-07-04 12:22 | Calculated | TF1608 | TF1608 - Transformer Fuse: TF1608 |  | 125SEG1535-1534 | Coast 125-06 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 40 | 1 | 24612 | 40 | 0.00163 | 4.0631e-05 | 7.5 | 301 | 2012/2013 | July-2012 | 7 | 2012
27820 | FUSE LINK 5338 BLEW | 2012-07-04 12:46 | 2012-07-04 | 2012-07-04 14:20 | Calculated | 5338 | 5338 - Fused Link 5338 |  | 402SEG5338 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 7 | 24612 | 659 | 0.02678 | 0.00028441 | 55 | 5179 | 2012/2013 | July-2012 | 7 | 2012
27821 | LV FAULT | 2012-07-04 16:35 | 2012-07-04 | 2012-07-04 17:00 | Calculated | TF402 | TF402 - Transformer Fuse: TF402 |  | No Segment | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 4 | 24612 | 100 | 0.00406 | 0.00016252 | 25 | 628 | 2012/2013 | July-2012 | 7 | 2012
27822 | LV LINE DOWN | 2012-07-04 16:58 | 2012-07-04 | 2012-07-04 19:23 | Calculated | TF600 | TF600 - Transformer Fuse: TF600 |  | No Segment | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 2 | 24612 | 290 | 0.01178 | 8.1261e-05 | 15 | 2177 | 2012/2013 | July-2012 | 7 | 2012
27823 | FEEDER UPGRADE - STAGE 2 | 2012-07-05 08:36 | 2012-07-05 | 2012-07-05 15:07 | Calculated | 5874 | 5874 - Air Break Switch 5874 |  | 421SEG5874-6730 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 338 | 101 | 24612 | 969 | 0.03937 | 0.0041037 | 777.5 | 11167 | 2012/2013 | July-2012 | 7 | 2012
27825 | TOTAL DISMANTLE TX 13I6 | 2012-07-05 11:02 | 2012-07-05 | 2012-07-05 12:05 | Calculated | 5492 | 5492 - Fused Link 5492 |  | 410SEG5492-5334 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 47 | 17 | 24612 | 784 | 0.03185 | 0.00069072 | 120 | 5537 | 2012/2013 | July-2012 | 7 | 2012
27830 | INSPECTION OF 11KV SWITCH GEAR AT TAHAROA SUB | 2012-07-06 12:06 | 2012-07-06 | 2012-07-07 17:23 | Calculated | 788 | 788 - Circuit Breaker 788 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa B 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 477 | 2 | 24612 | 952 | 0.03868 | 8.1261e-05 | 2515 | 1197181 | 2012/2013 | July-2012 | 7 | 2012
27828 | PRIVATE LV LINE DOWN | 2012-07-06 12:29 | 2012-07-06 | 2012-07-06 12:49 | Calculated | TF2035 | TF2035 - Transformer Fuse: TF2035 |  | No Segment | Huirimu 121-01 | Rural D | Huirimu | Arohena Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFPL | Fault on Private Line - Affecting Network | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24612 |  | 0 | 0 |  |  | 2012/2013 | July-2012 | 7 | 2012
27829 | BLOWN FUSED LINK 1297 | 2012-07-06 18:15 | 2012-07-06 | 2012-07-06 20:01 | Calculated | 1297 | 1297 - Fused Link 1297 |  | 117SEG1297-1296 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 73 | 24612 | 7747 | 0.31477 | 0.002966 | 555.5 | 58957 | 2012/2013 | July-2012 | 7 | 2012
27833 | Replace H/V Fuse | 2012-07-08 09:57 | 2012-07-08 | 2012-07-08 12:30 | Calculated | T1982 | T1982 - 1 Phase : 10.00 kVA : POLEMNT |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 153 | 2 | 24612 | 306 | 0.01243 | 8.1261e-05 | 10 | 1533 | 2012/2013 | July-2012 | 7 | 2012
27834 | Broken DDO 2 Tx 388 | 2012-07-09 10:37 | 2012-07-09 | 2012-07-09 12:28 | Calculated | T2882 | T2882 - 3 Phase : 15.00 kVA : POLEMNT |  | 111SEG363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 150 | 24612 | 13851 | 0.56277 | 0.0060946 | 987.1831 | 91319 | 2012/2013 | July-2012 | 7 | 2012
27835 | Replace Faulty Insulator | 2012-07-09 13:26 | 2012-07-09 | 2012-07-09 16:11 | Calculated | 5190 | 5190 - Circuit Breaker 5190 |  | 607SEG5833-5190 | Tokaanu / Kuratau 607-01 | Urban A | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24612 |  | 0 | 0 |  |  | 2012/2013 | July-2012 | 7 | 2012
27836 | Suspect Jumper Off/Line Down | 2012-07-09 21:21 | 2012-07-09 | 2012-07-09 23:01 | Calculated | 378 | 378 - Recloser 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 312 | 24612 | 12146 | 0.4935 | 0.012677 | 2763 | 108485 | 2012/2013 | July-2012 | 7 | 2012
27837 | Replace Red Tagged L/V Pole | 2012-07-10 09:33 | 2012-07-10 | 2012-07-10 15:36 | Calculated | T378 | T378 - 3 Phase : 100.00 kVA : POLEMNT |  | 108SEG181-219 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 363 | 18 | 24612 | 6538 | 0.26564 | 0.00073135 | 100 | 36326 | 2012/2013 | July-2012 | 7 | 2012
27838 | Line Down | 2012-07-10 09:54 | 2012-07-10 | 2012-07-10 12:13 | Calculated | 398 | 398 - Air Break Switch 398 |  | 122SEG366-398 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 36 | 24612 | 2292 | 0.09313 | 0.0014627 | 345 | 21964 | 2012/2013 | July-2012 | 7 | 2012
27839 | Replace H/V Fuse | 2012-07-10 12:32 | 2012-07-10 | 2012-07-10 13:32 | Calculated | 10K34 | 10K34 - 1 Phase : 15.00 kVA : POLEMNT |  | 409SEG5447-5319 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 3 | 24612 | 180 | 0.00731 | 0.00012189 | 15 | 903 | 2012/2013 | July-2012 | 7 | 2012
27841 | Replace Faulty Tx | 2012-07-10 15:29 | 2012-07-10 | 2012-07-10 16:38 | Calculated | T2727 | T2727 - 2 Phase : 15.00 kVA : POLEMNT |  | 116SEG1312-1362 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 1 | 24612 | 69 | 0.0028 | 4.0631e-05 | 15 | 1036 | 2012/2013 | July-2012 | 7 | 2012
27842 | Replace H/V Fuse | 2012-07-11 07:46 | 2012-07-11 | 2012-07-11 09:28 | Calculated | T410 | T410 - 1 Phase : 25.00 kVA : POLEMNT |  | 103SEG283 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 7 | 24612 | 714 | 0.02901 | 0.00028441 | 25 | 2553 | 2012/2013 | July-2012 | 7 | 2012
27843 | Replace H/V Fuse | 2012-07-11 08:01 | 2012-07-11 | 2012-07-11 12:52 | Calculated | T291 | T291 - 3 Phase : 15.00 kVA : POLEMNT |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 291 | 2 | 24612 | 582 | 0.02365 | 8.1261e-05 | 15 | 4366 | 2012/2013 | July-2012 | 7 | 2012
27845 | Replace Red Tagged Pole 3010305 | 2012-07-11 09:09 | 2012-07-11 | 2012-07-11 14:10 | Calculated | 142 | 142 - (RC) Air Break Switch 142 |  | 301SEG140-142 | Taharoa A 301-01 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24612 |  | 0 | 0 |  |  | 2012/2013 | July-2012 | 7 | 2012
27844 | Upgrade Earth Mat & L/A @ Tx 6i2 | 2012-07-11 09:33 | 2012-07-11 | 2012-07-11 15:17 | Calculated | 5467 | 5467 - Recloser with Bypass & Links 5467 |  | 402SEG5467-5472 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 344 | 68 | 24612 | 2908 | 0.11815 | 0.0027629 | 453 | 19896 | 2012/2013 | July-2012 | 7 | 2012
27846 | Deviate SWER One Span Beyond Tx 2178 | 2012-07-12 10:06 | 2012-07-12 | 2012-07-12 13:41 | Calculated | 1625 | 1625 - Recloser with Outgoing Link1625 |  | 128SEG1634-REG3 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 215 | 20 | 24612 | 4305 | 0.17491 | 0.00081261 | 122.5 | 26372 | 2012/2013 | July-2012 | 7 | 2012
27847 | Connect New 11kv U/G Cable & Remove O/H Line | 2012-07-12 10:29 | 2012-07-12 | 2012-07-12 15:53 | Calculated | 721 | 721 - Fused Link 721 |  | 129SEG721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 324 | 3 | 24612 | 972 | 0.03949 | 0.00012189 | 130 | 42152 | 2012/2013 | July-2012 | 7 | 2012
27849 | Replace H/V Fuse | 2012-07-13 18:16 | 2012-07-13 | 2012-07-13 18:59 | Calculated | 319 | 319 - Fused Link 319 |  | 112SEG319 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 10 | 24612 | 431 | 0.01751 | 0.00040631 | 85 | 3666 | 2012/2013 | July-2012 | 7 | 2012
27850 | Jumper Off - Pole Too Rotten to Climb | 2012-07-15 16:49 | 2012-07-15 | 2012-07-16 11:26 | Calculated | 1629 | 1629 - Air Break Switch 1629 |  | 128SEG1629 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1117 | 5 | 24612 | 5586 | 0.22696 | 0.00020315 | 22.5 | 25138 | 2012/2013 | July-2012 | 7 | 2012
27851 | Replace Faulty Tx | 2012-07-15 20:32 | 2012-07-15 | 2012-07-16 03:01 | Calculated | T1071 | T1071 - 3 Phase : 50.00 kVA : POLEMNT |  | 112SEG391-627 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 388 | 11 | 24612 | 4270 | 0.17349 | 0.00044694 | 45.8333 | 17791 | 2012/2013 | July-2012 | 7 | 2012
27852 | Replace H/V Fuse | 2012-07-16 08:52 | 2012-07-16 | 2012-07-16 09:50 | Calculated | T1471 | T1471 - 1 Phase : 10.00 kVA : POLEMNT |  | 128SEG1635-1626 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 1 | 24612 | 58 | 0.00236 | 4.0631e-05 | 10 | 582 | 2012/2013 | July-2012 | 7 | 2012
27855 | Change Faulty Tx | 2012-07-16 14:08 | 2012-07-16 | 2012-07-17 09:56 | Calculated | TF1471 | TF1471 - Transformer Fuse: TF1471 |  | 128SEG1635-1626 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1188 | 1 | 24612 | 1188 | 0.04827 | 4.0631e-05 | 10 | 11881 | 2012/2013 | July-2012 | 7 | 2012
27853 | Tree Through Line @ Pole 64/42/15 | 2012-07-16 17:54 | 2012-07-16 | 2012-07-16 20:58 | Calculated | 5314 | 5314 - Sectionaliser with Bypass 5314 |  | 403SEG5314-5765 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 183 | 15 | 24612 | 1966 | 0.07988 | 0.00060946 | 98 | 11875 | 2012/2013 | July-2012 | 7 | 2012
27856 | Pine Tree Through Line | 2012-07-17 06:15 | 2012-07-17 | 2012-07-17 12:27 | Calculated | 5851 | 5851 - Sectionaliser with Bypass & Links 5851 |  | 421SEG5434-5851 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 371 | 16 | 24612 | 5943 | 0.24147 | 0.00065009 | 105 | 39003 | 2012/2013 | July-2012 | 7 | 2012
27857 | Feeder Renewals | 2012-07-17 09:13 | 2012-07-17 | 2012-07-17 15:31 | Calculated | 549 | 549 - Load Break Switch 549 |  | 111SEG395-549 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 351 | 55 | 24612 | 19262 | 0.78263 | 0.0022347 | 503 | 176167 | 2012/2013 | July-2012 | 7 | 2012
27858 | Faulty L/A @ Tx 10F5 | 2012-07-17 09:45 | 2012-07-17 | 2012-07-17 11:39 | Calculated | 5869 | 5869 - Earth Working Link 5869 |  | 413SEG5869 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 114 | 1 | 24612 | 114 | 0.00463 | 4.0631e-05 | 15 | 1712 | 2012/2013 | July-2012 | 7 | 2012
27859 | Replace Rotten Pole | 2012-07-17 10:39 | 2012-07-17 | 2012-07-17 15:36 | Calculated | 1629 | 1629 - Air Break Switch 1629 |  | 128SEG1629 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOR | Pole Down - Rotten | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 297 | 11 | 24612 | 3173 | 0.12892 | 0.00044694 | 82.5 | 23560 | 2012/2013 | July-2012 | 7 | 2012
27861 | L/V Neutral Fault | 2012-07-17 11:39 | 2012-07-17 | 2012-07-17 13:11 | Calculated | TF10S47 | TF10S47 - Transformer Fuse: TF10S47 |  | 424SEG6651-6652 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBJ | Underground Cable Joint Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 29 | 24612 | 2672 | 0.10856 | 0.0011783 | 200 | 18429 | 2012/2013 | July-2012 | 7 | 2012
27862 | Replace H/V Fuse | 2012-07-17 20:11 | 2012-07-17 | 2012-07-17 21:28 | Calculated | TF297 | TF297 - Transformer Fuse: TF297 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 4 | 24612 | 308 | 0.01251 | 0.00016252 | 15 | 1157 | 2012/2013 | July-2012 | 7 | 2012
27863 | Close OCB | 2012-07-18 07:05 | 2012-07-18 | 2012-07-18 07:21 | Calculated | 378 | 378 - Recloser 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 312 | 24612 | 5033 | 0.20449 | 0.012677 | 2763 | 44576 | 2012/2013 | July-2012 | 7 | 2012
27864 | L/V Maintenance | 2012-07-18 09:01 | 2012-07-18 | 2012-07-18 13:10 | Calculated | TF1B25 | TF1B25 - Transformer Fuse: TF1B25 |  | 404SEGF1.16 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 249 | 35 | 24612 | 8721 | 0.35434 | 0.0014221 | 100 | 24919 | 2012/2013 | July-2012 | 7 | 2012
27868 | Replace Pole 205 | 2012-07-19 08:50 | 2012-07-19 | 2012-07-19 14:16 | Calculated | TF12N05 | TF12N05 - Transformer Fuse: TF12N05 |  | 609SEG5159-6761 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 326 | 8 | 24612 | 2609 | 0.10601 | 0.00032504 | 300 | 97859 | 2012/2013 | July-2012 | 7 | 2012
27869 | Replace ABS 361 Pole | 2012-07-19 09:38 | 2012-07-19 | 2012-07-19 10:45 | Calculated | TF92 | TF92 - Transformer Fuse: TF92 |  | No Segment | Rangitoto 106-07 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 67 | 6 | 24612 | 402 | 0.01633 | 0.00024378 | 30 | 2014 | 2012/2013 | July-2012 | 7 | 2012
27870 | Replace Pole | 2012-07-19 10:10 | 2012-07-19 | 2012-07-19 13:51 | Calculated | 369 | 369 - Fused Link 369 |  | 122SEG369-678 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 221 | 15 | 24612 | 3319 | 0.13485 | 0.00060946 | 195 | 43147 | 2012/2013 | July-2012 | 7 | 2012
27871 | Replace L/V Fuse Boxes | 2012-07-19 10:40 | 2012-07-19 | 2012-07-19 11:10 | Calculated | TF9K9 | TF9K9 - Transformer Fuse: TF9K9 |  | No Segment | Southern 409-03 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 12 | 24612 | 361 | 0.01467 | 0.00048757 | 50 | 1507 | 2012/2013 | July-2012 | 7 | 2012
27872 | Replace H/V Fuse | 2012-07-19 13:22 | 2012-07-19 | 2012-07-19 14:58 | Calculated | TF1044 | TF1044 - Transformer Fuse: TF1044 |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 2 | 24612 | 192 | 0.0078 | 8.1261e-05 | 25 | 2403 | 2012/2013 | July-2012 | 7 | 2012
27873 | Helicopter vs Line - Lines Down | 2012-07-19 15:49 | 2012-07-19 | 2012-07-19 22:19 | Calculated | 687 | 687 - Circuit Breaker 687 |  | 117SEG687-1289 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 390 | 236 | 24612 | 21770 | 0.88453 | 0.0095888 | 1882 | 178601 | 2012/2013 | July-2012 | 7 | 2012
27874 | Repair Broken Jumper @ Pole 146 | 2012-07-19 21:57 | 2012-07-19 | 2012-07-19 23:05 | Calculated | 1362 | 1362 - Air Break Switch 1362 |  | 116SEG1312-1362 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 30 | 24612 | 1453 | 0.05904 | 0.0012189 | 277.5 | 13440 | 2012/2013 | July-2012 | 7 | 2012
27877 | Replace Link | 2012-07-20 08:44 | 2012-07-20 | 2012-07-20 10:17 | Calculated | 5303 | 5303 - Fused Link 5303 |  | 413SEG5303-5644 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 92 | 5 | 24612 | 460 | 0.01869 | 0.00020315 | 25 | 2302 | 2012/2013 | July-2012 | 7 | 2012
27876 | shift Main Line Poles 128 & 129 | 2012-07-20 09:16 | 2012-07-20 | 2012-07-20 16:42 | Calculated | 1722 | 1722 - Fused Link 1722 |  | 117SEG1722-1721 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 424 | 40 | 24612 | 4321 | 0.17556 | 0.0016252 | 318 | 47044 | 2012/2013 | July-2012 | 7 | 2012
27878 | Repair Line | 2012-07-20 10:29 | 2012-07-20 | 2012-07-20 15:28 | Calculated | TF2176 | TF2176 - Transformer Fuse: TF2176 |  | 128SEG1634-REG3 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DICL | Conductor Low - Incorrect Clearances | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 299 | 14 | 24612 | 4188 | 0.17016 | 0.00056883 | 30 | 8974 | 2012/2013 | July-2012 | 7 | 2012
27879 | Replace Fuse | 2012-07-21 09:52 | 2012-07-21 | 2012-07-21 10:51 | Calculated | TF1016 | TF1016 - Transformer Fuse: TF1016 |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 3 | 24612 | 177 | 0.00719 | 0.00012189 | 30 | 1774 | 2012/2013 | July-2012 | 7 | 2012
27880 | Replace Fuse | 2012-07-21 15:21 | 2012-07-21 | 2012-07-21 17:59 | Calculated | TF1044 | TF1044 - Transformer Fuse: TF1044 |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 2 | 24612 | 316 | 0.01284 | 8.1261e-05 | 25 | 3954 | 2012/2013 | July-2012 | 7 | 2012
27881 | Replace Fuse | 2012-07-22 09:26 | 2012-07-22 | 2012-07-22 11:25 | Calculated | 5500 | 5500 - Fused Link 5500 |  | 421SEG5500-5501 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 119 | 39 | 24612 | 4646 | 0.18877 | 0.0015846 | 267.5 | 31872 | 2012/2013 | July-2012 | 7 | 2012
27882 | Line Down | 2012-07-23 05:46 | 2012-07-23 | 2012-07-23 12:16 | Calculated | 296 | 296 - Recloser with Bypass 296 |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 390 | 174 | 24612 | 60972 | 2.4773 | 0.0070697 | 1182.1831 | 403137 | 2012/2013 | July-2012 | 7 | 2012
27883 | Tree in Line | 2012-07-23 09:58 | 2012-07-23 | 2012-07-23 17:47 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 468 | 103 | 24612 | 13867 | 0.56342 | 0.004185 | 988 | 132561 | 2012/2013 | July-2012 | 7 | 2012
27884 | Replace Insulator | 2012-07-23 18:31 | 2012-07-23 | 2012-07-23 21:02 | Calculated | 1713 | 1713 - Fused Link 1713 |  | 115SEG1713 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 7 | 24612 | 1058 | 0.04299 | 0.00028441 | 60 | 9070 | 2012/2013 | July-2012 | 7 | 2012
27885 | Replace Fuse | 2012-07-23 20:00 | 2012-07-23 | 2012-07-23 21:01 | Calculated | TF285 | TF285 - Transformer Fuse: TF285 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 3 | 24612 | 184 | 0.00748 | 0.00012189 | 25 | 1534 | 2012/2013 | July-2012 | 7 | 2012
27888 | Change Tx | 2012-07-24 12:50 | 2012-07-24 | 2012-07-24 17:36 | Calculated | TF1044 | TF1044 - Transformer Fuse: TF1044 |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 285 | 2 | 24612 | 570 | 0.02316 | 8.1261e-05 | 25 | 7132 | 2012/2013 | July-2012 | 7 | 2012
27891 | Replace Faulty Insulator | 2012-07-25 08:49 | 2012-07-25 | 2012-07-25 12:54 | Calculated | 5409 | 5409 - Recloser with Bypass 5409 |  | 426SEG5409-5333 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 245 | 89 | 24612 | 14340 | 0.58264 | 0.0036161 | 643 | 105208 | 2012/2013 | July-2012 | 7 | 2012
27889 | Lower Taps | 2012-07-25 09:23 | 2012-07-25 | 2012-07-25 09:43 | Calculated | TF992 | TF992 - Transformer Fuse: TF992 |  | No Segment | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 3 | 24612 | 60 | 0.00244 | 0.00012189 | 25 | 502 | 2012/2013 | July-2012 | 7 | 2012
27892 | L/V Fault | 2012-07-25 13:15 | 2012-07-25 | 2012-07-25 14:50 | Calculated | TF1666 | TF1666 - Transformer Fuse: TF1666 |  | 116SEG1312-1362 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 3 | 24612 | 282 | 0.01146 | 0.00012189 | 25 | 2353 | 2012/2013 | July-2012 | 7 | 2012
27893 | Repair Broken Earth Wire | 2012-07-25 14:16 | 2012-07-25 | 2012-07-25 14:46 | Calculated | TF6Q9 | TF6Q9 - Transformer Fuse: TF6Q9 |  | 426SEG5239 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 30 | 1 | 24612 | 30 | 0.00122 | 4.0631e-05 | 15 | 452 | 2012/2013 | July-2012 | 7 | 2012
27894 | Unknown Bus Tie Trip | 2012-07-26 00:24 | 2012-07-26 | 2012-07-26 00:28 | Calculated | 5953 | 5953 - Circuit Breaker Western 5953 |  | 508SEG5953-6034 | 508-01 Borough | Rural B | No Feeder |  |  | Asset Related | Other | FAIL:FOLD:FOLN | Fault on Adjacent Circuit | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24612 |  | 0 | 0 |  |  | 2012/2013 | July-2012 | 7 | 2012
27896 | Replace H/V Fuse | 2012-07-26 20:56 | 2012-07-26 | 2012-07-26 22:06 | Calculated | TF297 | TF297 - Transformer Fuse: TF297 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 4 | 24612 | 276 | 0.01121 | 0.00016252 | 15 | 1037 | 2012/2013 | July-2012 | 7 | 2012
27899 | Replace Fuse | 2012-07-27 10:56 | 2012-07-27 | 2012-07-27 11:03 | Calculated | TF511 | TF511 - Transformer Fuse: TF511 |  | No Segment | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 1 | 24612 | 7 | 0.00028 | 4.0631e-05 | 10 | 72 | 2012/2013 | July-2012 | 7 | 2012
27901 | Replace H/V Fuse | 2012-07-28 09:26 | 2012-07-28 | 2012-07-28 11:07 | Calculated | TF535 | TF535 - Transformer Fuse: TF535 |  | No Segment | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 3 | 24612 | 300 | 0.01219 | 0.00012189 | 15 | 1502 | 2012/2013 | July-2012 | 7 | 2012
27902 | Replace H/V Fuse | 2012-07-28 12:28 | 2012-07-28 | 2012-07-28 13:04 | Calculated | TF3293 | TF3293 - Transformer Fuse: TF3293 |  | 117SEG1314-1324 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 35 | 1 | 24612 | 35 | 0.00142 | 4.0631e-05 | 75 | 2637 | 2012/2013 | July-2012 | 7 | 2012
27903 | Replace H/V Fuse | 2012-07-28 20:03 | 2012-07-28 | 2012-07-28 21:05 | Calculated | TF13L3 | TF13L3 - Transformer Fuse: TF13L3 |  | 410SEG5829-5545 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 15 | 24612 | 932 | 0.03787 | 0.00060946 | 50 | 3106 | 2012/2013 | July-2012 | 7 | 2012
27904 | Line Down | 2012-07-29 16:59 | 2012-07-29 | 2012-07-30 17:21 | Calculated | 5371 | 5371 - Recloser with Bypass & Links 5371 |  | 422SEG05G03-5371 | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1434 | 29 | 24612 | 24789 | 1.0072 | 0.0011783 | 216.5 | 184786 | 2012/2013 | July-2012 | 7 | 2012
27905 | Trees in Line | 2012-07-29 22:13 | 2012-07-29 | 2012-07-30 09:39 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 686 | 7 | 24612 | 4803 | 0.19515 | 0.00028441 | 80 | 54894 | 2012/2013 | July-2012 | 7 | 2012
27906 | Switch Opened Unexplainedly | 2012-07-29 22:56 | 2012-07-29 | 2012-07-30 00:58 | Calculated | 425 | 425 - Air Break Switch 425 |  | 121SEG425-748 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 103 | 24612 | 12481 | 0.50711 | 0.004185 | 891.5 | 108034 | 2012/2013 | July-2012 | 7 | 2012
27907 | Replace H/V Fuse | 2012-07-30 08:15 | 2012-07-30 | 2012-07-30 10:03 | Calculated | TF2274 | TF2274 - Transformer Fuse: TF2274 |  | 114SEG1104 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 2 | 24612 | 216 | 0.00878 | 8.1261e-05 | 10 | 1081 | 2012/2013 | July-2012 | 7 | 2012
27908 | Replace H/V Fuse | 2012-07-30 12:41 | 2012-07-30 | 2012-07-30 14:45 | Calculated | TF7J21 | TF7J21 - Transformer Fuse: TF7J21 |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 1 | 24612 | 124 | 0.00504 | 4.0631e-05 | 50 | 6208 | 2012/2013 | July-2012 | 7 | 2012
27909 | Replace H/V Fuse | 2012-07-30 13:00 | 2012-07-30 | 2012-07-30 13:05 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 27 | 24612 | 138 | 0.00561 | 0.001097 | 281.4286 | 1444 | 2012/2013 | July-2012 | 7 | 2012
27910 | Replace H/V Fuse | 2012-07-30 18:58 | 2012-07-30 | 2012-07-30 19:43 | Calculated | 341 | 341 - Fused Link 341 |  | 109SEG341-587 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 40 | 24612 | 1765 | 0.07171 | 0.0016252 | 355 | 15667 | 2012/2013 | July-2012 | 7 | 2012
27911 | Replace H/V Fuse | 2012-07-31 05:21 | 2012-07-31 | 2012-07-31 06:40 | Calculated | TF318 | TF318 - Transformer Fuse: TF318 |  | No Segment | McDonalds 110-04 | Urban A | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 5 | 24612 | 396 | 0.01609 | 0.00020315 | 25 | 1981 | 2012/2013 | July-2012 | 7 | 2012
27912 | Replace ABS 573 | 2012-07-31 09:31 | 2012-07-31 | 2012-07-31 12:57 | Calculated | 573 | 573 - Air Break Switch 573 |  | 111SEG573-638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 146 | 57 | 24612 | 8331 | 0.33849 | 0.0023159 | 700 | 102316 | 2012/2013 | July-2012 | 7 | 2012
27914 | SWER Hooked in Tree | 2012-07-31 10:42 | 2012-07-31 | 2012-07-31 11:07 | Calculated | 5744 | 5744 - Sectionaliser with Bypass 5744 |  | 410SEG5744-5631 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 25 | 11 | 24612 | 276 | 0.01121 | 0.00044694 | 48.5 | 1219 | 2012/2013 | July-2012 | 7 | 2012
27915 | Replace H/V Fuse | 2012-07-31 13:11 | 2012-07-31 | 2012-07-31 14:42 | Calculated | TF122 | TF122 - Transformer Fuse: TF122 |  | 110SEG387-328 | McDonalds 110-04 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 3 | 24612 | 273 | 0.01109 | 0.00012189 | 50 | 4557 | 2012/2013 | July-2012 | 7 | 2012
27916 | Replace H/V Fuse | 2012-08-01 09:44 | 2012-08-01 | 2012-08-01 11:21 | Calculated | TF3280 | TF3280 - Transformer Fuse: TF3280 |  | 103SEG1651-2227 | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 1 | 24554 | 97 | 0.00395 | 4.0727e-05 | 75 | 7286 | 2012/2013 | August-2012 | 8 | 2012
27917 | Digger vs Earth Mat | 2012-08-01 11:29 | 2012-08-01 | 2012-08-01 12:42 | Calculated | TF7R19 | TF7R19 - Transformer Fuse: TF7R19 |  | No Segment | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 1 | 24554 | 73 | 0.00297 | 4.0727e-05 | 0 | 0 | 2012/2013 | August-2012 | 8 | 2012
27918 | Maintenance | 2012-08-02 10:24 | 2012-08-02 | 2012-08-02 13:54 | Calculated | TF1303 | TF1303 - Transformer Fuse: TF1303 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 210 | 4 | 24554 | 840 | 0.03421 | 0.00016291 | 40 | 8407 | 2012/2013 | August-2012 | 8 | 2012
27919 | Replace H/V Fuse | 2012-08-03 07:00 | 2012-08-03 | 2012-08-03 08:32 | Calculated | TF7J13 | TF7J13 - Transformer Fuse: TF7J13 |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 3 | 24554 | 276 | 0.01124 | 0.00012218 | 15 | 1382 | 2012/2013 | August-2012 | 8 | 2012
27920 | Feder Renewals | 2012-08-03 09:34 | 2012-08-03 | 2012-08-03 15:38 | Calculated | 5105 | 5105 - Fused Link 5105 |  | 422SEG5105-5279 | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 364 | 29 | 24554 | 10560 | 0.43007 | 0.0011811 | 216.5 | 78838 | 2012/2013 | August-2012 | 8 | 2012
27921 | Replace Pole 1011035 | 2012-08-03 09:40 | 2012-08-03 | 2012-08-03 14:49 | Calculated | 519 | 519 - Fused Link 519 |  | 101SEG519-232 | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 309 | 21 | 24554 | 6491 | 0.26436 | 0.00085526 | 310 | 95831 | 2012/2013 | August-2012 | 8 | 2012
27923 | Replace H/V Fuse | 2012-08-03 16:14 | 2012-08-03 | 2012-08-03 17:01 | Calculated | TF7R9 | TF7R9 - Transformer Fuse: TF7R9 |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 4 | 24554 | 188 | 0.00766 | 0.00016291 | 15 | 707 | 2012/2013 | August-2012 | 8 | 2012
27924 | Replace ABS 361 | 2012-08-04 08:33 | 2012-08-04 | 2012-08-04 15:33 | Calculated | 191 | 191 - Air Break Switch 191 |  | 102SEG191-361 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 420 | 11 | 24554 | 4622 | 0.18824 | 0.00044799 | 1360 | 571449 | 2012/2013 | August-2012 | 8 | 2012
27925 | Upgrade Tx | 2012-08-06 11:17 | 2012-08-06 | 2012-08-06 14:31 | Calculated | TF5I6 | TF5I6 - Transformer Fuse: TF5I6 |  | 402SEG5446-5797 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 194 | 1 | 24554 | 194 | 0.0079 | 4.0727e-05 | 3 | 582 | 2012/2013 | August-2012 | 8 | 2012
27928 | Replace Hardware Pole 40310882 | 2012-08-07 08:33 | 2012-08-07 | 2012-08-07 16:27 | Calculated | 5322 | 5322 - Fused Link 5322 |  | 403SEG5887-5322 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 320 | 83 | 24554 | 4891 | 0.19919 | 0.0033803 | 493 | 26435 | 2012/2013 | August-2012 | 8 | 2012
27930 | Upgrade Earth | 2012-08-07 09:32 | 2012-08-07 | 2012-08-07 11:50 | Calculated | TF12S01 | TF12S01 - Transformer Fuse: TF12S01 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 138 | 1 | 24554 | 138 | 0.00562 | 4.0727e-05 | 200 | 27653 | 2012/2013 | August-2012 | 8 | 2012
27929 | Replace T 3124 with RTE Type | 2012-08-07 09:46 | 2012-08-07 | 2012-08-07 15:45 | Calculated | 1027 | 1027 - Ring Main Unit 1027 |  | 123SEG1029-1026 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 358 | 2 | 24554 | 716 | 0.02916 | 8.1453e-05 | 50 | 17910 | 2012/2013 | August-2012 | 8 | 2012
27931 | Replace Poles & Xarms | 2012-08-09 09:33 | 2012-08-09 | 2012-08-09 13:41 | Calculated | TF13S01 | TF13S01 - Transformer Fuse: TF13S01 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 2 | 24554 | 496 | 0.0202 | 8.1453e-05 | 200 | 49640 | 2012/2013 | August-2012 | 8 | 2012
27932 | Replace L/A | 2012-08-09 13:22 | 2012-08-09 | 2012-08-09 14:25 | Calculated | TF7J21 | TF7J21 - Transformer Fuse: TF7J21 |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 63 | 1 | 24554 | 63 | 0.00257 | 4.0727e-05 | 50 | 3157 | 2012/2013 | August-2012 | 8 | 2012
27933 | Faulty L/A | 2012-08-12 06:07 | 2012-08-12 | 2012-08-12 08:23 | Calculated | TF260 | TF260 - Transformer Fuse: TF260 |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:IBW9EJ | Lightning Damage to Insulators | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 2 | 24554 | 272 | 0.01108 | 8.1453e-05 | 50 | 6810 | 2012/2013 | August-2012 | 8 | 2012
27934 | Blow up in Tx 2417 | 2012-08-12 12:42 | 2012-08-12 | 2012-08-12 14:08 | Calculated | 668 | 668 - Fused Link 668 |  | 112SEG668-229 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLC | Condensation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 40 | 24554 | 3407 | 0.13876 | 0.0016291 | 400 | 34079 | 2012/2013 | August-2012 | 8 | 2012
27935 | Replace H/v Fuse | 2012-08-12 19:38 | 2012-08-12 | 2012-08-12 20:10 | Calculated | TF20L32 | TF20L32 - Transformer Fuse: TF20L32 |  | No Segment | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 10 | 24554 | 321 | 0.01307 | 0.00040727 | 50 | 1608 | 2012/2013 | August-2012 | 8 | 2012
27936 | Fault Repairs to Tx 2417 | 2012-08-13 22:12 | 2012-08-13 | 2012-08-14 00:32 | Calculated | 668 | 668 - Fused Link 668 |  | 112SEG668-229 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 140 | 40 | 24554 | 5607 | 0.22835 | 0.0016291 | 400 | 56073 | 2012/2013 | August-2012 | 8 | 2012
27937 | Re-test Earth Mat | 2012-08-14 09:36 | 2012-08-14 | 2012-08-14 14:03 | Calculated | TF9E11 | TF9E11 - Transformer Fuse: TF9E11 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 267 | 3 | 24554 | 801 | 0.03262 | 0.00012218 | 15 | 4007 | 2012/2013 | August-2012 | 8 | 2012
27944 | Replace Tx 2Q4 | 2012-08-15 09:04 | 2012-08-15 | 2012-08-15 13:28 | Calculated | 5581 | 5581 - Fused Link 5581 |  | 124SEG5581-5537 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 233 | 52 | 24554 | 2693 | 0.10968 | 0.0021178 | 370.5 | 19753 | 2012/2013 | August-2012 | 8 | 2012
27938 | Install New Earth Mat | 2012-08-15 10:26 | 2012-08-15 | 2012-08-15 14:22 | Calculated | TF2Q4 | TF2Q4 - Transformer Fuse: TF2Q4 |  | No Segment | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 236 | 1 | 24554 | 236 | 0.00961 | 4.0727e-05 | 10 | 2362 | 2012/2013 | August-2012 | 8 | 2012
27939 | Fault on RG12 | 2012-08-15 12:48 | 2012-08-15 | 2012-08-15 19:00 | Calculated | 5154 | 5154 - Circuit Breaker 5154 |  | No Segment | 513-01 Tawhai | Rural D | No Feeder |  |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 353 | 138 | 24554 | 48654 | 1.9815 | 0.0056203 | 12065 | 4253716 | 2012/2013 | August-2012 | 8 | 2012
27940 | Lower Tap | 2012-08-15 15:12 | 2012-08-15 | 2012-08-15 15:31 | Calculated | TF794 | TF794 - Transformer Fuse: TF794 |  | 129SEG725 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 2 | 24554 | 36 | 0.00147 | 8.1453e-05 | 15 | 274 | 2012/2013 | August-2012 | 8 | 2012
27941 | Replace H/V Fuse | 2012-08-15 17:42 | 2012-08-15 | 2012-08-15 18:09 | Calculated | TF682 | TF682 - Transformer Fuse: TF682 |  | 112SEG1021-318 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 7 | 24554 | 190 | 0.00774 | 0.00028509 | 25 | 679 | 2012/2013 | August-2012 | 8 | 2012
27942 | Replace H/V Fuse | 2012-08-15 22:07 | 2012-08-15 | 2012-08-15 22:45 | Calculated | TF292 | TF292 - Transformer Fuse: TF292 |  | No Segment | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 2 | 24554 | 76 | 0.0031 | 8.1453e-05 | 25 | 952 | 2012/2013 | August-2012 | 8 | 2012
27943 | Replace H/V Fuse | 2012-08-16 08:39 | 2012-08-16 | 2012-08-16 10:34 | Calculated | 1263 | 1263 - Sectionaliser with Incoming Link 1263 |  | 115SEG1356-1725 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 115 | 1 | 24554 | 115 | 0.00468 | 4.0727e-05 | 15 | 1727 | 2012/2013 | August-2012 | 8 | 2012
27945 | Install New L/A & DDO for Tx 6E18 | 2012-08-16 09:14 | 2012-08-16 | 2012-08-16 12:45 | Calculated | 5227 | 5227 - Fused Link 5227 |  | 412SEG5227-5269 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 189 | 13 | 24554 | 993 | 0.04044 | 0.00052945 | 93 | 8246 | 2012/2013 | August-2012 | 8 | 2012
27946 | A Line Fault | 2012-08-16 18:10 | 2012-08-16 | 2012-08-16 18:15 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24554 |  | 0 | 0 |  |  | 2012/2013 | August-2012 | 8 | 2012
27948 | Replace Structure & Sect 5623 | 2012-08-17 10:02 | 2012-08-17 | 2012-08-17 12:36 | Calculated | 5411 | 5411 - Fused Link 5411 |  | 409SEG5411-5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 153 | 22 | 24554 | 3374 | 0.13741 | 0.00089598 | 136.5 | 20939 | 2012/2013 | August-2012 | 8 | 2012
27947 | Tree Cutting | 2012-08-17 10:03 | 2012-08-17 | 2012-08-17 14:04 | Calculated | 659 | 659 - Air Break Switch 659 |  | 106SEG659-194 | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 241 | 32 | 24554 | 7718 | 0.31433 | 0.0013032 | 238 | 57409 | 2012/2013 | August-2012 | 8 | 2012
27949 | Maintenance | 2012-08-17 12:35 | 2012-08-17 | 2012-08-17 15:02 | Calculated | TF674 | TF674 - Transformer Fuse: TF674 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 146 | 2 | 24554 | 292 | 0.01189 | 8.1453e-05 | 15 | 2192 | 2012/2013 | August-2012 | 8 | 2012
27950 | Replace H/V Fuse | 2012-08-17 15:27 | 2012-08-17 | 2012-08-17 15:59 | Calculated | TF21M13 | TF21M13 - Transformer Fuse: TF21M13 |  | No Segment | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 2 | 24554 | 64 | 0.00261 | 8.1453e-05 | 15 | 482 | 2012/2013 | August-2012 | 8 | 2012
27951 | Jumper Off ABS 5709 | 2012-08-19 08:55 | 2012-08-19 | 2012-08-19 11:45 | Calculated | 5708 | 5708 - Air Break Switch 5708 |  | 416SEG5708-5700 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 169 | 29 | 24554 | 4905 | 0.19976 | 0.0011811 | 513 | 86782 | 2012/2013 | August-2012 | 8 | 2012
27952 | B Line Fault | 2012-08-20 10:38 | 2012-08-20 | 2012-08-20 10:41 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 431 | 24554 | 926 | 0.03771 | 0.017553 | 5743.9586 | 12349 | 2012/2013 | August-2012 | 8 | 2012
27953 | Install Prop Pole | 2012-08-21 13:01 | 2012-08-21 | 2012-08-21 14:00 | Calculated | 5468 | 5468 - Fused Link 5468 |  | 421SEG5468 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 59 | 18 | 24554 | 1064 | 0.04333 | 0.00073308 | 120 | 7097 | 2012/2013 | August-2012 | 8 | 2012
27954 | L/v Maintenance | 2012-08-22 12:25 | 2012-08-22 | 2012-08-22 14:22 | Calculated | TF2442 | TF2442 - Transformer Fuse: TF2442 |  | No Segment | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 3 | 24554 | 352 | 0.01434 | 0.00012218 | 25 | 2939 | 2012/2013 | August-2012 | 8 | 2012
27955 | Replace H/V Fuse | 2012-08-22 14:54 | 2012-08-22 | 2012-08-22 16:15 | Calculated | TF241 | TF241 - Transformer Fuse: TF241 |  | No Segment | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 5 | 24554 | 405 | 0.01649 | 0.00020363 | 25 | 2027 | 2012/2013 | August-2012 | 8 | 2012
27956 | Close CB | 2012-08-22 16:44 | 2012-08-22 | 2012-08-22 16:44 | Calculated | 6143 | 6143 - Circuit Breaker Manunui 33kV 6143 |  | 608SEG6144-5629 | Taumarunui / Kuratau 608-02 | Urban A | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 4 | 24554 | 4 | 0.00016 | 0.00016291 | 450 | 60 | 2012/2013 | August-2012 | 8 | 2012
27957 | Replace H/V Fuse | 2012-08-22 16:46 | 2012-08-22 | 2012-08-22 17:46 | Calculated | TF8Q5 | TF8Q5 - Transformer Fuse: TF8Q5 |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 2 | 24554 | 118 | 0.00481 | 8.1453e-05 | 7.5 | 443 | 2012/2013 | August-2012 | 8 | 2012
27958 | Replace H/V Fuse | 2012-08-22 17:39 | 2012-08-22 | 2012-08-22 18:16 | Calculated | TF8Q4 | TF8Q4 - Transformer Fuse: TF8Q4 |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 1 | 24554 | 37 | 0.00151 | 4.0727e-05 | 5 | 185 | 2012/2013 | August-2012 | 8 | 2012
27959 | Replace Poles 123004 & 1027 | 2012-08-23 08:56 | 2012-08-23 | 2012-08-23 15:51 | Calculated | 786 | 786 - Fused Link 786 |  | 124SEG542-786 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 370 | 50 | 24554 | 18458 | 0.75173 | 0.0020363 | 555 | 204887 | 2012/2013 | August-2012 | 8 | 2012
27960 | Replace H/V Fuse | 2012-08-23 13:54 | 2012-08-23 | 2012-08-23 14:55 | Calculated | TF1954 | TF1954 - Transformer Fuse: TF1954 |  | 114SEG1125-2160 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 1 | 24554 | 61 | 0.00248 | 4.0727e-05 | 3 | 183 | 2012/2013 | August-2012 | 8 | 2012
27961 | Lightning Storm | 2012-08-23 15:24 | 2012-08-23 | 2012-08-23 19:28 | Calculated | 519 | 519 - Fused Link 519 |  | 101SEG519-232 | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 244 | 21 | 24554 | 3112 | 0.12674 | 0.00085526 | 310 | 41381 | 2012/2013 | August-2012 | 8 | 2012
27962 | Replace Sect 5250 | 2012-08-24 10:02 | 2012-08-24 | 2012-08-24 12:17 | Calculated | 5617 | 5617 - Fused Link 5617 |  | 406SEG5248-5617 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 134 | 22 | 24554 | 2952 | 0.12022 | 0.00089598 | 112.5 | 15099 | 2012/2013 | August-2012 | 8 | 2012
27963 | Replace Rusted Tx | 2012-08-24 10:26 | 2012-08-24 | 2012-08-24 12:31 | Calculated | TF1029 | TF1029 - Transformer Fuse: TF1029 |  | 101SEG519-232 | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 125 | 3 | 24554 | 375 | 0.01527 | 0.00012218 | 25 | 3128 | 2012/2013 | August-2012 | 8 | 2012
27964 | Replace Un-numbered Link | 2012-08-24 16:37 | 2012-08-24 | 2012-08-24 17:58 | Calculated | TF4152 | TF4152 - Transformer Fuse: TF4152 |  | No Segment | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 16 | 24554 | 1298 | 0.05286 | 0.00065162 | 90 | 7301 | 2012/2013 | August-2012 | 8 | 2012
27965 | Replace H/V Fuse | 2012-08-24 17:01 | 2012-08-24 | 2012-08-24 18:29 | Calculated | TF1954 | TF1954 - Transformer Fuse: TF1954 |  | 114SEG1125-2160 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 1 | 24554 | 88 | 0.00358 | 4.0727e-05 | 3 | 264 | 2012/2013 | August-2012 | 8 | 2012
27966 | Replace H/V Fuse | 2012-08-25 09:01 | 2012-08-25 | 2012-08-25 10:31 | Calculated | TF2L9 | TF2L9 - Transformer Fuse: TF2L9 |  | No Segment | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 89 | 3 | 24554 | 267 | 0.01087 | 0.00012218 | 15 | 1337 | 2012/2013 | August-2012 | 8 | 2012
27967 | Replace Fuse | 2012-08-25 19:04 | 2012-08-25 | 2012-08-25 21:16 | Calculated | T1588 | T1588 - 3 Phase : 100.00 kVA : POLEMNT |  | 404SEGL1.10 | Matapuna 404-01 | Rural B | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24554 |  | 0 | 0 |  |  | 2012/2013 | August-2012 | 8 | 2012
27968 | L/V Maintenance | 2012-08-27 09:03 | 2012-08-27 | 2012-08-27 12:36 | Calculated | TF1339 | TF1339 - Transformer Fuse: TF1339 |  | 107SEG649-160 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 213 | 11 | 24554 | 2344 | 0.09546 | 0.00044799 | 50 | 10658 | 2012/2013 | August-2012 | 8 | 2012
27969 | Replace Faulty Tx | 2012-08-27 11:15 | 2012-08-27 | 2012-08-27 13:33 | Calculated | TF1954 | TF1954 - Transformer Fuse: TF1954 |  | 114SEG1125-2160 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 1 | 24554 | 138 | 0.00562 | 4.0727e-05 | 3 | 414 | 2012/2013 | August-2012 | 8 | 2012
27970 | Replace H/V Fuse | 2012-08-27 12:10 | 2012-08-27 | 2012-08-27 13:46 | Calculated | TF2487 | TF2487 - Transformer Fuse: TF2487 |  | No Segment | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 1 | 24554 | 96 | 0.00391 | 4.0727e-05 | 25 | 2402 | 2012/2013 | August-2012 | 8 | 2012
27971 | Change Poles & Xarms | 2012-08-29 08:56 | 2012-08-29 | 2012-08-29 15:45 | Calculated | 786 | 786 - Fused Link 786 |  | 124SEG542-786 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 355 | 21 | 24554 | 7064 | 0.28769 | 0.00085526 | 205 | 61825 | 2012/2013 | August-2012 | 8 | 2012
27972 | Replace H/V Fuse | 2012-08-29 20:40 | 2012-08-29 | 2012-08-29 21:09 | Calculated | TF3396 | TF3396 - Transformer Fuse 3396 |  | 106SEG112-REG30 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 1 | 24554 | 29 | 0.00118 | 4.0727e-05 | 75 | 2185 | 2012/2013 | August-2012 | 8 | 2012
27974 | Change Pole & Xarms | 2012-08-30 08:57 | 2012-08-30 | 2012-08-30 16:02 | Calculated | TF1384 | TF1384 - Transformer Fuse: TF1384 |  | 124SEG478RET | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 355 | 21 | 24554 | 7082 | 0.28843 | 0.00085526 | 205 | 61973 | 2012/2013 | August-2012 | 8 | 2012
27975 | Resite Tx 624 | 2012-08-30 09:30 | 2012-08-30 | 2012-08-30 13:16 | Calculated | 291 | 291 - Air Break Switch 291 |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 226 | 31 | 24554 | 7010 | 0.28549 | 0.0012625 | 248 | 56081 | 2012/2013 | August-2012 | 8 | 2012
27976 | Replace H/V Fuse | 2012-08-30 10:12 | 2012-08-30 | 2012-08-30 11:25 | Calculated | TF310 | TF310 - Transformer Fuse: TF310 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 5 | 24554 | 365 | 0.01487 | 0.00020363 | 30 | 2194 | 2012/2013 | August-2012 | 8 | 2012
27977 | Replace Link | 2012-08-31 08:09 | 2012-08-31 | 2012-08-31 10:04 | Calculated | 249 | 249 - Fused Link 249 |  | 101SEG253-295 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 4 | 24554 | 457 | 0.01861 | 0.00016291 | 25 | 2856 | 2012/2013 | August-2012 | 8 | 2012
27978 | Tx Audit | 2012-08-31 16:52 | 2012-08-31 | 2012-08-31 18:10 | Calculated | TF4297 | TF4297 - Transformer Fuse 4297 |  | 408SEG6707 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 78 | 1 | 24554 | 78 | 0.00318 | 4.0727e-05 | 15 | 1173 | 2012/2013 | August-2012 | 8 | 2012
27979 | Change Poles & Xarms | 2012-09-03 08:53 | 2012-09-03 | 2012-09-03 15:04 | Calculated | 5321 | 5321 - Fused Link 5321 |  | 403SEG5321-5740 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 154 | 27 | 24567 | 446 | 0.01815 | 0.001099 | 160 | 4514 | 2012/2013 | September-2012 | 9 | 2012
27980 | L/V Maintenance | 2012-09-03 11:15 | 2012-09-03 | 2012-09-03 14:57 | Calculated | TF9G2 | TF9G2 - Transformer Fuse: TF9G2 |  | No Segment | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 222 | 4 | 24567 | 888 | 0.03615 | 0.00016282 | 15 | 3332 | 2012/2013 | September-2012 | 9 | 2012
27981 | Replace H/V Fuse | 2012-09-03 20:25 | 2012-09-03 | 2012-09-03 21:08 | Calculated | TF22O5 | TF22O5 - Transformer Fuse: TF22O5 |  | 416SEG5689-5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 3 | 24567 | 126 | 0.00513 | 0.00012212 | 15 | 632 | 2012/2013 | September-2012 | 9 | 2012
27983 | A Line Fault | 2012-09-04 05:00 | 2012-09-04 | 2012-09-04 05:04 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24567 |  | 0 | 0 |  |  | 2012/2013 | September-2012 | 9 | 2012
27984 | A Line Fault | 2012-09-04 05:24 | 2012-09-04 | 2012-09-04 05:28 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24567 |  | 0 | 0 |  |  | 2012/2013 | September-2012 | 9 | 2012
27986 | Change Poles & Xarms | 2012-09-04 09:07 | 2012-09-04 | 2012-09-04 15:59 | Calculated | 5443 | 5443 - Fused Link 5443 |  | 403SEG5766-5460 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 412 | 7 | 24567 | 2885 | 0.11743 | 0.00028494 | 60 | 24729 | 2012/2013 | September-2012 | 9 | 2012
27987 | Upgrade Tx Earth | 2012-09-04 09:44 | 2012-09-04 | 2012-09-04 12:14 | Calculated | TF11K12 | TF11K12 - Transformer Fuse: TF11K12 |  | 409SEG5813 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 150 | 6 | 24567 | 900 | 0.03663 | 0.00024423 | 15 | 2251 | 2012/2013 | September-2012 | 9 | 2012
27988 | Upgrade Tx | 2012-09-04 10:26 | 2012-09-04 | 2012-09-04 16:29 | Calculated | TF1245 | TF1245 - Transformer Fuse: TF1245 |  | 120SEG408-465 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 363 | 1 | 24567 | 363 | 0.01478 | 4.0705e-05 | 3 | 1089 | 2012/2013 | September-2012 | 9 | 2012
27989 | Replace Xarm & DDO @ Tx1536 | 2012-09-04 12:37 | 2012-09-04 | 2012-09-04 14:31 | Calculated | TF1536 | TF1536 - Transformer Fuse: TF1536 |  | 109SEG144 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 3 | 24567 | 222 | 0.00904 | 0.00012212 | 40 | 3666 | 2012/2013 | September-2012 | 9 | 2012
27985 | A Line Fault | 2012-09-04 12:47 | 2012-09-04 | 2012-09-04 12:49 | Calculated | 796 | 796 - Circuit Breaker 796 |  | 301SEG1418-796 | Taharoa A 301-02 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24567 |  | 0 | 0 |  |  | 2012/2013 | September-2012 | 9 | 2012
27990 | Jumper Off @ Pole 47 | 2012-09-04 15:24 | 2012-09-04 | 2012-09-04 17:40 | Calculated | 5259 | 5259 - Fused Link 5259 |  | 422SEG5259-5533 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 110 | 24567 | 12904 | 0.52526 | 0.0044776 | 692 | 83494 | 2012/2013 | September-2012 | 9 | 2012
27991 | Test Earth for Shocks | 2012-09-04 15:26 | 2012-09-04 | 2012-09-04 16:42 | Calculated | TF1632 | TF1632 - Transformer Fuse: TF1632 |  | 113SEG1636-1537 | Mahoenui 113-07 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 3 | 24567 | 228 | 0.00928 | 0.00012212 | 10 | 761 | 2012/2013 | September-2012 | 9 | 2012
27992 | Replace H/V Fuse | 2012-09-05 07:46 | 2012-09-05 | 2012-09-05 09:38 | Calculated | TF12N08 | TF12N08 - Transformer Fuse: TF12N08 |  | 418SEG5836-5589 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 112 | 2 | 24567 | 224 | 0.00912 | 8.141e-05 | 100 | 11215 | 2012/2013 | September-2012 | 9 | 2012
27993 | Replace H/V Fuse | 2012-09-05 07:51 | 2012-09-05 | 2012-09-05 08:51 | Calculated | TF16J01 | TF16J01 - Transformer Fuse: TF16J01 |  | 410SEG5631 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 60 | 2 | 24567 | 120 | 0.00488 | 8.141e-05 | 3 | 180 | 2012/2013 | September-2012 | 9 | 2012
27994 | Pole 41 Burnt Up | 2012-09-05 08:19 | 2012-09-05 | 2012-09-05 17:12 | Calculated | 705 | 705 - Recloser with Bypass & Links 705 |  | 103SEG705-1736 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOF | Pole Top Fire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 118 | 11 | 24567 | 1309 | 0.05328 | 0.00044776 | 67.5 | 8032 | 2012/2013 | September-2012 | 9 | 2012
27995 | Replace Red Tagged Structure Tx467 | 2012-09-05 09:34 | 2012-09-05 | 2012-09-05 14:46 | Calculated | 333 | 333 - Fused Link 333 |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 312 | 30 | 24567 | 9367 | 0.38128 | 0.0012212 | 315 | 98358 | 2012/2013 | September-2012 | 9 | 2012
27996 | Change Poles & Xarms | 2012-09-05 09:42 | 2012-09-05 | 2012-09-05 13:33 | Calculated | 5546 | 5546 - Fused Link 5546 |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 231 | 13 | 24567 | 3005 | 0.12232 | 0.00052917 | 75 | 17339 | 2012/2013 | September-2012 | 9 | 2012
27997 | Raise Tap | 2012-09-05 09:46 | 2012-09-05 | 2012-09-05 10:11 | Calculated | TF4254 | TF4254 - Transformer Fuse: TF4254 |  | 409SEG5447-5319 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 25 | 1 | 24567 | 25 | 0.00102 | 4.0705e-05 | 30 | 754 | 2012/2013 | September-2012 | 9 | 2012
27998 | Replace H/V Fuse | 2012-09-05 12:13 | 2012-09-05 | 2012-09-05 14:14 | Calculated | 1713 | 1713 - Fused Link 1713 |  | 115SEG1713 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 7 | 24567 | 847 | 0.03448 | 0.00028494 | 60 | 7267 | 2012/2013 | September-2012 | 9 | 2012
27999 | Jumper Off Pole 122/7 | 2012-09-05 14:25 | 2012-09-05 | 2012-09-05 15:32 | Calculated | 5453 | 5453 - Fused Link 5453 |  | 413SEG5453-5647 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 67 | 24 | 24567 | 1610 | 0.06554 | 0.00097692 | 127.5 | 8555 | 2012/2013 | September-2012 | 9 | 2012
28000 | Replace Insulator @ Pole 169 | 2012-09-05 15:47 | 2012-09-05 | 2012-09-05 16:45 | Calculated | 1721 | 1721 - Sectionaliser 1721 |  | 117SEG1721-1307 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 58 | 15 | 24567 | 872 | 0.03549 | 0.00061058 | 103 | 5989 | 2012/2013 | September-2012 | 9 | 2012
28001 | L/V Line Down | 2012-09-06 06:11 | 2012-09-06 | 2012-09-06 08:08 | Calculated | TF179 | TF179 - Transformer Fuse: TF179 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:ECUS1 | Customer Installation Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 6 | 24567 | 703 | 0.02862 | 0.00024423 | 50 | 5861 | 2012/2013 | September-2012 | 9 | 2012
28002 | Change Poles & Xarms | 2012-09-06 09:05 | 2012-09-06 | 2012-09-06 15:00 | Calculated | 5740 | 5740 - Sectionaliser with Bypass & Links 5740 |  | 403SEG5740-5546 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 354 | 25 | 24567 | 8858 | 0.36056 | 0.0010176 | 135 | 47837 | 2012/2013 | September-2012 | 9 | 2012
28003 | Private Line Maintenance | 2012-09-06 10:06 | 2012-09-06 | 2012-09-06 11:59 | Calculated | TF1296 | TF1296 - Transformer Fuse: TF1296 |  | 110SEG642-343 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 2 | 24567 | 226 | 0.0092 | 8.141e-05 | 25 | 2827 | 2012/2013 | September-2012 | 9 | 2012
28005 | Upgrade Tx | 2012-09-07 09:36 | 2012-09-07 | 2012-09-07 11:16 | Calculated | TF447 | TF447 - Transformer Fuse: TF447 |  | No Segment | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 100 | 23 | 24567 | 2302 | 0.0937 | 0.00093622 | 30 | 3003 | 2012/2013 | September-2012 | 9 | 2012
28006 | Replace Kidney @ Pole 1061426 | 2012-09-07 15:09 | 2012-09-07 | 2012-09-07 20:34 | Calculated | 354 | 354 - Fused Link 354 |  | 106SEG354 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 325 | 4 | 24567 | 1300 | 0.05292 | 0.00016282 | 25 | 8128 | 2012/2013 | September-2012 | 9 | 2012
28007 | Broken Xarm | 2012-09-07 19:03 | 2012-09-07 | 2012-09-08 03:15 | Calculated | 6353 | 6353 - Sectionaliser with Bypass & Links 6353 |  | 406SEG5658-6355 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 492 | 368 | 24567 | 169701 | 6.9077 | 0.014979 | 2133.75 | 906311 | 2012/2013 | September-2012 | 9 | 2012
28010 | Re-fix Stay Straps | 2012-09-08 11:08 | 2012-09-08 | 2012-09-08 12:58 | Calculated | 127 | 127 - Circuit Breaker 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 71 | 24567 | 4056 | 0.1651 | 0.0028901 | 530 | 30280 | 2012/2013 | September-2012 | 9 | 2012
28009 | Replace H/V Fuse | 2012-09-08 11:46 | 2012-09-08 | 2012-09-08 18:01 | Calculated | 6012 | 6012 - Air Break Switch 6012 |  | 415SEG6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 375 | 1 | 24567 | 375 | 0.01526 | 4.0705e-05 | 50 | 18755 | 2012/2013 | September-2012 | 9 | 2012
28011 | Replace H/V Fuse | 2012-09-08 21:57 | 2012-09-08 | 2012-09-09 00:19 | Calculated | TF1627 | TF1627 - Transformer Fuse: TF1627 |  | 113SEG1548-1526 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 2 | 24567 | 284 | 0.01156 | 8.141e-05 | 7.5 | 1065 | 2012/2013 | September-2012 | 9 | 2012
28012 | Replace H/V Fuse | 2012-09-09 00:17 | 2012-09-09 | 2012-09-09 09:25 | Calculated | TF2185 | TF2185 - Transformer Fuse: TF2185 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 548 | 2 | 24567 | 1096 | 0.04461 | 8.141e-05 | 10 | 5481 | 2012/2013 | September-2012 | 9 | 2012
28014 | Replace H/V Fuse | 2012-09-09 21:21 | 2012-09-09 | 2012-09-09 23:10 | Calculated | TF508 | TF508 - Transformer Fuse: TF508 |  | 101SEG274-506 | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 3 | 24567 | 327 | 0.01331 | 0.00012212 | 15 | 1636 | 2012/2013 | September-2012 | 9 | 2012
28015 | Tree on Line - Line Down | 2012-09-10 05:01 | 2012-09-10 | 2012-09-10 15:49 | Calculated | 5506 | 5506 - Sectionaliser with Bypass & Links 5506 |  | 413SEG5506 | Ohura 413-03 | Rural D | Ohura | Nihoniho Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 611 | 26 | 24567 | 12547 | 0.51073 | 0.0010583 | 205.5 | 105034 | 2012/2013 | September-2012 | 9 | 2012
28016 | Replace H/V Fuse | 2012-09-10 06:35 | 2012-09-10 | 2012-09-10 09:13 | Calculated | TF2170 | TF2170 - Transformer Fuse: TF2170 |  | 128SEG1601 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 3 | 24567 | 474 | 0.01929 | 0.00012212 | 25 | 3953 | 2012/2013 | September-2012 | 9 | 2012
28017 | Replace H/V Fuse | 2012-09-10 06:57 | 2012-09-10 | 2012-09-10 07:59 | Calculated | TF506 | TF506 - Transformer Fuse: TF506 |  | 101SEG274-506 | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 4 | 24567 | 248 | 0.01009 | 0.00016282 | 10 | 621 | 2012/2013 | September-2012 | 9 | 2012
28018 | Close Sect | 2012-09-10 08:33 | 2012-09-10 | 2012-09-10 10:44 | Calculated | 5281 | 5281 - Recloser with Bypass & Links 5281 |  | 413SEG5281-5283 | Ohura 413-03 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 131 | 20 | 24567 | 2622 | 0.10673 | 0.0008141 | 153 | 20060 | 2012/2013 | September-2012 | 9 | 2012
28019 | Replace H/V Fuse | 2012-09-10 09:02 | 2012-09-10 | 2012-09-10 10:47 | Calculated | TF1837 | TF1837 - Transformer Fuse: TF1837 |  | 128SEG1612-1613 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 105 | 2 | 24567 | 210 | 0.00855 | 8.141e-05 | 10 | 1051 | 2012/2013 | September-2012 | 9 | 2012
28021 | Replace H/V Fuse | 2012-09-10 10:35 | 2012-09-10 | 2012-09-10 13:31 | Calculated | TF2539 | TF2539 - Transformer Fuse: TF2539 |  | No Segment | Coast 125-06 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 176 | 1 | 24567 | 176 | 0.00716 | 4.0705e-05 | 5 | 880 | 2012/2013 | September-2012 | 9 | 2012
28020 | Replace H/V Fuse | 2012-09-10 10:35 | 2012-09-10 | 2012-09-10 12:56 | Calculated | TF2812 | TF2812 - Transformer Fuse: TF2812 |  | No Segment | Coast 125-06 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 140 | 1 | 24567 | 140 | 0.0057 | 4.0705e-05 | 5 | 700 | 2012/2013 | September-2012 | 9 | 2012
28022 | Replace H/V Fuse | 2012-09-10 12:38 | 2012-09-10 | 2012-09-10 14:34 | Calculated | TF1817 | TF1817 - Transformer Fuse: TF1817 |  | 103SEG1346-1326 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 115 | 1 | 24567 | 115 | 0.00468 | 4.0705e-05 | 7.5 | 863 | 2012/2013 | September-2012 | 9 | 2012
28023 | Replace H/V Fuse | 2012-09-10 13:03 | 2012-09-10 | 2012-09-10 15:00 | Calculated | TF4I16 | TF4I16 - Transformer Fuse: TF4I16 |  | 402SEG5171 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 117 | 1 | 24567 | 117 | 0.00476 | 4.0705e-05 | 10 | 1171 | 2012/2013 | September-2012 | 9 | 2012
28024 | Faulty Tx for CB 727 | 2012-09-10 14:25 | 2012-09-10 | 2012-09-10 14:29 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 3414 | 24567 | 8184 | 0.33313 | 0.13897 | 26335 | 60456 | 2012/2013 | September-2012 | 9 | 2012
28025 | Close Sect | 2012-09-10 15:56 | 2012-09-10 | 2012-09-10 16:48 | Calculated | 5507 | 5507 - Sectionaliser with Bypass & Links 5507 |  | 413SEG5507 | Ohura 413-03 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 52 | 6 | 24567 | 312 | 0.0127 | 0.00024423 | 50 | 2607 | 2012/2013 | September-2012 | 9 | 2012
28027 | Bypass Faulty Recloser | 2012-09-11 06:07 | 2012-09-11 | 2012-09-11 07:23 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 99 | 24567 | 7538 | 0.30683 | 0.0040298 | 988 | 75236 | 2012/2013 | September-2012 | 9 | 2012
28028 | Pole Changes | 2012-09-11 08:36 | 2012-09-11 | 2012-09-11 15:07 | Calculated | 5237 | 5237 - Sectionaliser with Bypass 5237 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 390 | 40 | 24567 | 15604 | 0.63516 | 0.0016282 | 212.5 | 82899 | 2012/2013 | September-2012 | 9 | 2012
28029 | Replace H/V Fuse | 2012-09-11 12:34 | 2012-09-11 | 2012-09-11 13:52 | Calculated | TF416 | TF416 - Transformer Fuse: TF416 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 4 | 24567 | 312 | 0.0127 | 0.00016282 | 55 | 4299 | 2012/2013 | September-2012 | 9 | 2012
28031 | Bypass Faulty Sectionaliser | 2012-09-11 13:56 | 2012-09-11 | 2012-09-11 16:17 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | 410SEG5511-5517 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 141 | 27 | 24567 | 3810 | 0.15509 | 0.001099 | 183.5 | 25894 | 2012/2013 | September-2012 | 9 | 2012
28032 | Replace H/V Fuse | 2012-09-11 18:20 | 2012-09-11 | 2012-09-11 19:25 | Calculated | TF1004 | TF1004 - Transformer Fuse: TF1004 |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 4 | 24567 | 260 | 0.01058 | 0.00016282 | 30 | 1953 | 2012/2013 | September-2012 | 9 | 2012
28033 | Pole Changes | 2012-09-12 08:32 | 2012-09-12 | 2012-09-12 15:48 | Calculated | 5237 | 5237 - Sectionaliser with Bypass 5237 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 436 | 40 | 24567 | 17446 | 0.71014 | 0.0016282 | 212.5 | 92685 | 2012/2013 | September-2012 | 9 | 2012
28034 | Replace Poles & Xarms | 2012-09-12 09:03 | 2012-09-12 | 2012-09-12 13:26 | Calculated | 447 | 447 - Fused Link 447 |  | 129SEG447 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 263 | 13 | 24567 | 3420 | 0.13921 | 0.00052917 | 145 | 38151 | 2012/2013 | September-2012 | 9 | 2012
28036 | Broken Tx Earth | 2012-09-12 13:31 | 2012-09-12 | 2012-09-12 14:34 | Calculated | TF2079 | TF2079 - Transformer Fuse: TF2079 |  | No Segment | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 63 | 2 | 24567 | 126 | 0.00513 | 8.141e-05 | 10 | 631 | 2012/2013 | September-2012 | 9 | 2012
28037 | Replace H/V Fuse | 2012-09-12 14:01 | 2012-09-12 | 2012-09-12 15:01 | Calculated | TF4093 | TF4093 - Transformer Fuse: TF4093 |  | No Segment | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 60 | 1 | 24567 | 60 | 0.00244 | 4.0705e-05 | 5 | 300 | 2012/2013 | September-2012 | 9 | 2012
28038 | Replace H/V Fuse | 2012-09-13 06:31 | 2012-09-13 | 2012-09-13 08:02 | Calculated | TF1982 | TF1982 - Transformer Fuse: TF1982 |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 2 | 24567 | 182 | 0.00741 | 8.141e-05 | 10 | 911 | 2012/2013 | September-2012 | 9 | 2012
28039 | Replace H/V Fuse | 2012-09-13 10:24 | 2012-09-13 | 2012-09-13 11:57 | Calculated | TF7C1 | TF7C1 - Transformer Fuse: TF7C1 |  | 413SEG5420-5305 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 93 | 1 | 24567 | 93 | 0.00379 | 4.0705e-05 | 15 | 1396 | 2012/2013 | September-2012 | 9 | 2012
28040 | Replace H/V Fuse | 2012-09-13 11:49 | 2012-09-13 | 2012-09-13 13:28 | Calculated | TF1889 | TF1889 - Transformer Fuse: TF1889 |  | 128SEG1358-1602 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 2 | 24567 | 198 | 0.00806 | 8.141e-05 | 15 | 1486 | 2012/2013 | September-2012 | 9 | 2012
28041 | Replace H/V Fuse | 2012-09-14 13:29 | 2012-09-14 | 2012-09-14 16:33 | Calculated | TF7C3 | TF7C3 - Transformer Fuse: TF7C3 |  | 413SEG5304 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 184 | 1 | 24567 | 184 | 0.00749 | 4.0705e-05 | 10 | 1841 | 2012/2013 | September-2012 | 9 | 2012
28042 | Replace H/V Fuse | 2012-09-15 12:06 | 2012-09-15 | 2012-09-15 13:15 | Calculated | TF1676 | TF1676 - Transformer Fuse: TF1676 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 1 | 24567 | 69 | 0.00281 | 4.0705e-05 | 10 | 691 | 2012/2013 | September-2012 | 9 | 2012
28043 | Replace L/A | 2012-09-16 12:45 | 2012-09-16 | 2012-09-16 13:39 | Calculated | TF2956 | TF2956 - Transformer Fuse: TF2956 |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1 | 24567 | 54 | 0.0022 | 4.0705e-05 | 30 | 1623 | 2012/2013 | September-2012 | 9 | 2012
28044 | Remove Birds Nest | 2012-09-17 09:41 | 2012-09-17 | 2012-09-17 12:18 | Calculated | TF835 | TF835 - Transformer Fuse: TF835 |  | 103SEG236-731 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 2 | 24567 | 314 | 0.01278 | 8.141e-05 | 5 | 785 | 2012/2013 | September-2012 | 9 | 2012
28045 | Replace Jumpers & Repair Wire | 2012-09-17 09:47 | 2012-09-17 | 2012-09-17 15:38 | Calculated | 1259 | 1259 - Solid Link 1259 |  | 117SEG1259-1722 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 7 | 39 | 24567 | 312 | 0.0127 | 0.0015875 | 318 | 2544 | 2012/2013 | September-2012 | 9 | 2012
28046 | Replace Broken Pole | 2012-09-17 11:36 | 2012-09-17 | 2012-09-17 13:54 | Calculated | 269 | 269 - Load Break Switch 269 |  | 116SEG1334-269 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 290 | 24567 | 1120 | 0.04559 | 0.011804 | 2482.5 | 8095 | 2012/2013 | September-2012 | 9 | 2012
28047 | Replace H/V Fuse | 2012-09-18 09:29 | 2012-09-18 | 2012-09-18 12:28 | Calculated | TF9I12 | TF9I12 - Transformer Fuse: TF9I12 |  | No Segment | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 179 | 3 | 24567 | 537 | 0.02186 | 0.00012212 | 15 | 2687 | 2012/2013 | September-2012 | 9 | 2012
28048 | Eye Bolt Out @ Tx 528 | 2012-09-18 10:04 | 2012-09-18 | 2012-09-18 11:20 | Calculated | 583 | 583 - Air Break Switch 583 |  | 125SEG296-583 | Coast 125-04 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 145 | 24567 | 11036 | 0.44922 | 0.0059022 | 972.1014 | 73993 | 2012/2013 | September-2012 | 9 | 2012
28049 | Floating Insulator @ Tx 2722 | 2012-09-18 16:46 | 2012-09-18 | 2012-09-18 17:56 | Calculated | 2041 | 2041 - Fused Link 2041 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 4 | 24567 | 280 | 0.0114 | 0.00016282 | 65 | 4557 | 2012/2013 | September-2012 | 9 | 2012
28050 | Fit new Xarm & T/O Fuses | 2012-09-19 09:08 | 2012-09-19 | 2012-09-19 14:19 | Calculated | 5549 | 5549 - Air Break Switch 5549 |  | 409SEG5549 | Southern 409-02 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 311 | 11 | 24567 | 3422 | 0.13929 | 0.00044776 | 72.5 | 22557 | 2012/2013 | September-2012 | 9 | 2012
28051 | Move Tx 1309 | 2012-09-19 09:34 | 2012-09-19 | 2012-09-19 16:16 | Calculated | 172 | 172 - Fused Link 172 |  | 111SEG172 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 402 | 15 | 24567 | 6031 | 0.24549 | 0.00061058 | 115 | 46243 | 2012/2013 | September-2012 | 9 | 2012
28052 | Replace Xarm @ Pole 1250231 | 2012-09-20 09:01 | 2012-09-20 | 2012-09-20 15:54 | Calculated | TF640 | TF640 - Transformer Fuse: TF640 |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 294 | 145 | 24567 | 17705 | 0.72068 | 0.0059022 | 972.1014 | 170924 | 2012/2013 | September-2012 | 9 | 2012
28054 | Remove Tx 4e5 | 2012-09-20 11:05 | 2012-09-20 | 2012-09-20 11:45 | Calculated | 5753 | 5753 - Fused Link 5753 |  | 422SEG5753 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 40 | 3 | 24567 | 120 | 0.00488 | 0.00012212 | 21 | 843 | 2012/2013 | September-2012 | 9 | 2012
28055 | Replace Poles | 2012-09-21 09:02 | 2012-09-21 | 2012-09-21 14:26 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 324 | 21 | 24567 | 6807 | 0.27708 | 0.00085481 | 178 | 57701 | 2012/2013 | September-2012 | 9 | 2012
28056 | Replace L/A's | 2012-09-21 10:05 | 2012-09-21 | 2012-09-21 11:53 | Calculated | TF712 | TF712 - Transformer Fuse: TF712 |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 107 | 4 | 24567 | 428 | 0.01742 | 0.00016282 | 25 | 2680 | 2012/2013 | September-2012 | 9 | 2012
28057 | Close Loose Link | 2012-09-21 14:44 | 2012-09-21 | 2012-09-21 14:45 | Calculated | 5367J | 5367J - Incoming Link 5367J |  | 403SEG5367-5875 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1 | 20 | 24567 | 33 | 0.00134 | 0.0008141 | 110 | 183 | 2012/2013 | September-2012 | 9 | 2012
28058 | Loose L/V Neutral | 2012-09-22 10:05 | 2012-09-22 | 2012-09-22 12:10 | Calculated | TF4261 | TF4261 - Transformer Fuse: TF4261 |  | 415SEG6565 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 4 | 24567 | 500 | 0.02035 | 0.00016282 | 100 | 12513 | 2012/2013 | September-2012 | 9 | 2012
28059 | Replace Pole 8 | 2012-09-23 13:01 | 2012-09-23 | 2012-09-23 14:47 | Calculated | 757 | 757 - Recloser Switch 757 |  | 107SEG243-113 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 88 | 9 | 24567 | 789 | 0.03212 | 0.00036635 | 65 | 5701 | 2012/2013 | September-2012 | 9 | 2012
28060 | L/V Maintenance | 2012-09-24 00:07 | 2012-09-24 | 2012-09-24 02:26 | Calculated | 5.26 | 5.26 - Ring Main Unit 5.26 |  | No Segment | No Asset Group | Remote Rural F | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 25 | 24567 | 3479 | 0.14161 | 0.0010176 | 288.4615 | 40149 | 2012/2013 | September-2012 | 9 | 2012
28061 | Replace Structure Tx 11k12 | 2012-09-24 09:36 | 2012-09-24 | 2012-09-24 16:16 | Calculated | 5813 | 5813 - Fused Link 5813 |  | 409SEG5432-5813 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 399 | 7 | 24567 | 2794 | 0.11373 | 0.00028494 | 30 | 11976 | 2012/2013 | September-2012 | 9 | 2012
28065 | Replace H/V Fuse | 2012-09-24 16:46 | 2012-09-24 | 2012-09-25 09:45 | Calculated | TF1493 | TF1493 - Transformer Fuse: TF1493 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1019 | 2 | 24567 | 2038 | 0.08296 | 8.141e-05 | 15 | 15287 | 2012/2013 | September-2012 | 9 | 2012
28063 | Change Poles & Xarms | 2012-09-25 08:06 | 2012-09-25 | 2012-09-25 16:24 | Calculated | TF2432 | TF2432 - Transformer Fuse: TF2432 |  | 114SEG1126-1127 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 436 | 52 | 24567 | 7726 | 0.31449 | 0.0021167 | 375 | 56414 | 2012/2013 | September-2012 | 9 | 2012
28064 | L/V Jumper off Tx | 2012-09-25 08:53 | 2012-09-25 | 2012-09-25 10:02 | Calculated | TF468 | TF468 - Transformer Fuse: TF468 |  | 111SEG325 | Maihiihi 111-02 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 15 | 24567 | 1038 | 0.04225 | 0.00061058 | 50 | 3459 | 2012/2013 | September-2012 | 9 | 2012
28066 | Lower Tap | 2012-09-25 11:28 | 2012-09-25 | 2012-09-25 11:45 | Calculated | TF4155 | TF4155 - Transformer Fuse: TF4155 |  | 426SEG5220 | Waihaha 426-02 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLS | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 14 | 24567 | 240 | 0.00977 | 0.00056987 | 186.6667 | 3201 | 2012/2013 | September-2012 | 9 | 2012
28067 | Replace H/V Fuse | 2012-09-25 12:11 | 2012-09-25 | 2012-09-25 13:49 | Calculated | TF2183 | TF2183 - Transformer Fuse: TF2183 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 98 | 1 | 24567 | 98 | 0.00399 | 4.0705e-05 | 10 | 981 | 2012/2013 | September-2012 | 9 | 2012
28068 | B Line Fault | 2012-09-26 06:35 | 2012-09-26 | 2012-09-26 07:02 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 253 | 24567 | 295 | 0.01201 | 0.010298 | 2266 | 2643 | 2012/2013 | September-2012 | 9 | 2012
28069 | Rebuild of Okahukura SWER Sub | 2012-09-26 08:26 | 2012-09-26 | 2012-09-26 16:02 | Calculated | 5343 | 5343 - Fused Link 5343 |  | 402SEG5343-5446 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 419 | 69 | 24567 | 11762 | 0.47877 | 0.0028086 | 460 | 70460 | 2012/2013 | September-2012 | 9 | 2012
28070 | Replace Pole 1150264 | 2012-09-26 09:47 | 2012-09-26 | 2012-09-26 15:31 | Calculated | 1725 | 1725 - Fused Link 1725 |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 343 | 5 | 24567 | 1716 | 0.06985 | 0.00020353 | 60 | 20592 | 2012/2013 | September-2012 | 9 | 2012
28071 | Replace Red Tagged Pole 1222012 | 2012-09-26 10:22 | 2012-09-26 | 2012-09-26 15:52 | Calculated | 443 | 443 - Fused Link 443 |  | 122SEG443 | Wharepapa 122-01 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 330 | 18 | 24567 | 5942 | 0.24187 | 0.00073269 | 130 | 42915 | 2012/2013 | September-2012 | 9 | 2012
28072 | Pole Changes | 2012-09-27 08:36 | 2012-09-27 | 2012-09-27 16:33 | Calculated | TF8P2 | TF8P2 - Transformer Fuse: TF8P2 |  | 426SEG5892-5240 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 466 | 55 | 24567 | 9172 | 0.37335 | 0.0022388 | 317.5 | 58349 | 2012/2013 | September-2012 | 9 | 2012
28073 | Upgrade Tx 896 to 3 Phase | 2012-09-27 09:19 | 2012-09-27 | 2012-09-27 11:48 | Calculated | TF896 | TF896 - Transformer Fuse: TF896 |  | 123SEG450-469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 149 | 3 | 24567 | 447 | 0.0182 | 0.00012212 | 15 | 2237 | 2012/2013 | September-2012 | 9 | 2012
28074 | Restrain L/V | 2012-09-27 09:38 | 2012-09-27 | 2012-09-27 10:40 | Calculated | TF3H11 | TF3H11 - Transformer Fuse: TF3H11 |  | No Segment | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:ECUS1 | Customer Installation Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 62 | 1 | 24567 | 62 | 0.00252 | 4.0705e-05 | 15 | 932 | 2012/2013 | September-2012 | 9 | 2012
28075 | Replace Link | 2012-09-28 09:10 | 2012-09-28 | 2012-09-28 14:26 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 167 | 26 | 24567 | 4323 | 0.17597 | 0.0010583 | 305 | 50721 | 2012/2013 | September-2012 | 9 | 2012
28076 | Reconductor Line | 2012-09-30 08:44 | 2012-09-30 | 2012-09-30 16:02 | Calculated | TF1390 | TF1390 - Transformer Fuse: TF1390 |  | 126SEG504-578 | Rural 126-01 | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 41 | 24567 | 1763 | 0.07176 | 0.0016689 | 200 | 8600 | 2012/2013 | September-2012 | 9 | 2012
28077 | Replace H/V Fuse | 2012-10-01 06:04 | 2012-10-01 | 2012-10-01 08:56 | Calculated | TF959 | TF959 - Transformer Fuse: TF959 |  | 101SEG519-232 | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 1 | 24596 | 172 | 0.00699 | 4.0657e-05 | 15 | 2582 | 2012/2013 | October-2012 | 10 | 2012
28079 | Lightning | 2012-10-02 02:20 | 2012-10-02 | 2012-10-02 03:48 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24596 |  | 0 | 0 |  |  | 2012/2013 | October-2012 | 10 | 2012
28080 | Replace H/V Fuse | 2012-10-02 06:30 | 2012-10-02 | 2012-10-02 07:40 | Calculated | TF1685 | TF1686 - Transformer Fuse: TF1686 |  | 116SEG1354-1334 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 3 | 24596 | 210 | 0.00854 | 0.00012197 | 15 | 1052 | 2012/2013 | October-2012 | 10 | 2012
28081 | Replace H/V Fuse | 2012-10-02 06:53 | 2012-10-02 | 2012-10-02 08:23 | Calculated | TF153 | TF153 - Transformer Fuse: TF153 |  | 116SEG1334-269 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 4 | 24596 | 360 | 0.01464 | 0.00016263 | 25 | 2253 | 2012/2013 | October-2012 | 10 | 2012
28082 | Replace H/V Fuse | 2012-10-02 07:52 | 2012-10-02 | 2012-10-02 08:46 | Calculated | TF154 | TF154 - Transformer Fuse: TF154 |  | 116SEG1334-269 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 2 | 24596 | 108 | 0.00439 | 8.1314e-05 | 25 | 1356 | 2012/2013 | October-2012 | 10 | 2012
28083 | Replace H/V Fuse | 2012-10-02 07:58 | 2012-10-02 | 2012-10-02 09:07 | Calculated | TF151 | TF151 - Transformer Fuse: TF151 |  | 107SEG176-269 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 2 | 24596 | 138 | 0.00561 | 8.1314e-05 | 25 | 1728 | 2012/2013 | October-2012 | 10 | 2012
28084 | Replace H/V Fuse | 2012-10-02 08:04 | 2012-10-02 | 2012-10-02 09:18 | Calculated | TF919 | TF919 - Transformer Fuse: TF919 |  | 116SEG272 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 5 | 24596 | 370 | 0.01504 | 0.00020329 | 15 | 1111 | 2012/2013 | October-2012 | 10 | 2012
28085 | Pole Changes | 2012-10-02 08:20 | 2012-10-02 | 2012-10-02 15:54 | Calculated | TF9P1 | TF9P1 - Transformer Fuse: TF9P1 |  | 426SEG5240-5242 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 412 | 40 | 24596 | 7065 | 0.28724 | 0.0016263 | 212.5 | 43486 | 2012/2013 | October-2012 | 10 | 2012
28086 | Replace H/V Fuse | 2012-10-02 08:37 | 2012-10-02 | 2012-10-02 11:04 | Calculated | TF2036 | TF2036 - Transformer Fuse: TF2036 |  | 115SEG1730 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 1 | 24596 | 147 | 0.00598 | 4.0657e-05 | 10 | 1471 | 2012/2013 | October-2012 | 10 | 2012
28087 | Replace H/V Fuse | 2012-10-02 09:20 | 2012-10-02 | 2012-10-02 09:37 | Calculated | TF1345 | TF1345 - Transformer Fuse: TF1345 |  | 116SEG1334-269 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 2 | 24596 | 34 | 0.00138 | 8.1314e-05 | 15 | 256 | 2012/2013 | October-2012 | 10 | 2012
28088 | Replace H/V Fuse | 2012-10-02 10:16 | 2012-10-02 | 2012-10-02 11:51 | Calculated | TF9E16 | TF9E16 - Transformer Fuse: TF9E16 |  | No Segment | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 95 | 1 | 24596 | 95 | 0.00386 | 4.0657e-05 | 15 | 1426 | 2012/2013 | October-2012 | 10 | 2012
28089 | Replace H/V Fuse | 2012-10-02 14:23 | 2012-10-02 | 2012-10-02 15:02 | Calculated | TF9E16 | TF9E16 - Transformer Fuse: TF9E16 |  | No Segment | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 39 | 1 | 24596 | 39 | 0.00159 | 4.0657e-05 | 15 | 587 | 2012/2013 | October-2012 | 10 | 2012
28090 | Replace H/V Fuse | 2012-10-03 07:07 | 2012-10-03 | 2012-10-03 10:04 | Calculated | TF1873 | TF1873 - Transformer Fuse: TF1873 |  | 113SEG1520 | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 8 | 24596 | 1417 | 0.05761 | 0.00032526 | 50 | 8856 | 2012/2013 | October-2012 | 10 | 2012
28091 | Replace H/V Fuse | 2012-10-03 07:18 | 2012-10-03 | 2012-10-03 07:39 | Calculated | TF20L41 | TF20L41 - Transformer Fuse: TF20L41 |  | 414SEG6644-5643 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 61 | 24596 | 1229 | 0.04997 | 0.0024801 | 200 | 4029 | 2012/2013 | October-2012 | 10 | 2012
28093 | Install New Pole | 2012-10-04 09:33 | 2012-10-04 | 2012-10-04 15:10 | Calculated | 5409 | 5409 - Recloser with Bypass 5409 |  | 426SEG5409-5333 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 37 | 24596 | 5770 | 0.23459 | 0.0015043 | 272.5 | 47030 | 2012/2013 | October-2012 | 10 | 2012
28094 | Replace Red Tagged Pole 1091355 | 2012-10-04 09:36 | 2012-10-04 | 2012-10-04 15:37 | Calculated | 333 | 333 - Fused Link 333 |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 361 | 29 | 24596 | 10473 | 0.4258 | 0.0011791 | 315 | 113762 | 2012/2013 | October-2012 | 10 | 2012
28095 | Neutral Fault | 2012-10-04 11:48 | 2012-10-04 | 2012-10-04 12:38 | Calculated | TF156 | TF156 - Transformer Fuse: TF156 |  | 116SEG272 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 2 | 24596 | 100 | 0.00407 | 8.1314e-05 | 15 | 752 | 2012/2013 | October-2012 | 10 | 2012
28097 | Corroded Neutral Connection | 2012-10-04 17:03 | 2012-10-04 | 2012-10-04 17:37 | Calculated | TF1008 | TF1008 - Transformer Fuse: TF1008 |  | 111SEG138-663 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 35 | 24596 | 1162 | 0.04724 | 0.001423 | 200 | 6643 | 2012/2013 | October-2012 | 10 | 2012
28098 | Change Poles & Xarms | 2012-10-05 09:12 | 2012-10-05 | 2012-10-05 15:20 | Calculated | 5829 | 5829 - Fused Link 5829 |  | 410SEG5829-5545 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 367 | 23 | 24596 | 8445 | 0.34335 | 0.00093511 | 130 | 47733 | 2012/2013 | October-2012 | 10 | 2012
28100 | Replace H/V Fuse | 2012-10-06 07:37 | 2012-10-06 | 2012-10-06 09:04 | Calculated | TF5L3 | TF5L3 - Transformer Fuse: TF5L3 |  | No Segment | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 87 | 3 | 24596 | 261 | 0.01061 | 0.00012197 | 25 | 2179 | 2012/2013 | October-2012 | 10 | 2012
28101 | Replace H/V Fuse | 2012-10-06 10:20 | 2012-10-06 | 2012-10-06 11:30 | Calculated | TF996 | TF996 - Transformer Fuse: TF996 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 4 | 24596 | 280 | 0.01138 | 0.00016263 | 25 | 1753 | 2012/2013 | October-2012 | 10 | 2012
28103 | Replace H/V Fuse | 2012-10-06 15:20 | 2012-10-06 | 2012-10-06 21:25 | Calculated | TF1004 | TF1004 - Transformer Fuse: TF1004 |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 4 | 24596 | 601 | 0.02443 | 0.00016263 | 30 | 4509 | 2012/2013 | October-2012 | 10 | 2012
28104 | Close CB | 2012-10-06 19:42 | 2012-10-06 | 2012-10-06 19:45 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 4 | 24596 | 12 | 0.00049 | 0.00016263 | 450 | 1410 | 2012/2013 | October-2012 | 10 | 2012
28105 | Replace H/V Fuse | 2012-10-08 04:15 | 2012-10-08 | 2012-10-08 06:10 | Calculated | 458 | 458 - Fused Link 458 |  | 129SEG458 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 7 | 24596 | 806 | 0.03277 | 0.0002846 | 80 | 9211 | 2012/2013 | October-2012 | 10 | 2012
28106 | Replace Faulty Tx | 2012-10-08 08:22 | 2012-10-08 | 2012-10-08 12:49 | Calculated | TF2178 | TF2178 - Transformer Fuse: TF2178 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 267 | 2 | 24596 | 534 | 0.02171 | 8.1314e-05 | 15 | 4007 | 2012/2013 | October-2012 | 10 | 2012
28107 | Replace Poles & Xarms | 2012-10-08 08:54 | 2012-10-08 | 2012-10-08 13:05 | Calculated | 635 | 635 - Air Break Switch 635 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 234 | 126 | 24596 | 3031 | 0.12323 | 0.0051228 | 1595 | 33811 | 2012/2013 | October-2012 | 10 | 2012
28108 | Replace H/V Fuse | 2012-10-08 15:16 | 2012-10-08 | 2012-10-08 15:53 | Calculated | 6012 | 6012 - Air Break Switch 6012 |  | 415SEG6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 1 | 24596 | 37 | 0.0015 | 4.0657e-05 | 50 | 1863 | 2012/2013 | October-2012 | 10 | 2012
28109 | Replace H/V Fuse | 2012-10-09 07:50 | 2012-10-09 | 2012-10-09 08:28 | Calculated | 6012 | 6012 - Air Break Switch 6012 |  | 415SEG6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 1 | 24596 | 38 | 0.00154 | 4.0657e-05 | 50 | 1909 | 2012/2013 | October-2012 | 10 | 2012
28110 | Possum @ Tx 1851 | 2012-10-09 08:46 | 2012-10-09 | 2012-10-09 11:35 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 169 | 5 | 24596 | 847 | 0.03444 | 0.00020329 | 80 | 13561 | 2012/2013 | October-2012 | 10 | 2012
28111 | Tree Felled Through Line | 2012-10-09 12:38 | 2012-10-09 | 2012-10-09 16:59 | Calculated | 6063 | 6063 - Circuit Breaker 6063 |  | 404SEG6063-A1.3 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 260 | 1304 | 24596 | 93716 | 3.8102 | 0.053017 | 8738.965 | 492289 | 2012/2013 | October-2012 | 10 | 2012
28113 | Jumper Off Link 1613 | 2012-10-09 23:37 | 2012-10-09 | 2012-10-10 00:31 | Calculated | 1612 | 1612 - Sectionaliser with Bypass & Links 1612 |  | 128SEG1611-1612 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 54 | 42 | 24596 | 2273 | 0.09241 | 0.0017076 | 325 | 17593 | 2012/2013 | October-2012 | 10 | 2012
28115 | Pole Changes | 2012-10-11 09:05 | 2012-10-11 | 2012-10-11 15:13 | Calculated | 5580 | 5580 - Fused Link 5580 |  | 426SEG5526-5359 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 368 | 10 | 24596 | 3682 | 0.1497 | 0.00040657 | 90 | 33145 | 2012/2013 | October-2012 | 10 | 2012
28116 | Replace H/V Fuse | 2012-10-11 14:17 | 2012-10-11 | 2012-10-11 17:04 | Calculated | 234 | 234 - Fused Link 234 |  | 107SEG234 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 167 | 17 | 24596 | 2841 | 0.11551 | 0.00069117 | 112.5 | 18802 | 2012/2013 | October-2012 | 10 | 2012
28118 | Replace Structure Tx 13k13 | 2012-10-12 09:36 | 2012-10-12 | 2012-10-12 16:37 | Calculated | TF13K05 | TF13K05 - Transformer Fuse: TF13K05 |  | 410SEG5139-5829 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 421 | 10 | 24596 | 4212 | 0.17125 | 0.00040657 | 100 | 42126 | 2012/2013 | October-2012 | 10 | 2012
28119 | Replace L/V Poles | 2012-10-12 09:46 | 2012-10-12 | 2012-10-12 15:59 | Calculated | TF228 | TF228 - Transformer Fuse: TF228 |  | 111SEG325 | Maihiihi 111-02 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 373 | 8 | 24596 | 2985 | 0.12136 | 0.00032526 | 50 | 18660 | 2012/2013 | October-2012 | 10 | 2012
28120 | Fit new PTF & Polymer | 2012-10-12 11:01 | 2012-10-12 | 2012-10-12 13:02 | Calculated | 5897 | 5897 - Earth Working Link 5897 |  | 406SEG5897-5481 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 120 | 17 | 24596 | 2044 | 0.0831 | 0.00069117 | 100 | 12025 | 2012/2013 | October-2012 | 10 | 2012
28132 | Replace H/V Fuse | 2012-10-13 07:16 | 2012-10-13 | 2012-10-13 19:03 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 707 | 26 | 24596 | 18385 | 0.74748 | 0.0010571 | 281.4286 | 199007 | 2012/2013 | October-2012 | 10 | 2012
28121 | Replace H/V Fuse | 2012-10-13 08:33 | 2012-10-13 | 2012-10-13 10:20 | Calculated | 5454 | 5454 - Fused Link 5454 |  | 413SEG5454-5455 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 107 | 23 | 24596 | 2464 | 0.10018 | 0.00093511 | 153 | 16391 | 2012/2013 | October-2012 | 10 | 2012
28122 | Tree on Line | 2012-10-13 12:34 | 2012-10-13 | 2012-10-14 00:07 | Calculated | 687 | 687 - Circuit Breaker 687 |  | 117SEG687-1289 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 380 | 229 | 24596 | 56159 | 2.2833 | 0.0093105 | 1867 | 458419 | 2012/2013 | October-2012 | 10 | 2012
28123 | Line on Xarm | 2012-10-13 12:58 | 2012-10-13 | 2012-10-13 19:49 | Calculated | 117 | 117 - Circuit Breaker 117 |  | 111SEG647-117RET | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 411 | 228 | 24596 | 38595 | 1.5692 | 0.0092698 | 2261.25 | 327511 | 2012/2013 | October-2012 | 10 | 2012
28147 | Replace H/V Fuse | 2012-10-13 13:01 | 2012-10-13 | 2012-10-14 12:04 | Calculated | TF7G3 | TF7G3 - Transformer Fuse: TF7G3 |  | No Segment | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1383 | 2 | 24596 | 2766 | 0.11246 | 8.1314e-05 | 7.5 | 10373 | 2012/2013 | October-2012 | 10 | 2012
28124 | Wire off Insulator | 2012-10-13 13:01 | 2012-10-13 | 2012-10-13 22:28 | Calculated | 378 | 378 - Recloser 378 |  | 122SEG448-REG34J | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 552 | 302 | 24596 | 44616 | 1.8139 | 0.012278 | 2753 | 379916 | 2012/2013 | October-2012 | 10 | 2012
28139 | Replace Link | 2012-10-13 13:05 | 2012-10-13 | 2012-10-13 23:22 | Calculated | 1297 | 1297 - Fused Link 1297 |  | 117SEG1297-1296 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 617 | 72 | 24596 | 44432 | 1.8065 | 0.0029273 | 555.5 | 342808 | 2012/2013 | October-2012 | 10 | 2012
28125 | Trees Through Lines | 2012-10-13 13:10 | 2012-10-13 | 2012-10-13 20:44 | Calculated | 120 | 120 - Circuit Breaker 120 |  | No Segment | 203-01 Te Waireka Road | Urban A | No Feeder |  |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 449 | 448 | 24596 | 64661 | 2.6289 | 0.018214 | 5256.4615 | 687474 | 2012/2013 | October-2012 | 10 | 2012
28128 | Lines Down | 2012-10-13 13:34 | 2012-10-13 | 2012-10-13 20:46 | Calculated | 5144 | 5144 - Circuit Breaker with Bypass 5144 |  | 411SEG5144-5769 | National Park 411-01 | Rural D | National Park | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 432 | 360 | 24596 | 71005 | 2.8868 | 0.014637 | 3204.7759 | 626192 | 2012/2013 | October-2012 | 10 | 2012
28134 | Close Recloser | 2012-10-13 13:45 | 2012-10-13 | 2012-10-13 19:33 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG569-564 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 348 | 16 | 24596 | 5570 | 0.22646 | 0.00065051 | 140 | 48743 | 2012/2013 | October-2012 | 10 | 2012
28135 | Replace Link | 2012-10-13 14:14 | 2012-10-13 | 2012-10-13 20:51 | Calculated | 455 | 455 - Fused Link 455 |  | 129SEG455-402 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 397 | 59 | 24596 | 23435 | 0.9528 | 0.0023988 | 860 | 341606 | 2012/2013 | October-2012 | 10 | 2012
28129 | Replace H/V Fuses | 2012-10-13 14:36 | 2012-10-13 | 2012-10-13 17:54 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 197 | 26 | 24596 | 5125 | 0.20837 | 0.0010571 | 305 | 60125 | 2012/2013 | October-2012 | 10 | 2012
28133 | Close Sectionaliser | 2012-10-13 14:37 | 2012-10-13 | 2012-10-13 19:09 | Calculated | 5758 | 5758 - Sectionaliser 5758 |  | 413SEG5996-5758 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 272 | 123 | 24596 | 33470 | 1.3608 | 0.0050008 | 921 | 250619 | 2012/2013 | October-2012 | 10 | 2012
28136 | Replace H/V Link | 2012-10-13 14:46 | 2012-10-13 | 2012-10-13 21:22 | Calculated | 1417 | 1417 - Fused Link 1417 |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 395 | 5 | 24596 | 1976 | 0.08034 | 0.00020329 | 65 | 25693 | 2012/2013 | October-2012 | 10 | 2012
28131 | Close H/V Link | 2012-10-13 15:13 | 2012-10-13 | 2012-10-13 18:09 | Calculated | 5580 | 5580 - Fused Link 5580 |  | 426SEG5526-5359 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 10 | 24596 | 1761 | 0.0716 | 0.00040657 | 90 | 15851 | 2012/2013 | October-2012 | 10 | 2012
28140 | Replace H/V Fuse | 2012-10-13 15:45 | 2012-10-13 | 2012-10-14 01:23 | Calculated | TF2761 | TF2761 - Transformer Fuse: TF2761 |  | 129SEG477 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 578 | 4 | 24596 | 2312 | 0.094 | 0.00016263 | 30 | 17343 | 2012/2013 | October-2012 | 10 | 2012
28141 | Replace H/V Fuse | 2012-10-13 15:47 | 2012-10-13 | 2012-10-14 02:10 | Calculated | TF1439 | TF1439 - Transformer Fuse: TF1439 |  | 129SEG6621-1407 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 623 | 4 | 24596 | 2492 | 0.10132 | 0.00016263 | 25 | 15580 | 2012/2013 | October-2012 | 10 | 2012
28130 | Close Sectionaliser | 2012-10-13 16:10 | 2012-10-13 | 2012-10-13 17:55 | Calculated | 5489 | 5489 - Sectionaliser with Bypass 5489 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 26 | 24596 | 2733 | 0.11112 | 0.0010571 | 153.3333 | 16117 | 2012/2013 | October-2012 | 10 | 2012
28150 | Replace Jumper | 2012-10-13 18:45 | 2012-10-13 | 2012-10-14 13:11 | Calculated | TF1764 | TF1764 - Transformer Fuse: TF1764 |  | 116SEG717 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1105 | 5 | 24596 | 1341 | 0.05452 | 0.00020329 | 35 | 7299 | 2012/2013 | October-2012 | 10 | 2012
28143 | Replace Link | 2012-10-13 21:46 | 2012-10-13 | 2012-10-14 08:05 | Calculated | 355 | 355 - Fused Link 355 |  | 112SEG355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 619 | 10 | 24596 | 6191 | 0.25171 | 0.00040657 | 105 | 65007 | 2012/2013 | October-2012 | 10 | 2012
28137 | Replace Tx | 2012-10-13 23:02 | 2012-10-13 | 2012-10-14 10:50 | Calculated | TF214 | TF214 - Transformer Fuse: TF214 |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 708 | 4 | 24596 | 2832 | 0.11514 | 0.00016263 | 0 | 0 | 2012/2013 | October-2012 | 10 | 2012
28142 | Close OCB | 2012-10-14 02:08 | 2012-10-14 | 2012-10-14 02:09 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24596 |  | 0 | 0 |  |  | 2012/2013 | October-2012 | 10 | 2012
28151 | Replace Link | 2012-10-14 08:38 | 2012-10-14 | 2012-10-14 13:10 | Calculated | 5580 | 5580 - Fused Link 5580 |  | 426SEG5526-5359 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 272 | 10 | 24596 | 2721 | 0.11063 | 0.00040657 | 90 | 24494 | 2012/2013 | October-2012 | 10 | 2012
28153 | Replace H/V Fuse | 2012-10-14 09:56 | 2012-10-14 | 2012-10-14 20:56 | Calculated | TF517 | TF517 - Transformer Fuse: TF517 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 660 | 1 | 24596 | 660 | 0.02683 | 4.0657e-05 | 13 | 8581 | 2012/2013 | October-2012 | 10 | 2012
28146 | Line Down | 2012-10-14 11:50 | 2012-10-14 | 2012-10-14 13:16 | Calculated | 1627 | 1627 - Recloser with Incoming Link1627 |  | 128SEG1643-1627 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 9 | 24596 | 766 | 0.03114 | 0.00036591 | 80 | 6810 | 2012/2013 | October-2012 | 10 | 2012
28148 | Replace Faulty Tx | 2012-10-14 13:12 | 2012-10-14 | 2012-10-14 15:02 | Calculated | TF1096 | TF1096 - Transformer Fuse: TF1096 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 3 | 24596 | 330 | 0.01342 | 0.00012197 | 30 | 3305 | 2012/2013 | October-2012 | 10 | 2012
28152 | Replace Xarm | 2012-10-14 16:28 | 2012-10-14 | 2012-10-14 17:48 | Calculated | 2095 | 2095 - Air Break Switch 2095 |  | 128SEG2095-1635 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAU | Cross-Arm Burnt | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 154 | 24596 | 12350 | 0.50211 | 0.0062612 | 1033.5 | 82886 | 2012/2013 | October-2012 | 10 | 2012
28155 | Replace H/V Fuse | 2012-10-15 09:24 | 2012-10-15 | 2012-10-15 11:01 | Calculated | TF310 | TF310 - Transformer Fuse: TF310 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 4 | 24596 | 384 | 0.01561 | 0.00016263 | 30 | 2886 | 2012/2013 | October-2012 | 10 | 2012
28154 | Pole Change & Repair Conductor | 2012-10-15 09:42 | 2012-10-15 | 2012-10-15 15:39 | Calculated | TF12N05 | TF12N05 - Transformer Fuse: TF12N05 |  | 609SEG5159-6761 | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 357 | 7 | 24596 | 2500 | 0.10164 | 0.0002846 | 300 | 107155 | 2012/2013 | October-2012 | 10 | 2012
28156 | Lower Taps | 2012-10-15 15:31 | 2012-10-15 | 2012-10-15 16:11 | Calculated | TF1594 | TF1594 - Transformer Fuse: TF1594 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 40 | 2 | 24596 | 80 | 0.00325 | 8.1314e-05 | 10 | 401 | 2012/2013 | October-2012 | 10 | 2012
28157 | Replace Poles | 2012-10-16 08:36 | 2012-10-16 | 2012-10-16 15:55 | Calculated | TF640 | TF640 - Transformer Fuse: TF640 |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 225 | 145 | 24596 | 13232 | 0.53797 | 0.0058953 | 972.1014 | 127061 | 2012/2013 | October-2012 | 10 | 2012
28158 | Change Poles & Xarms | 2012-10-17 08:31 | 2012-10-17 | 2012-10-17 16:08 | Calculated | 1716 | 1716 - Recloser with Bypass1716 |  | 115SEG1716-1719 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 412 | 76 | 24596 | 9128 | 0.37112 | 0.0030899 | 543 | 53326 | 2012/2013 | October-2012 | 10 | 2012
28159 | Pole Changes | 2012-10-17 08:55 | 2012-10-17 | 2012-10-17 15:51 | Calculated | 5460 | 5460 - Fused Link 5460 |  | 403SEG5460-5812 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 0 | 0 | 24596 |  | 0 | 0 |  |  | 2012/2013 | October-2012 | 10 | 2012
28161 | Replace H/V Link | 2012-10-17 16:42 | 2012-10-17 | 2012-10-17 17:26 | Calculated | 677 | 677 - Fused Link 677 |  | 107SEG677 | Oparure 107-01 | Urban A | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 6 | 24596 | 265 | 0.01077 | 0.00024394 | 160 | 7066 | 2012/2013 | October-2012 | 10 | 2012
28162 | Pole Changes | 2012-10-18 08:41 | 2012-10-18 | 2012-10-18 15:42 | Calculated | 5460 | 5460 - Fused Link 5460 |  | 403SEG5460-5812 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 0 | 0 | 24596 |  | 0 | 0 |  |  | 2012/2013 | October-2012 | 10 | 2012
28163 | Replace Poles & Xarms | 2012-10-18 09:04 | 2012-10-18 | 2012-10-18 14:17 | Calculated | 1714 | 1714 - Fused Link 1714 |  | 115SEG1714 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 312 | 13 | 24596 | 4058 | 0.16499 | 0.00052854 | 95 | 29657 | 2012/2013 | October-2012 | 10 | 2012
28164 | Replace H/V Link | 2012-10-18 14:06 | 2012-10-18 | 2012-10-18 15:15 | Calculated | 1113 | 1113 - Fused Link 1113 |  | 114SEG1116-1113 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQW | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 13 | 24596 | 898 | 0.03651 | 0.00052854 | 80 | 5529 | 2012/2013 | October-2012 | 10 | 2012
28166 | Close CB | 2012-10-18 17:09 | 2012-10-18 | 2012-10-18 17:13 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24596 |  | 0 | 0 |  |  | 2012/2013 | October-2012 | 10 | 2012
28168 | Broken Xarm | 2012-10-18 17:25 | 2012-10-18 | 2012-10-18 21:40 | Calculated | 5507 | 5507 - Sectionaliser with Bypass & Links 5507 |  | 413SEG5507 | Ohura 413-03 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 255 | 20 | 24596 | 3269 | 0.13291 | 0.00081314 | 153 | 25551 | 2012/2013 | October-2012 | 10 | 2012
28169 | Tree vs Line | 2012-10-18 17:37 | 2012-10-18 | 2012-10-18 18:33 | Calculated | 5245 | 5245 - Solid Link 5245 |  | 417SEG5245-5497 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 108 | 24596 | 5954 | 0.24207 | 0.004391 | 590 | 32528 | 2012/2013 | October-2012 | 10 | 2012
28170 | Close OCB | 2012-10-18 22:43 | 2012-10-18 | 2012-10-18 22:48 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 4 | 24596 | 21 | 0.00085 | 0.00016263 | 450 | 2377 | 2012/2013 | October-2012 | 10 | 2012
28172 | Replace H/V Fuse | 2012-10-19 08:50 | 2012-10-19 | 2012-10-19 09:54 | Calculated | TF2922 | TF2922 - Transformer Fuse: TF2922 |  | 101SEG514 | Caves 101-11 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 2 | 24596 | 128 | 0.0052 | 8.1314e-05 | 10 | 641 | 2012/2013 | October-2012 | 10 | 2012
28175 | Faulty Tx | 2012-10-19 10:51 | 2012-10-19 | 2012-10-19 14:19 | Calculated | TF293 | TF293 - Transformer Fuse: TF293 |  | 101SEG286 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 208 | 2 | 24596 | 416 | 0.01691 | 8.1314e-05 | 15 | 3121 | 2012/2013 | October-2012 | 10 | 2012
28177 | Floating Insulator | 2012-10-19 11:49 | 2012-10-19 | 2012-10-19 16:33 | Calculated | 587 | 587 - Fused Link 587 |  | 109SEG587-2218 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 13 | 24596 | 1578 | 0.06416 | 0.00052854 | 100 | 12139 | 2012/2013 | October-2012 | 10 | 2012
28176 | Close OCB | 2012-10-19 12:11 | 2012-10-19 | 2012-10-19 12:37 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24596 |  | 0 | 0 |  |  | 2012/2013 | October-2012 | 10 | 2012
28178 | Close OCB | 2012-10-19 13:23 | 2012-10-19 | 2012-10-19 13:30 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24596 |  | 0 | 0 |  |  | 2012/2013 | October-2012 | 10 | 2012
28179 | Replace Link | 2012-10-19 15:12 | 2012-10-19 | 2012-10-19 17:36 | Calculated | 171 | 171 - Fused Link 171 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 7 | 24596 | 1008 | 0.04098 | 0.0002846 | 95 | 13689 | 2012/2013 | October-2012 | 10 | 2012
28180 | Replace Link | 2012-10-20 09:52 | 2012-10-20 | 2012-10-20 11:30 | Calculated | 2041 | 2041 - Fused Link 2041 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 4 | 24596 | 392 | 0.01594 | 0.00016263 | 65 | 6378 | 2012/2013 | October-2012 | 10 | 2012
28182 | Poles Down | 2012-10-21 18:44 | 2012-10-21 | 2012-10-23 16:24 | Calculated | 5367 | 5367 - Sectionaliser with Bypass 5367 |  | 403SEG5367-5875 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFPL | Fault on Private Line - Affecting Network | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 2740 | 20 | 24596 | 15473 | 0.62909 | 0.00081314 | 110 | 120940 | 2012/2013 | October-2012 | 10 | 2012
28183 | Install New L/A | 2012-10-23 11:08 | 2012-10-23 | 2012-10-23 13:03 | Calculated | TF11S09 | TF11S09 - Transformer Fuse: TF11S09 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 115 | 2 | 24596 | 230 | 0.00935 | 8.1314e-05 | 100 | 11515 | 2012/2013 | October-2012 | 10 | 2012
28184 | L/V Fault in Pillar 12098 | 2012-10-23 15:00 | 2012-10-23 | 2012-10-23 17:05 | Calculated | TF1336 | TF1336 - Transformer Fuse: TF1336 |  | 104SEG517-242 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 37 | 24596 | 4630 | 0.18824 | 0.0015043 | 200 | 25029 | 2012/2013 | October-2012 | 10 | 2012
28187 | Jumper off Tx 938 | 2012-10-24 12:16 | 2012-10-24 | 2012-10-24 12:37 | Calculated | 473 | 473 - Load Break Switch 473 |  | 123SEG473 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 22 | 24596 | 465 | 0.01891 | 0.00089445 | 340 | 7190 | 2012/2013 | October-2012 | 10 | 2012
28186 | Replace Link | 2012-10-24 21:40 | 2012-10-24 | 2012-10-24 22:44 | Calculated | 372 | 372 - Fused Link 372 |  | 122SEG372 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 22 | 24596 | 1391 | 0.05655 | 0.00089445 | 148 | 9363 | 2012/2013 | October-2012 | 10 | 2012
28192 | Repair Stay | 2012-10-26 10:17 | 2012-10-26 | 2012-10-26 10:57 | Calculated | TF2872 | TF2872 - Transformer Fuse: TF2872 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 39 | 1 | 24596 | 39 | 0.00159 | 4.0657e-05 | 15 | 586 | 2012/2013 | October-2012 | 10 | 2012
28193 | House vs Line | 2012-10-26 15:41 | 2012-10-26 | 2012-10-26 16:26 | Calculated | TF1286 | TF1286 - Transformer Fuse: TF1286 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 2 | 24596 | 90 | 0.00366 | 8.1314e-05 | 25 | 1129 | 2012/2013 | October-2012 | 10 | 2012
28194 | Close CB | 2012-10-27 07:23 | 2012-10-27 | 2012-10-27 07:25 | Calculated | TPHangatikiCB222 | TPHangatikiCB222 - 33kV Minimum Oil Circuit Breaker TP222 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24596 |  | 0 | 0 |  |  | 2012/2013 | October-2012 | 10 | 2012
28195 | Close Sect | 2012-10-27 10:01 | 2012-10-27 | 2012-10-27 11:07 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 66 | 12 | 24596 | 793 | 0.03224 | 0.00048788 | 100 | 6616 | 2012/2013 | October-2012 | 10 | 2012
28196 | Floating Insulator | 2012-10-27 10:23 | 2012-10-27 | 2012-10-27 11:32 | Calculated | 757 | 757 - Recloser Switch 757 |  | 107SEG243-113 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 99 | 24596 | 5119 | 0.20812 | 0.004025 | 610 | 31547 | 2012/2013 | October-2012 | 10 | 2012
28197 | Replace H/V Fuse | 2012-10-27 13:32 | 2012-10-27 | 2012-10-27 14:21 | Calculated | TF2959 | TF2959 - Transformer Fuse: TF2959 |  | 113SEG1514-1516 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 1 | 24596 | 48 | 0.00195 | 4.0657e-05 | 15 | 722 | 2012/2013 | October-2012 | 10 | 2012
28198 | Feeder Renewals | 2012-10-30 09:02 | 2012-10-30 | 2012-10-30 15:53 | Calculated | 5105 | 5105 - Fused Link 5105 |  | 422SEG5105-5279 | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 411 | 29 | 24596 | 11923 | 0.48475 | 0.0011791 | 216.5 | 89013 | 2012/2013 | October-2012 | 10 | 2012
28199 | Replace H/V Fuse | 2012-10-30 16:01 | 2012-10-30 | 2012-10-30 17:19 | Calculated | TF2533 | TF2533 - Transformer Fuse: TF2533 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 2 | 24596 | 156 | 0.00634 | 8.1314e-05 | 30 | 2343 | 2012/2013 | October-2012 | 10 | 2012
28200 | Replace H/V Fuse | 2012-10-30 17:45 | 2012-10-30 | 2012-10-30 18:52 | Calculated | TF1320 | TF1320 - Transformer Fuse: TF1320 |  | 122SEG702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 5 | 24596 | 330 | 0.01342 | 0.00020329 | 25 | 1654 | 2012/2013 | October-2012 | 10 | 2012
28201 | Replace Stub Pole | 2012-10-31 09:00 | 2012-10-31 | 2012-10-31 12:11 | Calculated | TF20L40 | TF20L40 - Transformer Fuse: TF20L40 |  | 416SEG5677-5681 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 191 | 5 | 24596 | 956 | 0.03887 | 0.00020329 | 25 | 4781 | 2012/2013 | October-2012 | 10 | 2012
28203 | Resag Wire | 2012-10-31 09:03 | 2012-10-31 | 2012-10-31 12:28 | Calculated | 758 | 758 - Air Break Switch 758 |  | 110SEG759-758 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 162 | 46 | 24596 | 7416 | 0.30151 | 0.0018702 | 335 | 54013 | 2012/2013 | October-2012 | 10 | 2012
28202 | Feeder Renewals | 2012-10-31 09:05 | 2012-10-31 | 2012-10-31 14:51 | Calculated | 5105 | 5105 - Fused Link 5105 |  | 422SEG5105-5279 | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 346 | 34 | 24596 | 10340 | 0.42039 | 0.0013823 | 231.5 | 75851 | 2012/2013 | October-2012 | 10 | 2012
28204 | Replace H/V Fuse | 2012-11-01 09:24 | 2012-11-01 | 2012-11-01 09:53 | Calculated | TF21M13 | TF21M13 - Transformer Fuse: TF21M13 |  | 416SEG5684-5747 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 2 | 24593 | 58 | 0.00236 | 8.1324e-05 | 15 | 436 | 2012/2013 | November-2012 | 11 | 2012
28205 | Feeder Renewals | 2012-11-01 09:36 | 2012-11-01 | 2012-11-01 14:18 | Calculated | 445 | 445 - Fused Link 445 |  | 124SEG445-694 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 29 | 24593 | 8183 | 0.33274 | 0.0011792 | 395 | 111462 | 2012/2013 | November-2012 | 11 | 2012
28206 | Truck vs L/V Pole | 2012-11-01 16:36 | 2012-11-01 | 2012-11-01 20:48 | Calculated | TF9U5 | TF9U5 - Transformer Fuse: TF9U5 |  | No Segment | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 252 | 23 | 24593 | 5796 | 0.23568 | 0.00093523 | 200 | 50436 | 2012/2013 | November-2012 | 11 | 2012
28207 | Replace Xarm | 2012-11-02 09:37 | 2012-11-02 | 2012-11-02 10:52 | Calculated | 5569 | 5569 - Fused Link 5569 |  | 413SEG5569-5437 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 75 | 11 | 24593 | 826 | 0.03359 | 0.00044728 | 87.5 | 6574 | 2012/2013 | November-2012 | 11 | 2012
28208 | Replace L/V Pole | 2012-11-02 10:02 | 2012-11-02 | 2012-11-02 12:56 | Calculated | TF228 | TF228 - Transformer Fuse: TF228 |  | 111SEG325 | Maihiihi 111-02 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 174 | 8 | 24593 | 1393 | 0.05664 | 0.0003253 | 50 | 8710 | 2012/2013 | November-2012 | 11 | 2012
28209 | Line Down | 2012-11-02 10:20 | 2012-11-02 | 2012-11-02 14:17 | Calculated | 509 | 509 - Fused Link 509 |  | 126SEG509 | Rural 126-02 | Rural D | Rural | Taharoa Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 236 | 9 | 24593 | 2124 | 0.08637 | 0.00036596 | 68 | 16054 | 2012/2013 | November-2012 | 11 | 2012
28211 | Close CB | 2012-11-03 11:49 | 2012-11-03 | 2012-11-03 11:52 | Calculated | 120 | 120 - Circuit Breaker 120 |  | No Segment | 203-01 Te Waireka Road | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 448 | 24593 | 1396 | 0.05676 | 0.018217 | 5256.4615 | 16382 | 2012/2013 | November-2012 | 11 | 2012
28212 | Replace H/V Fuse | 2012-11-04 14:05 | 2012-11-04 | 2012-11-04 20:37 | Calculated | TF21M13 | TF21M13 - Transformer Fuse: TF21M13 |  | 416SEG6118-5961 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 2 | 24593 | 201 | 0.00817 | 8.1324e-05 | 15 | 1513 | 2012/2013 | November-2012 | 11 | 2012
28213 | Vehicle vs Tx Pole | 2012-11-04 22:06 | 2012-11-04 | 2012-11-05 16:41 | Calculated | TF573 | TF573 - Transformer Fuse: TF573 |  | 102SEG1271-336 | Hangatiki East 102-01 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1115 | 4 | 24593 | 4460 | 0.18135 | 0.00016265 | 30 | 33454 | 2012/2013 | November-2012 | 11 | 2012
28214 | Replace Tx | 2012-11-05 09:10 | 2012-11-05 | 2012-11-05 11:22 | Calculated | TF21M13 | TF21M13 - Transformer Fuse: TF21M13 |  | 416SEG6118-5961 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 2 | 24593 | 264 | 0.01073 | 8.1324e-05 | 15 | 1981 | 2012/2013 | November-2012 | 11 | 2012
28215 | Replace Poles | 2012-11-05 09:33 | 2012-11-05 | 2012-11-05 15:33 | Calculated | 237 | 237 - Sectionaliser 237 |  | 103SEG636-238 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 360 | 3 | 24593 | 1080 | 0.04391 | 0.00012199 | 15 | 5402 | 2012/2013 | November-2012 | 11 | 2012
28216 | Fit T/O Fuses | 2012-11-05 10:03 | 2012-11-05 | 2012-11-05 15:38 | Calculated | 368 | 368 - Fused Link 368 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 335 | 33 | 24593 | 4611 | 0.18749 | 0.0013418 | 355 | 51372 | 2012/2013 | November-2012 | 11 | 2012
28217 | Upgrade Tx | 2012-11-06 09:04 | 2012-11-06 | 2012-11-06 10:04 | Calculated | TF2613 | TF2613 - Transformer Fuse: TF2613 |  | 120SEG410-632 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 1 | 24593 | 60 | 0.00244 | 4.0662e-05 | 25 | 1504 | 2012/2013 | November-2012 | 11 | 2012
28218 | Replace Poles | 2012-11-06 10:31 | 2012-11-06 | 2012-11-06 12:29 | Calculated | 1102 | 1102 - Air Break Switch 1102 |  | 114SEG1108-1102 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 118 | 52 | 24593 | 6148 | 0.24999 | 0.0021144 | 375 | 44337 | 2012/2013 | November-2012 | 11 | 2012
28219 | Replace Poles & Xarms | 2012-11-07 09:40 | 2012-11-07 | 2012-11-07 15:39 | Calculated | 1108 | 1108 - Recloser with Bypass 1108 |  | 114SEG1110-1107 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 344 | 6 | 24593 | 2064 | 0.08393 | 0.00024397 | 20 | 6880 | 2012/2013 | November-2012 | 11 | 2012
28221 | Change Damaged L/V Bushing | 2012-11-07 09:47 | 2012-11-07 | 2012-11-07 14:42 | Calculated | 6565 | 6565 - RTE Switch 6565 |  | 415SEG5699-5695 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 295 | 4 | 24593 | 1181 | 0.04802 | 0.00016265 | 100 | 29525 | 2012/2013 | November-2012 | 11 | 2012
28222 | Replace Rotten Conductor | 2012-11-08 09:32 | 2012-11-08 | 2012-11-08 14:57 | Calculated | 1625 | 1625 - Recloser with Outgoing Link1625 |  | 128SEG1625-1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 325 | 19 | 24593 | 6177 | 0.25117 | 0.00077258 | 122.5 | 39830 | 2012/2013 | November-2012 | 11 | 2012
28223 | Replace Poles & Xarms | 2012-11-08 09:32 | 2012-11-08 | 2012-11-08 15:23 | Calculated | 1102 | 1102 - Air Break Switch 1102 |  | 114SEG1108-1102 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 321 | 58 | 24593 | 1927 | 0.07836 | 0.0023584 | 395 | 6472 | 2012/2013 | November-2012 | 11 | 2012
28224 | Change Tx | 2012-11-08 10:34 | 2012-11-08 | 2012-11-08 11:39 | Calculated | TF2176 | TF2176 - Transformer Fuse: TF2176 |  | 128SEG REG3-2095 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 64 | 13 | 24593 | 833 | 0.03387 | 0.00052861 | 30 | 1923 | 2012/2013 | November-2012 | 11 | 2012
28225 | Tree Felled on Line | 2012-11-08 11:26 | 2012-11-08 | 2012-11-08 15:50 | Calculated | 5490 | 5490 - Recloser with Bypass 5490 |  | 410SEG5490-5438 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 264 | 70 | 24593 | 18490 | 0.75184 | 0.0028463 | 433 | 114376 | 2012/2013 | November-2012 | 11 | 2012
28226 | Close Recloser | 2012-11-08 17:11 | 2012-11-08 | 2012-11-08 17:46 | Calculated | 5440 | 5440 - Recloser with Bypass & Links 5440 |  | 409SEG5439-5440 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 35 | 24 | 24593 | 842 | 0.03424 | 0.00097589 | 227.5 | 7989 | 2012/2013 | November-2012 | 11 | 2012
28227 | Replace H/V Fuse | 2012-11-09 06:31 | 2012-11-09 | 2012-11-09 08:38 | Calculated | TF4001 | TF4001 - Transformer Fuse: TF4001 |  | 426SEG5580-5239 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 127 | 1 | 24593 | 127 | 0.00516 | 4.0662e-05 | 15 | 1906 | 2012/2013 | November-2012 | 11 | 2012
28228 | L/V Maintenance | 2012-11-09 09:01 | 2012-11-09 | 2012-11-09 10:06 | Calculated | TF709 | TF709 - Transformer Fuse: TF709 |  | 118SEG496-1741 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 65 | 48 | 24593 | 3124 | 0.12703 | 0.0019518 | 200 | 13019 | 2012/2013 | November-2012 | 11 | 2012
28229 | Replace Pole | 2012-11-09 09:04 | 2012-11-09 | 2012-11-09 12:20 | Calculated | 5546 | 5546 - Fused Link 5546 |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 196 | 13 | 24593 | 2551 | 0.10373 | 0.00052861 | 75 | 14719 | 2012/2013 | November-2012 | 11 | 2012
28230 | Replace Poles & Xarms | 2012-11-09 09:32 | 2012-11-09 | 2012-11-09 14:59 | Calculated | 1730 | 1730 - Fused Link 1730 |  | 115SEG1730 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 9 | 24593 | 2944 | 0.11971 | 0.00036596 | 67.5 | 22081 | 2012/2013 | November-2012 | 11 | 2012
28231 | Digger vs Line | 2012-11-09 15:07 | 2012-11-09 | 2012-11-09 16:38 | Calculated | 5748 | 5748 - Fused Link 5748 |  | 409SEG5440-5748 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 91 | 14 | 24593 | 1275 | 0.05184 | 0.00056927 | 152.5 | 13895 | 2012/2013 | November-2012 | 11 | 2012
28233 | Replace H/V Fuse | 2012-11-10 13:22 | 2012-11-10 | 2012-11-10 14:47 | Calculated | TF4163 | TF4163 - Transformer Fuse: TF4163 |  | No Segment | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 1 | 24593 | 85 | 0.00346 | 4.0662e-05 | 30 | 2553 | 2012/2013 | November-2012 | 11 | 2012
28234 | Replace H/V Link | 2012-11-11 12:44 | 2012-11-11 | 2012-11-11 13:39 | Calculated | 5488 | 5488 - Fused Link 5488 |  | 405SEG5488 | Hirangi 405-01 | Rural B | Hirangi | Awamate Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 55 | 1 | 24593 | 55 | 0.00224 | 4.0662e-05 | 10 | 551 | 2012/2013 | November-2012 | 11 | 2012
28235 | Close CB | 2012-11-11 16:35 | 2012-11-11 | 2012-11-11 16:43 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 110 | 24593 | 892 | 0.03627 | 0.0044728 | 3280.8571 | 26629 | 2012/2013 | November-2012 | 11 | 2012
28236 | Magpie - Line Down | 2012-11-11 16:57 | 2012-11-11 | 2012-11-11 19:11 | Calculated | 5880 | 5880 - Circuit Breaker Hakiaha 5880 |  | No Segment | 508-01 Borough | Rural B | No Feeder |  |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 298 | 24593 | 8954 | 0.36409 | 0.012117 | 3763.3768 | 168460 | 2012/2013 | November-2012 | 11 | 2012
28237 | Broken Insulator | 2012-11-11 18:48 | 2012-11-11 | 2012-11-12 11:50 | Calculated | 5490 | 5490 - Recloser with Bypass 5490 |  | 410SEG5490-5438 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1003 | 70 | 24593 | 70185 | 2.8539 | 0.0028463 | 433 | 434147 | 2012/2013 | November-2012 | 11 | 2012
28238 | Install New Tx | 2012-11-12 09:33 | 2012-11-12 | 2012-11-12 12:38 | Calculated | 494 | 494 - Fused Link 494 |  | 119SEG494 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 185 | 1 | 24593 | 185 | 0.00752 | 4.0662e-05 | 30 | 5556 | 2012/2013 | November-2012 | 11 | 2012
28239 | Replace Poles | 2012-11-12 09:57 | 2012-11-12 | 2012-11-12 15:13 | Calculated | 635 | 635 - Air Break Switch 635 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 275 | 29 | 24593 | 7950 | 0.32326 | 0.0011792 | 330 | 90469 | 2012/2013 | November-2012 | 11 | 2012
28240 | Replace Faulty Tx | 2012-11-12 11:30 | 2012-11-12 | 2012-11-12 14:23 | Calculated | TF2114 | TF2114 - Transformer Fuse: TF2114 |  | 114SEG1107-1116 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 173 | 1 | 24593 | 173 | 0.00703 | 4.0662e-05 | 3 | 519 | 2012/2013 | November-2012 | 11 | 2012
28241 | Close Sect | 2012-11-13 05:57 | 2012-11-13 | 2012-11-13 07:50 | Calculated | 5446 | 5446 - Sectionaliser with Bypass & Links 5446 |  | 402SEG5343-5446 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 113 | 39 | 24593 | 4413 | 0.17944 | 0.0015858 | 277.5 | 31403 | 2012/2013 | November-2012 | 11 | 2012
28243 | Replace Pole & Xarms | 2012-11-13 08:56 | 2012-11-13 | 2012-11-13 15:19 | Calculated | 787 | 787 - Load Break Switch 787 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 353 | 13 | 24593 | 4580 | 0.18623 | 0.00052861 | 115 | 40518 | 2012/2013 | November-2012 | 11 | 2012
28242 | L/V Maintenance | 2012-11-13 09:14 | 2012-11-13 | 2012-11-13 15:15 | Calculated | TF547 | TF547 - Transformer Fuse: TF547 |  | 125SEG281-298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 361 | 19 | 24593 | 6860 | 0.27894 | 0.00077258 | 300 | 108329 | 2012/2013 | November-2012 | 11 | 2012
28244 | Replace Poles & Xarms | 2012-11-13 09:38 | 2012-11-13 | 2012-11-13 15:16 | Calculated | 5139 | 5139 - Fused Link 5139 |  | 410SEG5543-5161 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 337 | 78 | 24593 | 26296 | 1.0693 | 0.0031716 | 440 | 148338 | 2012/2013 | November-2012 | 11 | 2012
28245 | Repair Broken Earth Mat | 2012-11-13 09:52 | 2012-11-13 | 2012-11-13 11:36 | Calculated | TF1178 | TF1178 - Transformer Fuse: TF1178 |  | 109SEG341-587 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 2 | 24593 | 208 | 0.00846 | 8.1324e-05 | 25 | 2604 | 2012/2013 | November-2012 | 11 | 2012
28246 | Replace H/V Fuse | 2012-11-13 11:22 | 2012-11-13 | 2012-11-13 14:24 | Calculated | TF4Q12 | TF4Q12 - Transformer Fuse: TF4Q12 |  | 426SEG5333-5532 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 182 | 1 | 24593 | 182 | 0.0074 | 4.0662e-05 | 7.5 | 1365 | 2012/2013 | November-2012 | 11 | 2012
28247 | Jumper Off | 2012-11-13 21:00 | 2012-11-13 | 2012-11-13 21:54 | Calculated | TF1139 | TF1139 - Transformer Fuse: TF1139 |  | 129SEG477 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 3 | 24593 | 162 | 0.00659 | 0.00012199 | 15 | 811 | 2012/2013 | November-2012 | 11 | 2012
28248 | Replace Pole | 2012-11-14 09:05 | 2012-11-14 | 2012-11-14 13:21 | Calculated | TF2585 | TF2585 - Transformer Fuse: TF2585 |  | 103SEG107-REG7 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 255 | 1 | 24593 | 255 | 0.01037 | 4.0662e-05 | 10 | 2551 | 2012/2013 | November-2012 | 11 | 2012
28249 | Replace Poles & Xarms | 2012-11-14 09:26 | 2012-11-14 | 2012-11-14 16:36 | Calculated | 652 | 652 - Load Break Switch 652 |  | 119SEG653-652 | Pureora 119-03 RETIRED | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 419 | 11 | 24593 | 4600 | 0.18705 | 0.00044728 | 85 | 35551 | 2012/2013 | November-2012 | 11 | 2012
28250 | Replace Sectionaliser | 2012-11-14 10:09 | 2012-11-14 | 2012-11-14 11:59 | Calculated | 5274 | 5274 - Fused Link 5274 |  | 422SEG5274-5278 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 110 | 45 | 24593 | 4962 | 0.20176 | 0.0018298 | 306 | 33746 | 2012/2013 | November-2012 | 11 | 2012
28251 | Replace H/V Fuse | 2012-11-14 11:25 | 2012-11-14 | 2012-11-14 13:15 | Calculated | 5856 | 5856 - Earth Working Link 5856 |  | 410SEG5856 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 110 | 1 | 24593 | 110 | 0.00447 | 4.0662e-05 | 15 | 1651 | 2012/2013 | November-2012 | 11 | 2012
28252 | Replace H/V Fuse | 2012-11-14 19:08 | 2012-11-14 | 2012-11-14 21:58 | Calculated | TF12H02 | TF12H02 - Transformer Fuse: TF12H02 |  | 410SEG5611-5400 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 170 | 6 | 24593 | 1020 | 0.04148 | 0.00024397 | 25 | 4252 | 2012/2013 | November-2012 | 11 | 2012
28253 | Close Recloser | 2012-11-14 20:05 | 2012-11-14 | 2012-11-14 20:09 | Calculated | 5494 | 5494 - Recloser with Bypass 5494 |  | 410SEG5494-5493 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 4 | 42 | 24593 | 173 | 0.00703 | 0.0017078 | 268.3333 | 1109 | 2012/2013 | November-2012 | 11 | 2012
28255 | Replace Poles & Xarms | 2012-11-15 08:47 | 2012-11-15 | 2012-11-15 15:22 | Calculated | 787 | 787 - Load Break Switch 787 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 368 | 13 | 24593 | 4773 | 0.19408 | 0.00052861 | 145 | 53244 | 2012/2013 | November-2012 | 11 | 2012
28256 | Replace Poles | 2012-11-15 09:54 | 2012-11-15 | 2012-11-15 16:47 | Calculated | TF13L3 | TF13L3 - Transformer Fuse: TF13L3 |  | 410SEG5829-5545 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 412 | 15 | 24593 | 6181 | 0.25133 | 0.00060993 | 50 | 20605 | 2012/2013 | November-2012 | 11 | 2012
28257 | Replace Xarms etc | 2012-11-15 11:03 | 2012-11-15 | 2012-11-15 14:04 | Calculated | 5550 | 5550 - Solid Link 5550 |  | 408SEG5550-5102 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 181 | 18 | 24593 | 3260 | 0.13256 | 0.00073192 | 135 | 24452 | 2012/2013 | November-2012 | 11 | 2012
28258 | Replace H/V Fuse | 2012-11-15 21:32 | 2012-11-15 | 2012-11-15 23:57 | Calculated | TF2822 | TF2822 - Transformer Fuse: TF2822 |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 1 | 24593 | 145 | 0.0059 | 4.0662e-05 | 15 | 2176 | 2012/2013 | November-2012 | 11 | 2012
28347 | SWER Backfeed Recloser 705 Replace Poles & X/Arms | 2012-11-16 08:32 | 2012-11-16 | 2012-11-16 16:05 | Calculated | 705 | 705 - Recloser with Bypass & Links 705 |  | 103SEG705-1736 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 402 | 88 | 24593 | 26400 | 1.0735 | 0.0035783 | 617.5 | 187972 | 2012/2013 | November-2012 | 11 | 2012
28309 | Tree felled through line Link 5534 | 2012-11-16 16:27 | 2012-11-16 | 2012-11-17 02:41 | Calculated | 5534 | 5534 - Sectionaliser 5534 |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 614 | 51 | 24593 | 11223 | 0.45635 | 0.0020738 | 375.5 | 83675 | 2012/2013 | November-2012 | 11 | 2012
28313 | Refer 2012/403 link 808 Upgrade 11KV Metering Unit | 2012-11-17 08:09 | 2012-11-17 | 2012-11-17 11:27 | Calculated | 808 | 808 - Solid Link 808 |  | 102SEG521-505 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 198 | 1 | 24593 | 198 | 0.00805 | 4.0662e-05 | 1000 | 198000 | 2012/2013 | November-2012 | 11 | 2012
28314 | Jumper Off at T1619 | 2012-11-17 13:39 | 2012-11-17 | 2012-11-17 14:34 | Calculated | 569 | 569 - Air Break Switch 569 |  | 125SEG569-564 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 16 | 24593 | 880 | 0.03578 | 0.00065059 | 140 | 7700 | 2012/2013 | November-2012 | 11 | 2012
28315 | Unknown T1471 | 2012-11-17 14:22 | 2012-11-17 | 2012-11-17 16:40 | Calculated | TF1471 | TF1471 - Transformer Fuse: TF1471 |  | 128SEG1635-1626 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 1 | 24593 | 138 | 0.00561 | 4.0662e-05 | 15 | 2070 | 2012/2013 | November-2012 | 11 | 2012
28316 | Lightning | 2012-11-18 04:21 | 2012-11-18 | 2012-11-18 05:51 | Calculated | TF2974 | TF2974 - Transformer Fuse: TF2974 |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 1 | 24593 | 90 | 0.00366 | 4.0662e-05 | 100 | 9000 | 2012/2013 | November-2012 | 11 | 2012
28319 | L/V Fault T1449 | 2012-11-19 08:12 | 2012-11-19 | 2012-11-19 09:55 | Calculated | TF1449 | TF1449 - Transformer Fuse: TF1449 |  | 119SEG456 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 2 | 24593 | 206 | 0.00838 | 8.1324e-05 | 30 | 3090 | 2012/2013 | November-2012 | 11 | 2012
28320 | Refer 2012/406 Link 664 Reconfigure Main Line & Remove Pole 901/53/3/6 | 2012-11-19 11:02 | 2012-11-19 | 2012-11-19 13:49 | Calculated | 5664 | 5664 - Fused Link 5664 |  | 408SEG5664-5661 | Manunui 408-03 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 167 | 14 | 24593 | 2338 | 0.09507 | 0.00056927 | 86.3889 | 14426 | 2012/2013 | November-2012 | 11 | 2012
28321 | Unknown T2696 | 2012-11-19 17:00 | 2012-11-19 | 2012-11-19 19:05 | Calculated | TF2696 | TF2696 - Transformer Fuse: TF2696 |  | 124SEG433 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 1 | 24593 | 125 | 0.00508 | 4.0662e-05 | 30 | 3750 | 2012/2013 | November-2012 | 11 | 2012
28322 | Bird TF8K4 | 2012-11-19 18:00 | 2012-11-19 | 2012-11-19 18:35 | Calculated | TF8K4 | TF8K4 - Transformer Fuse: TF8K4 |  | No Segment | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 35 | 4 | 24593 | 140 | 0.00569 | 0.00016265 | 15 | 525 | 2012/2013 | November-2012 | 11 | 2012
28324 | Refer 201/408 Link 587 Replace Red Tagged Pole 1091423 | 2012-11-20 09:30 | 2012-11-20 | 2012-11-20 15:07 | Calculated | 587 | 587 - Fused Link 587 |  | 109SEG587-2218 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 337 | 13 | 24593 | 4381 | 0.17814 | 0.00052861 | 100 | 33699 | 2012/2013 | November-2012 | 11 | 2012
28329 | Refer 2012/407 Rec 107 - RG7 Changing Poles - Feedr Renewal Project | 2012-11-20 09:37 | 2012-11-20 | 2012-11-20 15:19 | Calculated | 107W | 107W - Bypass Switch 107W |  | 103SEG107-REG7 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 29 | 24593 | 9918 | 0.40329 | 0.0011792 | 205 | 70110 | 2012/2013 | November-2012 | 11 | 2012
28325 | Digger vs L/V T 730 | 2012-11-20 14:01 | 2012-11-20 | 2012-11-20 14:50 | Calculated | TF730 | TF730 - Transformer Fuse: TF730 |  | 120SEG419 | Whakamaru 120-05 (was part 124-01) | Rural D | Whakamaru | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 5 | 24593 | 245 | 0.00996 | 0.00020331 | 30 | 1470 | 2012/2013 | November-2012 | 11 | 2012
28326 | Oveloadded T2696 Upgrade fusing TX2696 overloaded | 2012-11-20 16:32 | 2012-11-20 | 2012-11-20 20:43 | Calculated | TF2696 | TF2696 - Transformer Fuse: TF2696 |  | 124SEG433 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 251 | 1 | 24593 | 251 | 0.01021 | 4.0662e-05 | 30 | 7530 | 2012/2013 | November-2012 | 11 | 2012
28337 | Refer 2012/409 Changing Poles - Feeder renewal Project | 2012-11-21 09:20 | 2012-11-21 | 2012-11-21 15:24 | Calculated | 236 | 236 - Air Break Switch 236 |  | 103SEG REG7-236 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 364 | 9 | 24593 | 3276 | 0.13321 | 0.00036596 | 50 | 18200 | 2012/2013 | November-2012 | 11 | 2012
28340 | Private Line L/V Maintenance TF624 | 2012-11-21 10:58 | 2012-11-21 | 2012-11-21 12:58 | Calculated | TF624 | TF624 - Transformer Fuse: TF624 |  | 101SEG291-752 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 120 | 5 | 24593 | 600 | 0.0244 | 0.00020331 | 30 | 3600 | 2012/2013 | November-2012 | 11 | 2012
28341 | Broken DDO at TX1695 | 2012-11-21 12:17 | 2012-11-21 | 2012-11-21 14:00 | Calculated | 1516 | 1516 - Air Break Switch 1516 |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 137 | 24593 | 14111 | 0.57378 | 0.0055707 | 885.5 | 91206 | 2012/2013 | November-2012 | 11 | 2012
28343 | Building Fire T660 | 2012-11-21 17:50 | 2012-11-21 | 2012-11-21 18:25 | Calculated | TF660 | TF660 - Transformer Fuse: TF660 |  | 101SEG746-1656 | Caves 101-08 | Urban A | Caves | Hangatiki Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFIH | House Fire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 12 | 24593 | 420 | 0.01708 | 0.00048794 | 100 | 3499 | 2012/2013 | November-2012 | 11 | 2012
28346 | Refer 2012/410 ABS 541 - LInks & Bypass RG 23 Replace Poles & X/arms | 2012-11-22 09:03 | 2012-11-22 | 2012-11-22 15:26 | Calculated | 787 | 787 - Load Break Switch 787 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 383 | 13 | 24593 | 4979 | 0.20246 | 0.00052861 | 115 | 44045 | 2012/2013 | November-2012 | 11 | 2012
28344 | Refer 2012/411 ABS 340 - 191 Changing Poles | 2012-11-22 09:33 | 2012-11-22 | 2012-11-22 15:03 | Calculated | 340 | 340 - Air Break Switch 340 |  | 102SEG340-191 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 330 | 9 | 24593 | 2970 | 0.12077 | 0.00036596 | 75 | 24749 | 2012/2013 | November-2012 | 11 | 2012
28374 | Unknown TF12P05 | 2012-11-23 06:26 | 2012-11-23 | 2012-11-23 07:34 | Calculated | TF12P05 | TF12P05 - Transformer Fuse: TF12P05 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 68 | 1 | 24593 | 68 | 0.00277 | 4.0662e-05 | 15 | 1020 | 2012/2013 | November-2012 | 11 | 2012
28375 | SWER Backfeed Link 1719 Changing Poles & X/arms | 2012-11-23 08:34 | 2012-11-23 | 2012-11-23 16:11 | Calculated | 1716 | 1716 - Recloser with Bypass1716 |  | 115SEG1716-1719 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 423 | 54 | 24593 | 4339 | 0.17643 | 0.0021957 | 415.5 | 23254 | 2012/2013 | November-2012 | 11 | 2012
28376 | L/V Line Down TX1320 | 2012-11-23 09:24 | 2012-11-23 | 2012-11-23 10:59 | Calculated | TF1320 | TF1320 - Transformer Fuse: TF1320 |  | 122SEG702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 5 | 24593 | 475 | 0.01931 | 0.00020331 | 25 | 2375 | 2012/2013 | November-2012 | 11 | 2012
28378 | L/V Maintenance Remove L/V Back Feed - TX 706 | 2012-11-23 09:44 | 2012-11-23 | 2012-11-23 14:47 | Calculated | TF706 | TF706 - Transformer Fuse: TF706 |  | 118SEG664-666 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 303 | 32 | 24593 | 9696 | 0.39426 | 0.0013012 | 150 | 45450 | 2012/2013 | November-2012 | 11 | 2012
28379 | Upgrade Earthing TX10L01 | 2012-11-23 10:33 | 2012-11-23 | 2012-11-23 12:57 | Calculated | 10L01 | 10L01 - 1 Phase : 30.00 kVA : POLEMNT |  | 409SEG5319-5114 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 144 | 2 | 24593 | 288 | 0.01171 | 8.1324e-05 | 30 | 4320 | 2012/2013 | November-2012 | 11 | 2012
28380 | Refer 2012/413 Connect New 3 Phase Ext For Dairy @ TX09J03 | 2012-11-23 12:33 | 2012-11-23 | 2012-11-23 17:02 | Calculated | 6619 | 6619 - Air Break Switch 6619 |  | 409SEG5757-5761 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 242 | 18 | 24593 | 1052 | 0.04278 | 0.00073192 | 158 | 5196 | 2012/2013 | November-2012 | 11 | 2012
28381 | Magpies x 2 Replace H/V Fuse TF2516 | 2012-11-23 15:00 | 2012-11-23 | 2012-11-23 16:18 | Calculated | TF2516 | TF2516 - Transformer Fuse: TF2516 |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 2 | 24593 | 156 | 0.00634 | 8.1324e-05 | 75 | 5850 | 2012/2013 | November-2012 | 11 | 2012
28363 | Faulty L/A Replace Fuse TF3322 | 2012-11-24 00:27 | 2012-11-24 | 2012-11-24 16:57 | Calculated | TF3322 | TF3322 - Transformer Fuse 3322 |  | 103SEG1335-1301 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 990 | 1 | 24593 | 990 | 0.04026 | 4.0662e-05 | 15 | 14850 | 2012/2013 | November-2012 | 11 | 2012
28364 | Unknown TF12S4 | 2012-11-24 13:45 | 2012-11-24 | 2012-11-24 14:49 | Calculated | TF12S4 | TF12S4 - Transformer Fuse: TF12S4 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 1 | 24593 | 64 | 0.0026 | 4.0662e-05 | 7.5 | 480 | 2012/2013 | November-2012 | 11 | 2012
28385 | Refer 2012/414 Isolation for Transpower Outage @ Ohakune | 2012-11-25 07:25 | 2012-11-25 | 2012-11-25 17:25 | Calculated | 5003 | 5003 - Circuit Breaker 5003 |  | No Segment | 517-01 Transpower Ohakune | Urban A | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 4 | 1961 | 24593 | 5234 | 0.21282 | 0.079738 | 14693.8181 | 38859 | 2012/2013 | November-2012 | 11 | 2012
28382 | Refer 2012/416 Links 5139 Changing Poles & X/arms - Raurimy feeder Renewal Project | 2012-11-26 09:09 | 2012-11-26 | 2012-11-26 16:11 | Calculated | 5139 | 5139 - Fused Link 5139 |  | 410SEG5543-5161 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 422 | 78 | 24593 | 32916 | 1.3384 | 0.0031716 | 440 | 185679 | 2012/2013 | November-2012 | 11 | 2012
28383 | Refer 2012/147 Replace Poles & X/arms | 2012-11-26 09:48 | 2012-11-26 | 2012-11-26 14:17 | Calculated | 1715 | 1715 - Fused Link 1715 |  | 115SEG1715 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 10 | 24593 | 2690 | 0.10938 | 0.00040662 | 57.5 | 15467 | 2012/2013 | November-2012 | 11 | 2012
28384 | Unknown TF 197 | 2012-11-26 13:40 | 2012-11-26 | 2012-11-26 15:17 | Calculated | TF197 | TF197 - Transformer Fuse: TF197 |  | 112SEG326-288 | Otorohanga 112-06 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 3 | 24593 | 291 | 0.01183 | 0.00012199 | 15 | 1455 | 2012/2013 | November-2012 | 11 | 2012
28387 | Possum - Line down | 2012-11-27 05:55 | 2012-11-27 | 2012-11-27 13:52 | Calculated | 1549 | 1549 - Recloser 1549 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 477 | 29 | 24593 | 13833 | 0.56248 | 0.0011792 | 207.5 | 98977 | 2012/2013 | November-2012 | 11 | 2012
28388 | Unknown | 2012-11-27 07:20 | 2012-11-27 | 2012-11-27 10:25 | Calculated | TF08C01 | TF08C01 - Transformer Fuse: TF8C1 |  | 413SEG5295-5454 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 2 | 24593 | 370 | 0.01504 | 8.1324e-05 | 15 | 2775 | 2012/2013 | November-2012 | 11 | 2012
28389 | Refer 2012/149 Remove ABS, Replace Pole & Install Links 1313 | 2012-11-27 09:14 | 2012-11-27 | 2012-11-27 13:03 | Calculated | 1313 | 1313 - Air Break Switch 1313 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 229 | 27 | 24593 | 6183 | 0.25141 | 0.0010979 | 250 | 57249 | 2012/2013 | November-2012 | 11 | 2012
28390 | Refer 2012/420 Resag 11 kV Line | 2012-11-27 10:03 | 2012-11-27 | 2012-11-27 13:39 | Calculated | 369 | 369 - Fused Link 369 |  | 122SEG369-678 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 216 | 15 | 24593 | 3240 | 0.13174 | 0.00060993 | 195 | 42120 | 2012/2013 | November-2012 | 11 | 2012
28391 | Scheduled Maintenance Link 467 | 2012-11-27 11:31 | 2012-11-27 | 2012-11-27 13:56 | Calculated | 467 | 467 - Fused Link 467 |  | 123SEG467 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 145 | 10 | 24593 | 1450 | 0.05896 | 0.00040662 | 60 | 8699 | 2012/2013 | November-2012 | 11 | 2012
28392 | Broken Stay | 2012-11-27 11:46 | 2012-11-27 | 2012-11-27 12:00 | Calculated | TF192 | TF192 - Transformer Fuse: TF192 |  | 109SEG341-587 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:OIWAWD | Broken Stay Wire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 2 | 24593 | 28 | 0.00114 | 8.1324e-05 | 25 | 350 | 2012/2013 | November-2012 | 11 | 2012
28393 | Fuse pulled Apart | 2012-11-27 19:30 | 2012-11-27 | 2012-11-27 19:59 | Calculated | TF20L62 | TF20L62 - Transformer Fuse: TF20L62 |  | 414SEG6644-5643 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 11 | 24593 | 319 | 0.01297 | 0.00044728 | 100 | 2899 | 2012/2013 | November-2012 | 11 | 2012
28394 | Bolt Out Of X/Arm | 2012-11-28 02:17 | 2012-11-28 | 2012-11-28 05:23 | Calculated | 5032 | 5032 - Circuit Breaker Incomer 5032 |  | No Segment | Tokaanu 420-01 | Rural C | Tokaanu | Tokaanu Village Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 85 | 24593 | 3282 | 0.13345 | 0.0034563 | 750 | 26399 | 2012/2013 | November-2012 | 11 | 2012
28396 | Refer 2012/421 Remove O/H From Poles 60 - 62 & Connect New U/G Cable | 2012-11-28 09:25 | 2012-11-28 | 2012-11-28 14:52 | Calculated | 470 | 470 - Air Break Switch 470 |  | 123SEG470-2135 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 301 | 4 | 24593 | 1204 | 0.04896 | 0.00016265 | 40 | 12040 | 2012/2013 | November-2012 | 11 | 2012
28398 | Refer 2012/422 Remove O/H From Poles 65 - 66 & Connect New U/G Cable | 2012-11-29 09:36 | 2012-11-29 | 2012-11-29 14:10 | Calculated | 787 | 787 - Load Break Switch 787 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 274 | 4 | 24593 | 1096 | 0.04457 | 0.00016265 | 40 | 10960 | 2012/2013 | November-2012 | 11 | 2012
28399 | Private Line L/V Maintenance | 2012-11-29 10:26 | 2012-11-29 | 2012-11-29 12:25 | Calculated | TF2963 | TF2963 - Transformer Fuse: TF2963 |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 1 | 24593 | 119 | 0.00484 | 4.0662e-05 | 15 | 1785 | 2012/2013 | November-2012 | 11 | 2012
28400 | Unknown | 2012-11-29 11:54 | 2012-11-29 | 2012-11-29 11:56 | Calculated | 5290 | 5290 - Circuit Breaker 5290 |  | No Segment | 503-01 Nihiniho | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 380 | 24593 | 760 | 0.0309 | 0.015452 | 2726.4316 | 5452 | 2012/2013 | November-2012 | 11 | 2012
28401 | Lower Tap | 2012-11-29 16:16 | 2012-11-29 | 2012-11-29 17:02 | Calculated | TF2575 | TF2575 - Transformer Fuse: TF2575 |  | 101SEG500-186 | Caves 101-07 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 3 | 24593 | 138 | 0.00561 | 0.00012199 | 10 | 459 | 2012/2013 | November-2012 | 11 | 2012
28402 | Unknown | 2012-11-29 16:30 | 2012-11-29 | 2012-11-29 18:35 | Calculated | 5758 | 5758 - Sectionaliser 5758 |  | 413SEG5996-5758 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 123 | 24593 | 15375 | 0.62518 | 0.0050014 | 921 | 115124 | 2012/2013 | November-2012 | 11 | 2012
28405 | Refer 2012/423 Replace Red Tagged Pothead Pole | 2012-11-30 09:16 | 2012-11-30 | 2012-11-30 14:25 | Calculated | TF1001 | TF1001 - Transformer Fuse: TF1001 |  | 110SEG1784-600 | McDonalds 110-01 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 309 | 1 | 24593 | 309 | 0.01256 | 4.0662e-05 | 85 | 26265 | 2012/2013 | November-2012 | 11 | 2012
28406 | Scheduled Maintenance | 2012-11-30 09:34 | 2012-11-30 | 2012-11-30 16:19 | Calculated | 273 | 273 - Air Break Switch 273 |  | 103SEG177-598 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 405 | 20 | 24593 | 8100 | 0.32936 | 0.00081324 | 65 | 26324 | 2012/2013 | November-2012 | 11 | 2012
28407 | Unknown | 2012-11-30 12:40 | 2012-11-30 | 2012-11-30 15:31 | Calculated | TF1962 | TF1962 - Transformer Fuse: TF1962 |  | 114SEG1108-1102 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 4 | 24593 | 684 | 0.02781 | 0.00016265 | 10 | 1710 | 2012/2013 | November-2012 | 11 | 2012
28408 | Unknown C Phase E/F | 2012-12-02 14:15 | 2012-12-02 | 2012-12-02 15:57 | Calculated | 5641 | 5641 - Recloser with Bypass & Links 5641 |  | 413SEG6781-5666 | Ohura 413-01 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 365 | 24592 | 13514 | 0.54953 | 0.014842 | 2588.9316 | 100613 | 2012/2013 | December-2012 | 12 | 2012
28410 | Bolt out Ox/ X/arm @ P44 | 2012-12-03 09:14 | 2012-12-03 | 2012-12-03 09:28 | Calculated | 5684 | 5684 - Recloser 5684 |  | 416SEG5721-5684 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 65 | 24592 | 910 | 0.037 | 0.0026431 | 632.5 | 8854 | 2012/2013 | December-2012 | 12 | 2012
28411 | Refer 2012/427 Fit New T/O Fuses For Tx 1312 | 2012-12-03 09:35 | 2012-12-03 | 2012-12-03 14:56 | Calculated | 248 | 248 - Fused Link 248 |  | 101SEG253-295 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 321 | 11 | 24592 | 1614 | 0.06563 | 0.0004473 | 60 | 8610 | 2012/2013 | December-2012 | 12 | 2012
28412 | Replace Stub Pole | 2012-12-03 09:53 | 2012-12-03 | 2012-12-03 11:56 | Calculated | TF192 | TF192 - Transformer Fuse: TF192 |  | 109SEG341-587 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 123 | 2 | 24592 | 246 | 0.01 | 8.1327e-05 | 25 | 3075 | 2012/2013 | December-2012 | 12 | 2012
28413 | Earthing | 2012-12-03 10:01 | 2012-12-03 | 2012-12-03 12:03 | Calculated | TF8J50 | TF8J50 - Transformer Fuse: TF8J50 |  | No Segment | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 122 | 15 | 24592 | 1830 | 0.07441 | 0.00060995 | 50 | 6099 | 2012/2013 | December-2012 | 12 | 2012
28414 | Broken X/arm | 2012-12-03 14:59 | 2012-12-03 | 2012-12-03 15:54 | Calculated | 5298 | 5298 - Air Break Switch 5298 |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 81 | 24592 | 4455 | 0.18116 | 0.0032938 | 613 | 33714 | 2012/2013 | December-2012 | 12 | 2012
28417 | Unknown | 2012-12-04 07:47 | 2012-12-04 | 2012-12-04 10:46 | Calculated | TF8P12 | TF8P12 - Transformer Fuse: TF8P12 |  | 426SEG5359-5237 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 179 | 2 | 24592 | 358 | 0.01456 | 8.1327e-05 | 15 | 2685 | 2012/2013 | December-2012 | 12 | 2012
28418 | Refer 2012 / 428 Changing Poles & X/arms - Raurimu Feeder Renewal Project | 2012-12-04 09:15 | 2012-12-04 | 2012-12-04 15:57 | Calculated | 5139 | 5139 - Fused Link 5139 |  | 410SEG5543-5161 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 402 | 78 | 24592 | 31356 | 1.2751 | 0.0031718 | 440 | 176879 | 2012/2013 | December-2012 | 12 | 2012
28419 | Refer 2012 / 429 Changing Poles & X/arms | 2012-12-04 09:33 | 2012-12-04 | 2012-12-04 15:50 | Calculated | 1712 | 1712 - Fused Link 1712 |  | 115SEG1712-1714 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 377 | 28 | 24592 | 10556 | 0.42925 | 0.0011386 | 197.5 | 74457 | 2012/2013 | December-2012 | 12 | 2012
28420 | Magpie | 2012-12-04 14:32 | 2012-12-04 | 2012-12-04 15:52 | Calculated | TF9L6 | TF9L6 - Transformer Fuse: TF9L6 |  | No Segment | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 80 | 5 | 24592 | 400 | 0.01627 | 0.00020332 | 10 | 800 | 2012/2013 | December-2012 | 12 | 2012
28421 | Magpie @ Tx 9E2 | 2012-12-05 04:46 | 2012-12-05 | 2012-12-05 06:06 | Calculated | 5417 | 5417 - Recloser 5417 |  | 413SEG5418-5417 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 80 | 58 | 24592 | 6090 | 0.24764 | 0.0023585 | 413 | 43364 | 2012/2013 | December-2012 | 12 | 2012
28423 | Trees | 2012-12-05 06:00 | 2012-12-05 | 2012-12-05 07:25 | Calculated | TF2542 | TF2542 - Transformer Fuse: TF2542 |  | 101SEG514 | Caves 101-11 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 1 | 24592 | 85 | 0.00346 | 4.0664e-05 | 15 | 1275 | 2012/2013 | December-2012 | 12 | 2012
28424 | Unknown | 2012-12-05 06:08 | 2012-12-05 | 2012-12-05 07:36 | Calculated | 705J | 705 - Recloser with Bypass & Links 705 |  | 103SEG705-1736 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 88 | 22 | 24592 | 1936 | 0.07872 | 0.0008946 | 147.5 | 12979 | 2012/2013 | December-2012 | 12 | 2012
28425 | Refer 2012 / 432 Replacing Poles & X/arms | 2012-12-05 09:34 | 2012-12-05 | 2012-12-05 15:44 | Calculated | 1714 | 1714 - Fused Link 1714 |  | 115SEG1714 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 370 | 13 | 24592 | 4810 | 0.19559 | 0.00052863 | 95 | 35150 | 2012/2013 | December-2012 | 12 | 2012
28426 | Jumper Off | 2012-12-05 12:18 | 2012-12-05 | 2012-12-05 12:54 | Calculated | 419 | 419 - Air Break Switch 419 |  | 120SEG419 | Whakamaru 120-05 (was part 124-01) | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 26 | 24592 | 936 | 0.03806 | 0.0010573 | 285 | 10260 | 2012/2013 | December-2012 | 12 | 2012
28427 | Lower Tap | 2012-12-05 14:06 | 2012-12-05 | 2012-12-05 14:17 | Calculated | TF7R14 | TF7R14 - Transformer Fuse: TF7R14 |  | 426SEG6408 | Waihaha 426-02 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 40 | 24592 | 440 | 0.01789 | 0.0016265 | 200 | 2200 | 2012/2013 | December-2012 | 12 | 2012
28428 | SWER Backfeed Changing Poles & X/arms | 2012-12-06 09:02 | 2012-12-06 | 2012-12-06 16:11 | Calculated | 705 | 705 - Recloser with Bypass & Links 705 |  | 103SEG705-1736 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 385 | 26 | 24592 | 1594 | 0.06482 | 0.0010573 | 177.5 | 11902 | 2012/2013 | December-2012 | 12 | 2012
28429 | L/V Maintenace | 2012-12-06 09:30 | 2012-12-06 | 2012-12-06 11:01 | Calculated | TF496 | TF496 - Transformer Fuse: TF496 |  | 112SEG316-637 | Otorohanga 112-07 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 7 | 24592 | 637 | 0.0259 | 0.00028465 | 25 | 2274 | 2012/2013 | December-2012 | 12 | 2012
28431 | Unknown | 2012-12-06 11:25 | 2012-12-06 | 2012-12-06 11:34 | Calculated | 446 | 446 - Recloser 446 |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 168 | 24592 | 1512 | 0.06148 | 0.0068315 | 1679.1667 | 15112 | 2012/2013 | December-2012 | 12 | 2012
28432 | Unknown | 2012-12-06 14:39 | 2012-12-06 | 2012-12-06 17:05 | Calculated | TF138 | TF138 - Transformer Fuse: TF138 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 22 | 24592 | 2311 | 0.09397 | 0.0008946 | 185.5 | 18576 | 2012/2013 | December-2012 | 12 | 2012
28434 | Tree On line | 2012-12-07 04:35 | 2012-12-07 | 2012-12-07 07:43 | Calculated | 112 | 112 - Circuit Breaker with Bypass & Links 112 |  | 106SEG112-REG30 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 188 | 263 | 24592 | 26124 | 1.0623 | 0.010695 | 2496.5 | 239001 | 2012/2013 | December-2012 | 12 | 2012
28436 | Wind | 2012-12-07 06:15 | 2012-12-07 | 2012-12-07 08:06 | Calculated | TF2139 | TF2139 - Transformer Fuse: TF2139 |  | 128SEG REG2-1609 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 4 | 24592 | 444 | 0.01805 | 0.00016265 | 30 | 3330 | 2012/2013 | December-2012 | 12 | 2012
28437 | H/V Maintenance | 2012-12-07 09:05 | 2012-12-07 | 2012-12-07 13:29 | Calculated | TF1378 | TF1378 - Transformer Fuse: TF1378 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 4 | 24592 | 1056 | 0.04294 | 0.00016265 | 10 | 2640 | 2012/2013 | December-2012 | 12 | 2012
28438 | Refer 2012 / 435 Changing Poles & X/arms | 2012-12-07 09:06 | 2012-12-07 | 2012-12-07 14:54 | Calculated | 705 | 705 - Recloser with Bypass & Links 705 |  | 103SEG705-1736 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 316 | 26 | 24592 | 1300 | 0.05286 | 0.0010573 | 177.5 | 9714 | 2012/2013 | December-2012 | 12 | 2012
28439 | Unknown | 2012-12-07 13:20 | 2012-12-07 | 2012-12-07 15:01 | Calculated | 725 | 725 - Fused Link 725 |  | 129SEG402-725 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 4 | 24592 | 404 | 0.01643 | 0.00016265 | 60 | 6060 | 2012/2013 | December-2012 | 12 | 2012
28440 | Tree in L/V | 2012-12-07 13:25 | 2012-12-07 | 2012-12-07 15:51 | Calculated | TF1286 | TF1286 - Transformer Fuse: TF1286 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 2 | 24592 | 292 | 0.01187 | 8.1327e-05 | 25 | 3650 | 2012/2013 | December-2012 | 12 | 2012
28441 | Magpie | 2012-12-07 17:07 | 2012-12-07 | 2012-12-07 18:20 | Calculated | TF7J23 | TF7J23 - Transformer Fuse: TF7J23 |  | 402SEG5596-5930 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 73 | 1 | 24592 | 73 | 0.00297 | 4.0664e-05 | 15 | 1095 | 2012/2013 | December-2012 | 12 | 2012
28487 | Faulty Installation - X/arm & Pole Burnt Off | 2012-12-07 22:34 | 2012-12-07 | 2012-12-08 10:58 | Calculated | 2092 | 2092 - Circuit Breaker Maraetai 11 kV 2092 |  | No Segment | 210-01 Maraetai | Rural D | No Feeder |  |  | Asset Related | Pole | FAIL:FPOL2:FPOF | Pole Top Fire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 743 | 270 | 24592 | 43107 | 1.7529 | 0.010979 | 4642.5 | 652454 | 2012/2013 | December-2012 | 12 | 2012
28443 | Unknown | 2012-12-08 06:59 | 2012-12-08 | 2012-12-08 10:50 | Calculated | TF516 | TF516 - Transformer Fuse: TF516 |  | No Segment | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 231 | 5 | 24592 | 1155 | 0.04697 | 0.00020332 | 25 | 5775 | 2012/2013 | December-2012 | 12 | 2012
28444 | Unknown | 2012-12-08 18:56 | 2012-12-08 | 2012-12-08 20:50 | Calculated | TF1572 | TF1572 - Transformer Fuse: TF1572 |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 2 | 24592 | 228 | 0.00927 | 8.1327e-05 | 15 | 1710 | 2012/2013 | December-2012 | 12 | 2012
28445 | Unknown | 2012-12-08 21:44 | 2012-12-08 | 2012-12-08 22:36 | Calculated | TF176 | TF176 - Transformer Fuse: TF176 |  | 102SEG1271-336 | Hangatiki East 102-01 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 3 | 24592 | 156 | 0.00634 | 0.00012199 | 50 | 2599 | 2012/2013 | December-2012 | 12 | 2012
28446 | Faulty L/A | 2012-12-10 05:35 | 2012-12-10 | 2012-12-10 08:42 | Calculated | 5720 | 5720 - Fused Link 5720 |  | 416SEG5720 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 187 | 3 | 24592 | 561 | 0.02281 | 0.00012199 | 50 | 9349 | 2012/2013 | December-2012 | 12 | 2012
28447 | SWER Backfeed Replace Pole 901/4/9 | 2012-12-10 09:10 | 2012-12-10 | 2012-12-10 13:38 | Calculated | 5935 | 5935 - Fuse Switch 5935 |  | 408SEG5935-5936 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 199 | 88 | 24592 | 7861 | 0.31966 | 0.0035784 | 513.9167 | 53096 | 2012/2013 | December-2012 | 12 | 2012
28449 | Lightning | 2012-12-10 17:16 | 2012-12-10 | 2012-12-10 19:04 | Calculated | TF485 | TF485 - Transformer Fuse: TF485 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 108 | 1 | 24592 | 108 | 0.00439 | 4.0664e-05 | 7.5 | 810 | 2012/2013 | December-2012 | 12 | 2012
28450 | Upgrade Tx | 2012-12-11 08:03 | 2012-12-11 | 2012-12-11 15:49 | Calculated | TF9U7 | TF9U7 - Transformer Fuse: TF9U7 |  | 417SEG5297-5245 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 466 | 69 | 24592 | 32154 | 1.3075 | 0.0028058 | 200 | 93199 | 2012/2013 | December-2012 | 12 | 2012
28451 | Refer 2012 / 443 Replace Tx & X/arms - Tx 1224 | 2012-12-11 09:32 | 2012-12-11 | 2012-12-11 15:29 | Calculated | 2143 | 2143 - Fused Link 2143 |  | 107SEG2143 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 357 | 4 | 24592 | 1428 | 0.05807 | 0.00016265 | 20 | 7140 | 2012/2013 | December-2012 | 12 | 2012
28452 | Unknown | 2012-12-11 16:45 | 2012-12-11 | 2012-12-11 17:42 | Calculated | TF1495 | TF1495 - Transformer Fuse: TF1495 |  | 109SEG341-587 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 1 | 24592 | 57 | 0.00232 | 4.0664e-05 | 5 | 285 | 2012/2013 | December-2012 | 12 | 2012
28454 | Unknown | 2012-12-12 05:46 | 2012-12-12 | 2012-12-12 07:08 | Calculated | TF83 | TF83 - Transformer Fuse: TF83 |  | 101SEG577-679 | Caves 101-05 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 3 | 24592 | 246 | 0.01 | 0.00012199 | 10 | 819 | 2012/2013 | December-2012 | 12 | 2012
28455 | Upgrade Tx | 2012-12-12 08:08 | 2012-12-12 | 2012-12-12 16:11 | Calculated | TF9U10 | TF9U10 - Transformer Fuse: TF9U10 |  | 417SEG5297-5245 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 483 | 124 | 24592 | 20356 | 0.82775 | 0.0050423 | 690 | 117449 | 2012/2013 | December-2012 | 12 | 2012
28456 | Refer 2012 / 444 Replace Poles & X/arms | 2012-12-12 08:12 | 2012-12-12 | 2012-12-12 14:30 | Calculated | 451 | 451 - Air Break Switch 451 |  | 129SEG451-787 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 285 | 13 | 24592 | 3705 | 0.15066 | 0.00052863 | 115 | 32775 | 2012/2013 | December-2012 | 12 | 2012
28459 | Unknown | 2012-12-12 11:41 | 2012-12-12 | 2012-12-12 12:38 | Calculated | TF6J17 | TF6J17 - Transformer Fuse: TF6J17 |  | 402SEG5354 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 57 | 1 | 24592 | 57 | 0.00232 | 4.0664e-05 | 7.5 | 427 | 2012/2013 | December-2012 | 12 | 2012
28462 | Old Age | 2012-12-13 04:25 | 2012-12-13 | 2012-12-13 06:36 | Calculated | TF2533 | TF2533 - Transformer Fuse: TF2533 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 131 | 2 | 24592 | 262 | 0.01065 | 8.1327e-05 | 30 | 3930 | 2012/2013 | December-2012 | 12 | 2012
28463 | Unknown - O/C Installation | 2012-12-13 08:39 | 2012-12-13 | 2012-12-13 08:41 | Calculated | TPTokaanu CB1062 | TPTokaanu CB1062 - 33kV Minimum Oil Circuit Breaker TP1062 |  | No Segment | 515-01 Transpower Tokaanu | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 1955 | 24592 | 3910 | 0.15899 | 0.079497 | 13808.7975 | 27617 | 2012/2013 | December-2012 | 12 | 2012
28464 | Refer 2012 / 445 Replace Structure - TX 7K14 | 2012-12-13 09:03 | 2012-12-13 | 2012-12-13 17:12 | Calculated | TF7K14 | TF7K14 - Transformer Fuse: TF7K14 |  | 408SEG5385-5624 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 489 | 5 | 24592 | 2443 | 0.09934 | 0.00020332 | 40 | 19535 | 2012/2013 | December-2012 | 12 | 2012
28465 | Refer 2012 / 446 Replace poles & X/arms | 2012-12-13 09:05 | 2012-12-13 | 2012-12-13 14:00 | Calculated | TF765 | TF765 - Transformer Fuse: TF765 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 295 | 4 | 24592 | 1180 | 0.04798 | 0.00016265 | 30 | 8850 | 2012/2013 | December-2012 | 12 | 2012
28466 | Magpie | 2012-12-13 09:13 | 2012-12-13 | 2012-12-13 10:22 | Calculated | TF9R6 | TF9R6 - Transformer Fuse: TF9R6 |  | 406SEG5897-5481 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 4 | 24592 | 276 | 0.01122 | 0.00016265 | 15 | 1035 | 2012/2013 | December-2012 | 12 | 2012
28467 | Fuse Pulled Apart | 2012-12-14 04:57 | 2012-12-14 | 2012-12-14 06:03 | Calculated | T814 | T814 - 3 Phase : 30.00 kVA : GNDPAD |  | 119SEG456 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 11 | 24592 | 726 | 0.02952 | 0.0004473 | 30 | 1979 | 2012/2013 | December-2012 | 12 | 2012
28475 | Refer 2012 / 448 Check Repair Links 6191 | 2012-12-14 09:36 | 2012-12-14 | 2012-12-14 10:43 | Calculated | 6193 | 6193 - Fused Link 6193 |  | 423SEG6196-5205 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 61 | 152 | 24592 | 9272 | 0.37703 | 0.0061809 | 550 | 33549 | 2012/2013 | December-2012 | 12 | 2012
28471 | L/V Maintenance | 2012-12-14 10:18 | 2012-12-14 | 2012-12-14 12:19 | Calculated | TF1537 | TF1537 - Transformer Fuse: TF1537 |  | 111SEG359-2141 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 3 | 24592 | 363 | 0.01476 | 0.00012199 | 15 | 1815 | 2012/2013 | December-2012 | 12 | 2012
28472 | Switch Board Fire | 2012-12-15 10:26 | 2012-12-15 | 2012-12-15 11:06 | Calculated | TF1576 | TF1576 - Transformer Fuse: TF1576 |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFIH | House Fire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 1 | 24592 | 40 | 0.00163 | 4.0664e-05 | 15 | 600 | 2012/2013 | December-2012 | 12 | 2012
28473 | Suspect Stolen Earth | 2012-12-15 18:02 | 2012-12-15 | 2012-12-15 20:20 | Calculated | TF6Q9 | TF6Q9 - Transformer Fuse: TF6Q9 |  | 426SEG5239 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUV | Wilful Damage or Interference | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 138 | 1 | 24592 | 138 | 0.00561 | 4.0664e-05 | 15 | 2070 | 2012/2013 | December-2012 | 12 | 2012
28476 | Fuse Pulled Apart | 2012-12-17 12:25 | 2012-12-17 | 2012-12-17 13:40 | Calculated | 08F04 | 08F04 - 1 Phase : 15.00 kVA : POLEMNT |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 75 | 2 | 24592 | 150 | 0.0061 | 8.1327e-05 | 15 | 1125 | 2012/2013 | December-2012 | 12 | 2012
28477 | Faulty Tx 6Q9 | 2012-12-17 17:08 | 2012-12-17 | 2012-12-17 18:15 | Calculated | TF6Q9 | TF6Q9 - Transformer Fuse: TF6Q9 |  | 426SEG5239 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 67 | 6 | 24592 | 392 | 0.01594 | 0.00024398 | 60 | 3930 | 2012/2013 | December-2012 | 12 | 2012
28479 | Magpie | 2012-12-18 09:00 | 2012-12-18 | 2012-12-18 11:31 | Calculated | 07R09 | 07R09 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 4 | 24592 | 604 | 0.02456 | 0.00016265 | 15 | 2265 | 2012/2013 | December-2012 | 12 | 2012
28480 | Refer 2012 / 450 Replace Poles & X/arms | 2012-12-18 09:08 | 2012-12-18 | 2012-12-18 17:14 | Calculated | 6000 | 6000 - Circuit Breaker 6000 |  | 611SEG5174-6000 | 516-01 Transpower National Park | Rural D | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 393 | 22 | 24592 | 8646 | 0.35158 | 0.0008946 | 112.5 | 44212 | 2012/2013 | December-2012 | 12 | 2012
28481 | Rework | 2012-12-18 10:00 | 2012-12-18 | 2012-12-18 10:28 | Calculated | TF2193 | TF2193 - Transformer Fuse: TF2193 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 28 | 27 | 24592 | 756 | 0.03074 | 0.0010979 | 100 | 2799 | 2012/2013 | December-2012 | 12 | 2012
28482 | Unknown | 2012-12-19 07:16 | 2012-12-19 | 2012-12-19 10:00 | Calculated | 5847 | 5847 - Recloser w Bypass & Links 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 39 | 24592 | 6396 | 0.26008 | 0.0015859 | 343.5 | 56333 | 2012/2013 | December-2012 | 12 | 2012
28483 | Magpie | 2012-12-19 07:24 | 2012-12-19 | 2012-12-19 07:59 | Calculated | 1.36 | 1.36 - Fused Link 1.36 |  | 404SEGF1.36 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 42 | 24592 | 1470 | 0.05978 | 0.0017079 | 100 | 3499 | 2012/2013 | December-2012 | 12 | 2012
28484 | Replace Leaking Transformer | 2012-12-19 12:17 | 2012-12-19 | 2012-12-19 13:41 | Calculated | TF7K14 | TF7K14 - Transformer Fuse: TF7K14 |  | 408SEG5385-5624 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 3 | 24592 | 252 | 0.01025 | 0.00012199 | 15 | 1260 | 2012/2013 | December-2012 | 12 | 2012
28485 | L/V Fault | 2012-12-19 13:47 | 2012-12-19 | 2012-12-19 14:15 | Calculated | T2317 | T2317 - 1 Phase : 10.00 kVA : POLEMNT |  | 107SEG243-113 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 1 | 24592 | 28 | 0.00114 | 4.0664e-05 | 10 | 280 | 2012/2013 | December-2012 | 12 | 2012
28489 | Refer 2012 / 453 Reworks | 2012-12-20 09:05 | 2012-12-20 | 2012-12-20 12:42 | Calculated | 372 | 372 - Fused Link 372 |  | 122SEG372 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 217 | 22 | 24592 | 4774 | 0.19413 | 0.0008946 | 148 | 32115 | 2012/2013 | December-2012 | 12 | 2012
28491 | L/V Fault | 2012-12-21 09:20 | 2012-12-21 | 2012-12-21 10:00 | Calculated | TF2204 | TF2204 - Transformer Fuse: TF2204 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 5 | 24592 | 200 | 0.00813 | 0.00020332 | 30 | 1200 | 2012/2013 | December-2012 | 12 | 2012
28492 | Branch On Line | 2012-12-22 06:05 | 2012-12-22 | 2012-12-22 07:33 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 26 | 24592 | 2288 | 0.09304 | 0.0010573 | 281.4286 | 24765 | 2012/2013 | December-2012 | 12 | 2012
28493 | Unknown | 2012-12-22 08:19 | 2012-12-22 | 2012-12-22 11:00 | Calculated | 05Q01 | 05Q01 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG6129 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 1 | 24592 | 161 | 0.00655 | 4.0664e-05 | 15 | 2415 | 2012/2013 | December-2012 | 12 | 2012
28494 | Old Age | 2012-12-22 17:08 | 2012-12-22 | 2012-12-22 18:11 | Calculated | T1525 | T1525 - 3 Phase : 30.00 kVA : POLEMNT |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 3 | 24592 | 189 | 0.00769 | 0.00012199 | 30 | 1890 | 2012/2013 | December-2012 | 12 | 2012
28495 | Faulty Insulator | 2012-12-22 18:15 | 2012-12-22 | 2012-12-22 22:04 | Calculated | 5370 | 5370 - Recloser with Bypass & Links 5370 |  | 402SEG5370-5199 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLI | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 229 | 78 | 24592 | 17862 | 0.72633 | 0.0031718 | 590 | 135110 | 2012/2013 | December-2012 | 12 | 2012
28496 | Faulty DDO | 2012-12-24 09:56 | 2012-12-24 | 2012-12-24 10:35 | Calculated | TF4G8 | TF4G8 - Transformer Fuse: TF4G8 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 39 | 1 | 24592 | 39 | 0.00159 | 4.0664e-05 | 15 | 585 | 2012/2013 | December-2012 | 12 | 2012
28497 | Lightning | 2012-12-24 16:10 | 2012-12-24 | 2012-12-24 17:17 | Calculated | 667 | 667 - Fused Link 667 |  | 120SEG667 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 3 | 24592 | 201 | 0.00817 | 0.00012199 | 65 | 4355 | 2012/2013 | December-2012 | 12 | 2012
28499 | Fuse Fell Out | 2012-12-26 08:44 | 2012-12-26 | 2012-12-26 09:45 | Calculated | TF4056 | TF4056 - Transformer Fuse: TF4056 |  | 409SEG5599-5600 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 61 | 1 | 24592 | 61 | 0.00248 | 4.0664e-05 | 5 | 305 | 2012/2013 | December-2012 | 12 | 2012
28500 | Burnt X/arm | 2012-12-26 10:55 | 2012-12-26 | 2012-12-26 11:40 | Calculated | TF1037 | TF1037 - Transformer Fuse: TF1037 |  | 116SEG1334-269 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAU | Cross-Arm Burnt | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 3 | 24592 | 135 | 0.00549 | 0.00012199 | 15 | 675 | 2012/2013 | December-2012 | 12 | 2012
28501 | Unknown | 2012-12-26 17:53 | 2012-12-26 | 2012-12-26 18:12 | Calculated | T2657 | T2657 - 3 Phase : 15.00 kVA : POLEMNT |  | 110SEG711 | McDonalds 110-04 | Urban A | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 1 | 24592 | 19 | 0.00077 | 4.0664e-05 | 15 | 285 | 2012/2013 | December-2012 | 12 | 2012
28502 | Unknown | 2012-12-26 20:15 | 2012-12-26 | 2012-12-26 21:45 | Calculated | T336 | T336 - 3 Phase : 30.00 kVA : POLEMNT |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 4 | 24592 | 360 | 0.01464 | 0.00016265 | 30 | 2700 | 2012/2013 | December-2012 | 12 | 2012
28504 | Scheduled Maintenance @TX2272 | 2012-12-27 09:39 | 2012-12-27 | 2012-12-27 13:32 | Calculated | TF2272 | TF2272 - Transformer Fuse: TF2272 |  | 109SEG396-397 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 233 | 1 | 24592 | 233 | 0.00947 | 4.0664e-05 | 100 | 23300 | 2012/2013 | December-2012 | 12 | 2012
28507 | Refer 2012 / 456 Replace Structure - Tx 1B18 | 2012-12-28 08:22 | 2012-12-28 | 2012-12-28 16:03 | Calculated | 5831 | 5831 - Air Break Switch 5831 |  | 401SEG5967-5831 | Hakiaha 401-02 | Rural B | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 346 | 90 | 24592 | 31140 | 1.2663 | 0.0036597 | 430 | 148779 | 2012/2013 | December-2012 | 12 | 2012
28510 | Trees In Swamp | 2012-12-28 16:42 | 2012-12-28 | 2012-12-28 21:00 | Calculated | 379 | 379 - Air Break Switch 379 |  | 122SEG379 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 256 | 303 | 24592 | 13405 | 0.5451 | 0.012321 | 2808 | 117569 | 2012/2013 | December-2012 | 12 | 2012
28511 | Jumper Off @ Link 546 | 2012-12-29 08:02 | 2012-12-29 | 2012-12-29 10:50 | Calculated | 5546 | 5546 - Fused Link 5546 |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 168 | 13 | 24592 | 2184 | 0.08881 | 0.00052863 | 75 | 12599 | 2012/2013 | December-2012 | 12 | 2012
28512 | Broken X/arm @ Tx 1512 | 2012-12-29 13:35 | 2012-12-29 | 2012-12-29 16:01 | Calculated | TF1512 | TF1512 - Transformer Fuse: TF1512 |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 1 | 24592 | 146 | 0.00594 | 4.0664e-05 | 25 | 3650 | 2012/2013 | December-2012 | 12 | 2012
28513 | Faulty L/A - 3 x Blown | 2012-12-29 13:58 | 2012-12-29 | 2012-12-29 17:18 | Calculated | 808 | 808 - Solid Link 808 |  | 102SEG521-505 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 200 | 72 | 24592 | 6377 | 0.25931 | 0.0029278 | 3000 | 374000 | 2012/2013 | December-2012 | 12 | 2012
28514 | Inframax & Tree vs Line | 2012-12-29 14:35 | 2012-12-29 | 2012-12-29 16:15 | Calculated | 5243 | 5243 - Fused Link 5243 |  | 403SEG5243-5855 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 50 | 24592 | 5000 | 0.20332 | 0.0020332 | 370 | 36999 | 2012/2013 | December-2012 | 12 | 2012
28516 | Faulty DDO - Burnt Up | 2012-12-29 15:42 | 2012-12-29 | 2012-12-29 17:04 | Calculated | TF2511 | TF2511 - Transformer Fuse: TF2511 |  | 109SEG119-2107 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 1 | 24592 | 82 | 0.00333 | 4.0664e-05 | 10 | 820 | 2012/2013 | December-2012 | 12 | 2012
28517 | Unknown | 2012-12-31 00:56 | 2012-12-31 | 2012-12-31 01:04 | Calculated | 594 | 594 - Circuit Breaker 594 |  | No Segment | 205-01 Gadsby Road | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 2046 | 24592 | 14322 | 0.58238 | 0.083198 | 14509.5 | 101566 | 2012/2013 | December-2012 | 12 | 2012
28518 | Unknown | 2012-12-31 07:32 | 2012-12-31 | 2012-12-31 08:28 | Calculated | TF4056 | TF4056 - Transformer Fuse: TF4056 |  | 409SEG5599-5600 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 56 | 1 | 24592 | 56 | 0.00228 | 4.0664e-05 | 5 | 280 | 2012/2013 | December-2012 | 12 | 2012
28519 | L/V Fault | 2012-12-31 09:46 | 2012-12-31 | 2012-12-31 11:17 | Calculated | TF595 | TF595 - Transformer Fuse: TF595 |  | 122SEG633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 3 | 24592 | 273 | 0.0111 | 0.00012199 | 30 | 2730 | 2012/2013 | December-2012 | 12 | 2012
28520 | Jumper Off @ Pole 12 | 2012-12-31 19:05 | 2012-12-31 | 2012-12-31 21:15 | Calculated | 5472 | 5472 - Fused Link 5472 |  | 402SEG5467-5472 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 130 | 67 | 24592 | 8710 | 0.35418 | 0.0027245 | 450 | 58500 | 2012/2013 | December-2012 | 12 | 2012
28522 | Private Tree Felling | 2013-01-01 07:54 | 2013-01-01 | 2013-01-01 09:43 | Calculated | 5385 | 5385 - Recloser with Bypass 5385 |  | 408SEG5388-5385 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUV | Wilful Damage or Interference | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 178 | 24581 | 10180 | 0.41414 | 0.0072414 | 1313.1389 | 76450 | 2012/2013 | January-2013 | 1 | 2013
28523 | Unknown | 2013-01-01 14:56 | 2013-01-01 | 2013-01-01 15:38 | Calculated | TF1452 | TF1452 - Transformer Fuse: TF1452 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 3 | 24581 | 126 | 0.00513 | 0.00012205 | 50 | 2099 | 2012/2013 | January-2013 | 1 | 2013
28521 | Birds Nest | 2013-01-02 17:48 | 2013-01-02 | 2013-01-02 18:50 | Calculated | T1452 | T1452 - 3 Phase : 50.00 kVA : POLEMNT |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 3 | 24581 | 186 | 0.00757 | 0.00012205 | 50 | 3099 | 2012/2013 | January-2013 | 1 | 2013
28525 | Unknown | 2013-01-03 08:42 | 2013-01-03 | 2013-01-03 10:16 | Calculated | 6012 | 6012 - Air Break Switch 6012 |  | 415SEG6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 1 | 24581 | 94 | 0.00382 | 4.0682e-05 | 50 | 4700 | 2012/2013 | January-2013 | 1 | 2013
28527 | Repair Earth Wire | 2013-01-03 10:40 | 2013-01-03 | 2013-01-03 11:15 | Calculated | TF9R5 | TF9R5 - Transformer Fuse: TF9R5 |  | 406SEG5897-5481 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 3 | 24581 | 105 | 0.00427 | 0.00012205 | 15 | 525 | 2012/2013 | January-2013 | 1 | 2013
28528 | Refer 2012 / 2 Replave Link 657 & 669 with Electronic Sectionaliser | 2013-01-03 12:31 | 2013-01-03 | 2013-01-03 12:36 | Calculated | 5657 | 5657 - Fused Link 5657 |  | 421SEG5657-5473 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 5 | 11 | 24581 | 55 | 0.00224 | 0.0004475 | 105 | 525 | 2012/2013 | January-2013 | 1 | 2013
28529 | Refer 2012 / 2 Replave Link 657 & 669 with Electronic Sectionaliser | 2013-01-03 12:43 | 2013-01-03 | 2013-01-03 12:48 | Calculated | 5669 | 5669 - Fused Link 5669 |  | 421SEG5669-5342 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 5 | 47 | 24581 | 235 | 0.00956 | 0.001912 | 340.5 | 1702 | 2012/2013 | January-2013 | 1 | 2013
28530 | Refer 2012 / 3 Upgrade Link 792 to fit Electronic Sectionaliser | 2013-01-03 13:30 | 2013-01-03 | 2013-01-03 14:58 | Calculated | 5342 | 5342 - Fused Link 5342 |  | 421SEG5342-5792 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 61 | 27 | 24581 | 1647 | 0.067 | 0.0010984 | 200.5 | 12230 | 2012/2013 | January-2013 | 1 | 2013
28531 | Split X/Arm - Insulator Pulled | 2013-01-04 19:51 | 2013-01-04 | 2013-01-05 04:45 | Calculated | 6337 | 6337 - Circuit Breaker Waiotaka 11kV 6337 |  | 427SEG6337-6549 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 534 | 8 | 24581 | 1758 | 0.07152 | 0.00032545 | 350 | 165950 | 2012/2013 | January-2013 | 1 | 2013
28532 | Unknown | 2013-01-04 20:08 | 2013-01-04 | 2013-01-04 21:05 | Calculated | 5415 | 5415 - Recloser with Bypass & Links 5415 |  | 409SEG5415-5844 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 34 | 24581 | 1938 | 0.07884 | 0.0013832 | 241.5 | 13765 | 2012/2013 | January-2013 | 1 | 2013
28533 | Broken Insulator | 2013-01-06 11:32 | 2013-01-06 | 2013-01-06 16:48 | Calculated | 5318 | 5318 - Recloser with Bypass & Links 5318 |  | 427SEG5318-5524 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 316 | 6 | 24581 | 1896 | 0.07713 | 0.00024409 | 50 | 15800 | 2012/2013 | January-2013 | 1 | 2013
28535 | Unknown | 2013-01-07 08:57 | 2013-01-07 | 2013-01-07 10:17 | Calculated | 5524 | 5524 - Sectionaliser 5524 |  | 427SEG5524 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 6 | 24581 | 480 | 0.01953 | 0.00024409 | 50 | 4000 | 2012/2013 | January-2013 | 1 | 2013
28536 | SWER Backfeed Refer 2013 / 5 Replace Pole 901/4/9 | 2013-01-07 09:07 | 2013-01-07 | 2013-01-07 14:41 | Calculated | 5935 | 5935 - Fuse Switch 5935 |  | 408SEG5935-5936 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 274 | 88 | 24581 | 10726 | 0.43635 | 0.00358 | 513.9167 | 73321 | 2012/2013 | January-2013 | 1 | 2013
28537 | Goose Line-Down | 2013-01-07 13:06 | 2013-01-07 | 2013-01-07 15:21 | Calculated | 5955 | 5955 - Circuit Breaker Northern 5955 |  | No Segment | 508-01 Borough | Rural B | No Feeder |  |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 1227 | 24581 | 86225 | 3.5078 | 0.049917 | 7797.5493 | 454073 | 2012/2013 | January-2013 | 1 | 2013
28540 | Old Age | 2013-01-07 13:56 | 2013-01-07 | 2013-01-07 15:09 | Calculated | TF702 | TF702 - Transformer Fuse: TF702 |  | 120SEG497-REG31 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 3 | 24581 | 219 | 0.00891 | 0.00012205 | 25 | 1824 | 2012/2013 | January-2013 | 1 | 2013
28542 | High Winds - Clash | 2013-01-07 15:29 | 2013-01-07 | 2013-01-09 16:30 | Calculated | 796 | 796 - Circuit Breaker 796 |  | 301SEG1418-796 | Taharoa A 301-02 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24581 |  | 0 | 0 |  |  | 2012/2013 | January-2013 | 1 | 2013
28543 | Trees @ Pole 1130061 | 2013-01-07 17:15 | 2013-01-07 | 2013-01-07 18:58 | Calculated | 1339 | 1339 - Air Break Switch 1339 |  | 113SEG1339-1511 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 87 | 24581 | 3849 | 0.15658 | 0.0035393 | 733 | 31962 | 2012/2013 | January-2013 | 1 | 2013
28545 | Bush Fire - Poles On Fire | 2013-01-08 00:54 | 2013-01-08 | 2013-01-08 14:26 | Calculated | 466 | 466 - Recloser 466 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:7TQSV7 | Other Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 812 | 28 | 24581 | 22736 | 0.92494 | 0.0011391 | 232.5 | 188790 | 2012/2013 | January-2013 | 1 | 2013
28546 | Loose X/arm @ Pole 40 | 2013-01-08 07:38 | 2013-01-08 | 2013-01-08 18:06 | Calculated | 6650 | 6650 - Load Break Switch 6650 |  | 424SEG5200-6650 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 540 | 854 | 24581 | 16111 | 0.65542 | 0.034742 | 8455 | 1024732 | 2012/2013 | January-2013 | 1 | 2013
28547 | Refer 2013 / 7 Repalce Poles 95 & 105 | 2013-01-08 08:31 | 2013-01-08 | 2013-01-08 15:44 | Calculated | 531 | 531 - Air Break Switch 531 |  | 121SEG487-531 | Huirimu 121-04 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 345 | 25 | 24581 | 8625 | 0.35088 | 0.001017 | 510 | 175949 | 2012/2013 | January-2013 | 1 | 2013
28548 | Broken L/V X/arm | 2013-01-08 09:20 | 2013-01-08 | 2013-01-08 10:31 | Calculated | TF2094 | TF2094 - Transformer Fuse: TF2094 |  | 117SEG1721-1307 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 71 | 5 | 24581 | 355 | 0.01444 | 0.00020341 | 30 | 2130 | 2012/2013 | January-2013 | 1 | 2013
28549 | Broken Link 411 | 2013-01-08 16:48 | 2013-01-08 | 2013-01-08 23:38 | Calculated | 5415 | 5415 - Recloser with Bypass & Links 5415 |  | 409SEG5415-5844 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 369 | 185 | 24581 | 17856 | 0.72641 | 0.0075261 | 1323.1667 | 128123 | 2012/2013 | January-2013 | 1 | 2013
28550 | Trees | 2013-01-09 00:06 | 2013-01-09 | 2013-01-09 00:08 | Calculated | 788 | 788 - Circuit Breaker 788 |  | 302SEG147-788 | Taharoa B 302-02 | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 116 | 24581 | 232 | 0.00944 | 0.0047191 | 3275.0833 | 6550 | 2012/2013 | January-2013 | 1 | 2013
28551 | Refer 2013 / 8 Replace Poles & Xarms | 2013-01-09 07:54 | 2013-01-09 | 2013-01-09 15:14 | Calculated | 1749 | 1749 - Solid Links 1749 |  | 129SEG1749-2204 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 355 | 6 | 24581 | 2130 | 0.08665 | 0.00024409 | 45 | 15975 | 2012/2013 | January-2013 | 1 | 2013
28555 | Lower Tap | 2013-01-09 12:30 | 2013-01-09 | 2013-01-09 12:38 | Calculated | TF88 | TF88 - Transformer Fuse: TF88 |  | 101SEG746-1656 | Caves 101-08 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 1 | 24581 | 8 | 0.00033 | 4.0682e-05 | 200 | 1600 | 2012/2013 | January-2013 | 1 | 2013
28554 | Broken Link @ 6012 | 2013-01-09 13:45 | 2013-01-09 | 2013-01-09 14:35 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 26 | 24581 | 1300 | 0.05289 | 0.0010577 | 281.4286 | 14071 | 2012/2013 | January-2013 | 1 | 2013
28559 | Refer 2013 / 13 Fit Bolt Extension on 11kv Cable Arrestors | 2013-01-10 12:58 | 2013-01-10 | 2013-01-10 14:47 | Calculated | TF787 | TF787 - Transformer Fuse: TF787 |  | 123SEG490-528 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 109 | 6 | 24581 | 638 | 0.02596 | 0.00024409 | 35 | 3715 | 2012/2013 | January-2013 | 1 | 2013
28560 | Refer 2013 / 14 Replace Pole 1141101 | 2013-01-11 10:37 | 2013-01-11 | 2013-01-11 13:06 | Calculated | 1108 | 1108 - Recloser with Bypass 1108 |  | 114SEG1110-1107 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 149 | 58 | 24581 | 8642 | 0.35157 | 0.0023595 | 395 | 58854 | 2012/2013 | January-2013 | 1 | 2013
28561 | Refer 2013 / 12 Cut & Reterminate Cable - Commission Tx 4298 | 2013-01-11 13:46 | 2013-01-11 | 2013-01-11 15:08 | Calculated | 5818 | 5818 - Air Break Switch 5818 |  | 416SEG5818-5697 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 82 | 190 | 24581 | 15580 | 0.63382 | 0.0077295 | 1585.7143 | 130028 | 2012/2013 | January-2013 | 1 | 2013
28562 | Party Streamers Into Line | 2013-01-11 16:31 | 2013-01-11 | 2013-01-11 16:32 | Calculated | 5132 | 5132 - Circuit Breaker Manunui SF6 5132 |  | 409SEG5132-5900 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 618 | 24581 | 618 | 0.02514 | 0.025141 | 4245.1667 | 4245 | 2012/2013 | January-2013 | 1 | 2013
28563 | Tx Pole Snapped | 2013-01-11 18:40 | 2013-01-11 | 2013-01-12 17:27 | Calculated | TF197 | TF197 - Transformer Fuse: TF197 |  | 112SEG326-288 | Otorohanga 112-06 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1367 | 3 | 24581 | 4101 | 0.16684 | 0.00012205 | 15 | 20505 | 2012/2013 | January-2013 | 1 | 2013
28564 | Vehicle vs Pole | 2013-01-13 01:47 | 2013-01-13 | 2013-01-13 06:05 | Calculated | 1312 | 1312 - Air Break Switch 1312 |  | 116SEG1312-1362 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 258 | 45 | 24581 | 11610 | 0.47232 | 0.0018307 | 448 | 115583 | 2012/2013 | January-2013 | 1 | 2013
28565 | Rat in L/V | 2013-01-13 09:40 | 2013-01-13 | 2013-01-13 11:37 | Calculated | TF12P05 | TF12P05 - Transformer Fuse: TF12P05 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AOTH | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 117 | 1 | 24581 | 117 | 0.00476 | 4.0682e-05 | 15 | 1755 | 2012/2013 | January-2013 | 1 | 2013
28566 | Silage Contractor vs L/V | 2013-01-13 12:48 | 2013-01-13 | 2013-01-13 14:57 | Calculated | TF1244 | TF1244 - Transformer Fuse: TF1244 |  | 120SEG481-422 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 3 | 24581 | 387 | 0.01574 | 0.00012205 | 15 | 1935 | 2012/2013 | January-2013 | 1 | 2013
28567 | Refer 2013 / 17 Shift Line & Connect New Tx Structure | 2013-01-14 09:32 | 2013-01-14 | 2013-01-14 16:18 | Calculated | 1346 | 1346 - Sectionaliser 1346 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 406 | 19 | 24581 | 7654 | 0.31138 | 0.00077295 | 125 | 50412 | 2012/2013 | January-2013 | 1 | 2013
28569 | Broken DDO | 2013-01-15 00:35 | 2013-01-15 | 2013-01-15 10:28 | Calculated | TF444 | TF444 - Transformer Fuse: TF444 |  | 111SEG382 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 593 | 1 | 24581 | 593 | 0.02412 | 4.0682e-05 | 10 | 5930 | 2012/2013 | January-2013 | 1 | 2013
28570 | Refer 2013 / 19 Replace Poles & X/arms @ Poles 1241260, 61, 62, 63, 67, 68 & 71 | 2013-01-15 08:35 | 2013-01-15 | 2013-01-15 15:48 | Calculated | 480 | 480 - Air Break Switch 480 |  | 120SEG482-480 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 376 | 9 | 24581 | 3384 | 0.13767 | 0.00036614 | 130 | 48880 | 2012/2013 | January-2013 | 1 | 2013
28573 | Fire @ Tx 12P3 | 2013-01-16 07:15 | 2013-01-16 | 2013-01-16 11:45 | Calculated | TF12P03 | TF12P03 - Transformer Fuse: TF12P03 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Third Party (includeds unauthorised contractors) | Fire | 3PAR:EFIR:EFIB | Fire (Not Electrical) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 270 | 50 | 24581 | 5450 | 0.22172 | 0.0020341 | 198 | 21434 | 2012/2013 | January-2013 | 1 | 2013
28575 | Refer 2013 / 20 Replace Poles && X/arms | 2013-01-16 09:03 | 2013-01-16 | 2013-01-16 14:57 | Calculated | 1713 | 1713 - Fused Link 1713 |  | 115SEG1713 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 354 | 7 | 24581 | 2478 | 0.10081 | 0.00028477 | 60 | 21240 | 2012/2013 | January-2013 | 1 | 2013
28579 | Bolt Down Tx | 2013-01-16 10:29 | 2013-01-16 | 2013-01-16 11:30 | Calculated | TF6H5 | TF6H5 - Transformer Fuse: TF6H5 |  | 422SEG5538-5841 | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 29 | 5 | 24581 | 55 | 0.00224 | 0.00020341 | 33 | 399 | 2012/2013 | January-2013 | 1 | 2013
28576 | Stock Rubbing - Clash | 2013-01-17 07:35 | 2013-01-17 | 2013-01-17 09:08 | Calculated | TF24 | TF24 - Transformer Fuse: TF24 |  | 103SEG731-REG14 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AFAR | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 2 | 24581 | 186 | 0.00757 | 8.1364e-05 | 15 | 1395 | 2012/2013 | January-2013 | 1 | 2013
28577 | Line Down @ Pole 36/30 | 2013-01-17 08:32 | 2013-01-17 | 2013-01-17 13:28 | Calculated | 5669 | 5669 - Fused Link 5669 |  | 421SEG5669-5342 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 296 | 82 | 24581 | 14297 | 0.58163 | 0.0033359 | 563.5 | 103240 | 2012/2013 | January-2013 | 1 | 2013
28578 | Refer 2013 / 21 Remove Temp ABS 2 & Replace 2 Poles | 2013-01-17 09:42 | 2013-01-17 | 2013-01-17 14:03 | Calculated | 786 | 786 - Fused Link 786 |  | 124SEG542-786 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 236 | 54 | 24581 | 12744 | 0.51845 | 0.0021968 | 615 | 145139 | 2012/2013 | January-2013 | 1 | 2013
28580 | Refer 2013 / 22 Replace poles & X /arms | 2013-01-18 07:57 | 2013-01-18 | 2013-01-18 16:17 | Calculated | 426 | 426 - Recloser 426 |  | 129SEG434-426 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 412 | 4 | 24581 | 1648 | 0.06704 | 0.00016273 | 40 | 16480 | 2012/2013 | January-2013 | 1 | 2013
28581 | Wind - O/C T | 2013-01-18 13:59 | 2013-01-18 | 2013-01-19 07:28 | Calculated | 796 | 796 - Circuit Breaker 796 |  | 301SEG1418-796 | Taharoa A 301-02 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24581 |  | 0 | 0 |  |  | 2012/2013 | January-2013 | 1 | 2013
28582 | Unknown | 2013-01-19 06:00 | 2013-01-19 | 2013-01-19 08:18 | Calculated | TF3368 | TF3368 - Transformer Fuse TF3368 |  | 421SEG5874-6730 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 138 | 1 | 24581 | 138 | 0.00561 | 4.0682e-05 | 75 | 10350 | 2012/2013 | January-2013 | 1 | 2013
28584 | Bypass Faulty Sect 352 | 2013-01-20 08:35 | 2013-01-20 | 2013-01-20 09:06 | Calculated | 5370 | 5370 - Recloser with Bypass & Links 5370 |  | 402SEG5370-5199 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLI | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 78 | 24581 | 2418 | 0.09837 | 0.0031732 | 590 | 18290 | 2012/2013 | January-2013 | 1 | 2013
28585 | Wind | 2013-01-20 14:00 | 2013-01-20 | 2013-01-20 16:02 | Calculated | 514 | 514 - Fused Link 514 |  | 101SEG274-506 | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 26 | 24581 | 3172 | 0.12904 | 0.0010577 | 185 | 22570 | 2012/2013 | January-2013 | 1 | 2013
28586 | Wind - O/C T | 2013-01-20 15:20 | 2013-01-20 | 2013-01-21 08:44 | Calculated | 796 | 796 - Circuit Breaker 796 |  | 301SEG1418-796 | Taharoa A 301-02 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24581 |  | 0 | 0 |  |  | 2012/2013 | January-2013 | 1 | 2013
28588 | Faulty Tx | 2013-01-20 18:55 | 2013-01-20 | 2013-01-21 12:36 | Calculated | TF2138 | TF2138 - Transformer Fuse: TF2138 |  | 128SEG REG2-1609 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLI | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1061 | 3 | 24581 | 3183 | 0.12949 | 0.00012205 | 15 | 15915 | 2012/2013 | January-2013 | 1 | 2013
28589 | Refer 2013 / 26 Terminate @ Pole 6 & Cut Away Rest Of Line | 2013-01-21 10:05 | 2013-01-21 | 2013-01-21 13:04 | Calculated | 5749 | 5749 - Fused Link 5749 |  | 409SEG5749 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 179 | 3 | 24581 | 537 | 0.02185 | 0.00012205 | 27.5 | 4922 | 2012/2013 | January-2013 | 1 | 2013
28593 | Unknown | 2013-01-22 07:39 | 2013-01-22 | 2013-01-22 09:18 | Calculated | 5529 | 5529 - Recloser 5529 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 69 | 24581 | 6831 | 0.2779 | 0.002807 | 432.5 | 42817 | 2012/2013 | January-2013 | 1 | 2013
28594 | L/V Reworks | 2013-01-22 10:00 | 2013-01-22 | 2013-01-22 11:30 | Calculated | TF613 | TF613 - Transformer Fuse: TF613 |  | 122SEG398-380 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 90 | 6 | 24581 | 540 | 0.02197 | 0.00024409 | 25 | 2249 | 2012/2013 | January-2013 | 1 | 2013
28595 | Upgrade Tx | 2013-01-22 10:38 | 2013-01-22 | 2013-01-22 13:16 | Calculated | TF2622 | TF2622 - Transformer Fuse: TF2622 |  | 129SEG635-REG23J | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 158 | 1 | 24581 | 158 | 0.00643 | 4.0682e-05 | 15 | 2370 | 2012/2013 | January-2013 | 1 | 2013
28596 | Refer 2013 / 28 Upgrade Structure & Earthing @ Tx 8F5 | 2013-01-23 09:02 | 2013-01-23 | 2013-01-23 15:33 | Calculated | 5123 | 5123 - Fused Link 5123 |  | 413SEG5123 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 391 | 5 | 24581 | 1955 | 0.07953 | 0.00020341 | 40 | 15640 | 2012/2013 | January-2013 | 1 | 2013
28597 | L/V Fault | 2013-01-23 23:35 | 2013-01-23 | 2013-01-24 00:15 | Calculated | TF9K12 | TF9K12 - Transformer Fuse: TF9K12 |  | 409SEG5549 | Southern 409-02 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 3 | 24581 | 120 | 0.00488 | 0.00012205 | 15 | 600 | 2012/2013 | January-2013 | 1 | 2013
28599 | Refer 2013 / 30 Install New Magnafix Unit, New Links @ Pole 54 & Replace Links 767 | 2013-01-24 08:35 | 2013-01-24 | 2013-01-24 17:47 | Calculated | 6321 | 6321 - Fused Link 6321 |  | 103SEG453- Temp Link between Pole 544 & Pole 538 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 535 | 161 | 24581 | 85185 | 3.4655 | 0.0065498 | 1300 | 688499 | 2012/2013 | January-2013 | 1 | 2013
28600 | Jumper Off @ Link 1528 | 2013-01-26 09:38 | 2013-01-26 | 2013-01-26 14:45 | Calculated | 1526 | 1526 - Fused Link 1526 |  | 113SEG1526-1525 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 307 | 101 | 24581 | 20359 | 0.82824 | 0.0041089 | 663 | 135175 | 2012/2013 | January-2013 | 1 | 2013
28601 | L/V Neutral Fault | 2013-01-27 11:55 | 2013-01-27 | 2013-01-27 13:42 | Calculated | TF177 | TF177 - Transformer Fuse: TF177 |  | 102SEG1271-336 | Hangatiki East 102-01 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 3 | 24581 | 321 | 0.01306 | 0.00012205 | 15 | 1605 | 2012/2013 | January-2013 | 1 | 2013
28602 | Fuse Pulled Apart | 2013-01-27 14:44 | 2013-01-27 | 2013-01-27 17:08 | Calculated | TF3319 | TF3319 - Transformer Fuse 3319 |  | 124SEG475-440 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 1 | 24581 | 144 | 0.00586 | 4.0682e-05 | 100 | 14400 | 2012/2013 | January-2013 | 1 | 2013
28605 | Raise Tap | 2013-01-29 12:01 | 2013-01-29 | 2013-01-29 13:37 | Calculated | TF2335 | TF2335 - Transformer Fuse: TF2335 |  | 110SEG713 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 3 | 24581 | 288 | 0.01172 | 0.00012205 | 30 | 2880 | 2012/2013 | January-2013 | 1 | 2013
28606 | Old Age | 2013-01-29 19:25 | 2013-01-29 | 2013-01-29 19:50 | Calculated | TF7L8 | TF7L8 - Transformer Fuse: TF7L8 |  | 408SEG5736-5341 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 1 | 24581 | 25 | 0.00102 | 4.0682e-05 | 15 | 375 | 2012/2013 | January-2013 | 1 | 2013
28612 | Unknown | 2013-01-30 05:40 | 2013-01-30 | 2013-01-30 07:12 | Calculated | 5230 | 5230 - Fused Link 5230 |  | 403SEG5230 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 92 | 7 | 24581 | 644 | 0.0262 | 0.00028477 | 30 | 2759 | 2012/2013 | January-2013 | 1 | 2013
28613 | Refer 2013 / 33 Repalce Poles & Xarms / Deviate Line x 2 U/G Cable Sections | 2013-01-30 08:55 | 2013-01-30 | 2013-01-30 15:47 | Calculated | 1748 | 1748 - Circuit Breaker 1748 |  | 129SEG216T1-1748 | No Asset Group | Remote Rural F | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 362 | 6 | 24581 | 2172 | 0.08836 | 0.00024409 | 45 | 16290 | 2012/2013 | January-2013 | 1 | 2013
28615 | L/V Maintenance | 2013-01-31 09:01 | 2013-01-31 | 2013-01-31 10:44 | Calculated | TF2381 | TF2381 - Transformer Fuse: TF2381 |  | 129SEG434-426 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 103 | 3 | 24581 | 309 | 0.01257 | 0.00012205 | 15 | 1545 | 2012/2013 | January-2013 | 1 | 2013
28616 | Refer 2013 / 35 Remove H/V Fuses Tx 2511 & Install new Set @ T/O | 2013-01-31 09:07 | 2013-01-31 | 2013-01-31 14:09 | Calculated | 529 | 529 - Air Break Switch 529 |  | 109SEG2107-529 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 262 | 10 | 24581 | 2620 | 0.10659 | 0.00040682 | 72.5 | 18995 | 2012/2013 | January-2013 | 1 | 2013
28614 | Refer 2013 / 32 Replace Tx 20L50 | 2013-01-31 09:15 | 2013-01-31 | 2013-01-31 18:54 | Calculated | 6609 | 6609 - RTE Switch 6609 |  | 414SEG5788-6609 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 579 | 119 | 24581 | 68901 | 2.803 | 0.0048411 | 688.2353 | 398488 | 2012/2013 | January-2013 | 1 | 2013
28617 | Refer 2013 / 36 Replace Red Tagged Structure - Tx 1049 | 2013-01-31 09:36 | 2013-01-31 | 2013-01-31 16:54 | Calculated | 587 | 587 - Fused Link 587 |  | 109SEG587-2218 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 400 | 13 | 24581 | 5200 | 0.21155 | 0.00052886 | 100 | 39999 | 2012/2013 | January-2013 | 1 | 2013
28618 | Refer 2013 / 38 Disconnet Disused Section Of Line | 2013-01-31 10:04 | 2013-01-31 | 2013-01-31 13:03 | Calculated | 5919 | 5919 - Fused Link 5919 |  | 410SEG5919 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 179 | 4 | 24581 | 716 | 0.02913 | 0.00016273 | 27.5 | 4922 | 2012/2013 | January-2013 | 1 | 2013
28620 | Refer 2013 / 39 Install New T/O @ Pole 94/901/10 | 2013-02-01 10:03 | 2013-02-01 | 2013-02-01 13:47 | Calculated | 5447 | 5447 - Fused Link 5447 |  | 409SEG5447-5319 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 192 | 40 | 24580 | 6080 | 0.24736 | 0.0016273 | 377.6667 | 60245 | 2012/2013 | February-2013 | 2 | 2013
28621 | Bird in L/A @ Tx6F3 | 2013-02-02 15:08 | 2013-02-02 | 2013-02-02 19:26 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 258 | 33 | 24580 | 3516 | 0.14304 | 0.0013426 | 208.5 | 14285 | 2012/2013 | February-2013 | 2 | 2013
28622 | Unknown | 2013-02-02 21:45 | 2013-02-02 | 2013-02-02 23:50 | Calculated | TF6Q8 | TF6Q8 - Transformer Fuse: TF6Q8 |  | 426SEG5588-5583 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 2 | 24580 | 250 | 0.01017 | 8.1367e-05 | 10 | 1250 | 2012/2013 | February-2013 | 2 | 2013
28623 | Over Loaded | 2013-02-03 18:46 | 2013-02-03 | 2013-02-03 19:59 | Calculated | TF517 | TF517 - Transformer Fuse: TF517 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 1 | 24580 | 73 | 0.00297 | 4.0683e-05 | 13 | 949 | 2012/2013 | February-2013 | 2 | 2013
28624 | Duck | 2013-02-04 10:07 | 2013-02-04 | 2013-02-04 13:18 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 25 | 24580 | 4775 | 0.19426 | 0.0010171 | 271.4286 | 51842 | 2012/2013 | February-2013 | 2 | 2013
28625 | Unknown | 2013-02-04 10:51 | 2013-02-04 | 2013-02-04 11:54 | Calculated | 5245 | 5245 - Solid Link 5245 |  | 417SEG5245-5497 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 107 | 24580 | 6741 | 0.27425 | 0.0043531 | 590 | 37169 | 2012/2013 | February-2013 | 2 | 2013
28626 | Replace Stub Pole | 2013-02-04 11:54 | 2013-02-04 | 2013-02-04 12:37 | Calculated | TF528 | TF528 - Transformer Fuse: TF528 |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 43 | 1 | 24580 | 43 | 0.00175 | 4.0683e-05 | 7.5 | 322 | 2012/2013 | February-2013 | 2 | 2013
28627 | Duck | 2013-02-04 13:22 | 2013-02-04 | 2013-02-04 14:37 | Calculated | 5730 | 5730 - Fused Link 5730 |  | 416SEG5730-5676 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 14 | 24580 | 1050 | 0.04272 | 0.00056957 | 130 | 9750 | 2012/2013 | February-2013 | 2 | 2013
28628 | Tree Through Line | 2013-02-05 08:05 | 2013-02-05 | 2013-02-05 17:37 | Calculated | 5739 | 5739 - Sectionaliser with Bypass & Links 5739 |  | 421SEG5436-5434 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 572 | 2 | 24580 | 1144 | 0.04654 | 8.1367e-05 | 3 | 1716 | 2012/2013 | February-2013 | 2 | 2013
28629 | SWER Backfeed Refer 2013 / 41 Changing Poles & X/arms | 2013-02-05 08:36 | 2013-02-05 | 2013-02-05 16:16 | Calculated | 1717 | 1717 - Recloser with Bypass 1717 |  | 115SEG1717-1723 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 381 | 116 | 24580 | 14643 | 0.59573 | 0.0047193 | 860.5 | 108130 | 2012/2013 | February-2013 | 2 | 2013
28630 | Dead Bird @ Pole 4261223 | 2013-02-05 08:47 | 2013-02-05 | 2013-02-05 16:15 | Calculated | 5592 | 5592 - Fused Link 5592 |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 313 | 39 | 24580 | 8446 | 0.34361 | 0.0015867 | 343.5 | 72902 | 2012/2013 | February-2013 | 2 | 2013
28631 | Faulty Polymer @ Pole 56 | 2013-02-05 12:12 | 2013-02-05 | 2013-02-05 19:28 | Calculated | 5462J | 5462J - Incoming Link 5462J |  | 421SEG6554-5462RET | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLI | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 436 | 121 | 24580 | 52756 | 2.1463 | 0.0049227 | 967.5 | 421829 | 2012/2013 | February-2013 | 2 | 2013
28632 | Suspect H/V Cable Fault | 2013-02-05 14:10 | 2013-02-05 | 2013-02-05 15:46 | Calculated | TF1B25 | TF1B25 - Transformer Fuse: TF1B25 |  | 404SEGF1.16 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLX | Faulty Manufacture | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 35 | 24580 | 3360 | 0.1367 | 0.0014239 | 100 | 9599 | 2012/2013 | February-2013 | 2 | 2013
28633 | Unknown | 2013-02-05 14:32 | 2013-02-05 | 2013-02-05 17:37 | Calculated | TF7K4 | TF7K4 - Transformer Fuse: TF7K4 |  | 408SEG5620-5660 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 2 | 24580 | 370 | 0.01505 | 8.1367e-05 | 30 | 5550 | 2012/2013 | February-2013 | 2 | 2013
28634 | Suspect Cable Fault | 2013-02-05 21:05 | 2013-02-05 | 2013-02-07 14:10 | Calculated | 6338 | 6338 - Fused Link 6338 |  | 419SEG6338-6339 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 2465 | 39 | 24580 | 66834 | 2.719 | 0.0015867 | 1640 | 2846024 | 2012/2013 | February-2013 | 2 | 2013
28635 | Unknown | 2013-02-06 21:52 | 2013-02-06 | 2013-02-06 23:03 | Calculated | 5402 | 5402 - Sectionaliser with Bypass & Links 5402 |  | 409SEG5884-5403 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 71 | 21 | 24580 | 1491 | 0.06066 | 0.00085435 | 185.5 | 13170 | 2012/2013 | February-2013 | 2 | 2013
28636 | Faulty L/A @ Tx 11J2 | 2013-02-07 01:28 | 2013-02-07 | 2013-02-07 02:40 | Calculated | 5402 | 5402 - Sectionaliser with Bypass & Links 5402 |  | 409SEG5884-5403 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 72 | 21 | 24580 | 1512 | 0.06151 | 0.00085435 | 185.5 | 13356 | 2012/2013 | February-2013 | 2 | 2013
28637 | Refer 2013 / 42 Replace Poles & X/arms | 2013-02-07 09:05 | 2013-02-07 | 2013-02-07 16:04 | Calculated | 1713 | 1713 - Fused Link 1713 |  | 115SEG1713 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 419 | 7 | 24580 | 2933 | 0.11932 | 0.00028478 | 60 | 25140 | 2012/2013 | February-2013 | 2 | 2013
28638 | L/V Maintenance | 2013-02-07 10:10 | 2013-02-07 | 2013-02-07 15:38 | Calculated | TF1724 | TF1724 - Transformer Fuse: TF1724 |  | 116SEG1310-1781 | Piopio 116-03 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 328 | 5 | 24580 | 1640 | 0.06672 | 0.00020342 | 30 | 9840 | 2012/2013 | February-2013 | 2 | 2013
28639 | Unknown | 2013-02-07 10:54 | 2013-02-07 | 2013-02-07 11:48 | Calculated | TF5I12 | TF5I12 - Transformer Fuse: TF5I12 |  | 402SEG5798 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 54 | 1 | 24580 | 54 | 0.0022 | 4.0683e-05 | 5 | 270 | 2012/2013 | February-2013 | 2 | 2013
28640 | Broken Xarm @ Tx 62 | 2013-02-07 14:40 | 2013-02-07 | 2013-02-07 15:35 | Calculated | 508 | 508 - Air Break Switch 508 |  | 107SEG508-1798 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 16 | 24580 | 880 | 0.0358 | 0.00065094 | 75 | 4124 | 2012/2013 | February-2013 | 2 | 2013
28641 | Tree on Line | 2013-02-07 16:17 | 2013-02-07 | 2013-02-07 18:49 | Calculated | 5378 | 5378 - Recloser 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 152 | 60 | 24580 | 9120 | 0.37103 | 0.002441 | 383 | 58215 | 2012/2013 | February-2013 | 2 | 2013
28642 | Unknown | 2013-02-08 08:10 | 2013-02-08 | 2013-02-08 09:39 | Calculated | 5360 | 5360 - Sectionaliser with Bypass & Links 5360 |  | 402SEG5360-5267 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 89 | 12 | 24580 | 1068 | 0.04345 | 0.0004882 | 90 | 8010 | 2012/2013 | February-2013 | 2 | 2013
28643 | Fuse Fell Out | 2013-02-08 08:14 | 2013-02-08 | 2013-02-08 09:03 | Calculated | TF6J4 | TF6J4 - Transformer Fuse: TF6J4 |  | 402SEG5354 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 49 | 3 | 24580 | 147 | 0.00598 | 0.00012205 | 15 | 735 | 2012/2013 | February-2013 | 2 | 2013
28644 | Unknown | 2013-02-08 08:31 | 2013-02-08 | 2013-02-08 09:33 | Calculated | 266 | 266 - Fused Link 266 |  | 107SEG266 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 5 | 24580 | 310 | 0.01261 | 0.00020342 | 50 | 3099 | 2012/2013 | February-2013 | 2 | 2013
28645 | Refer 2013 / 43 Feeder Renewal Project | 2013-02-08 09:01 | 2013-02-08 | 2013-02-08 16:11 | Calculated | 549 | 549 - Load Break Switch 549 |  | 111SEG395-549 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 421 | 54 | 24580 | 22734 | 0.9249 | 0.0021969 | 528 | 222287 | 2012/2013 | February-2013 | 2 | 2013
28646 | Disconnet Gen Set, Recoonect Cable After Fault | 2013-02-08 16:10 | 2013-02-08 | 2013-02-08 17:15 | Calculated | 5773 | 5773 - Circuit Breaker 5773 |  | 419SEG5773-5998 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 20 | 39 | 24580 | 780 | 0.03173 | 0.0015867 | 1640 | 32799 | 2012/2013 | February-2013 | 2 | 2013
28647 | Bird | 2013-02-10 14:45 | 2013-02-10 | 2013-02-10 16:15 | Calculated | TF11G4 | TF11G4 - Transformer Fuse: TF11G4 |  | 403SEG5313-5541 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 90 | 5 | 24580 | 450 | 0.01831 | 0.00020342 | 15 | 1350 | 2012/2013 | February-2013 | 2 | 2013
28648 | Unknown | 2013-02-10 15:05 | 2013-02-10 | 2013-02-10 16:57 | Calculated | 5705 | 5705 - Fused Link 5705 |  | 415SEG6039-5704 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 7 | 24580 | 784 | 0.0319 | 0.00028478 | 50 | 5600 | 2012/2013 | February-2013 | 2 | 2013
28649 | Unknown | 2013-02-10 17:25 | 2013-02-10 | 2013-02-10 18:05 | Calculated | TF6J11 | TF6J11 - Transformer Fuse: TF6J11 |  | 402SEG5354 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 40 | 3 | 24580 | 120 | 0.00488 | 0.00012205 | 30 | 1200 | 2012/2013 | February-2013 | 2 | 2013
28650 | Bird | 2013-02-10 18:25 | 2013-02-10 | 2013-02-10 19:30 | Calculated | TF4056 | TF4056 - Transformer Fuse: TF4056 |  | 409SEG5599-5600 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 65 | 1 | 24580 | 65 | 0.00264 | 4.0683e-05 | 5 | 325 | 2012/2013 | February-2013 | 2 | 2013
28651 | Unknown | 2013-02-10 19:52 | 2013-02-10 | 2013-02-10 21:15 | Calculated | TF8E7 | TF8E7 - Transformer Fuse: TF8E7 |  | 413SEG5572-5579 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 83 | 1 | 24580 | 83 | 0.00338 | 4.0683e-05 | 3 | 249 | 2012/2013 | February-2013 | 2 | 2013
28652 | Unknown | 2013-02-10 20:31 | 2013-02-10 | 2013-02-10 21:00 | Calculated | TF1151 | TF1151 - Transformer Fuse: TF1151 |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 4 | 24580 | 116 | 0.00472 | 0.00016273 | 50 | 1450 | 2012/2013 | February-2013 | 2 | 2013
28654 | Tree On Line @ Tx 10J8 | 2013-02-11 08:35 | 2013-02-11 | 2013-02-11 09:50 | Calculated | 5623 | 5623 - Electronic Sectionaliser 5623 |  | 409SEG5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 15 | 24580 | 1125 | 0.04577 | 0.00061025 | 71.5 | 5362 | 2012/2013 | February-2013 | 2 | 2013
28655 | Fuse Pulled Apart | 2013-02-12 07:22 | 2013-02-12 | 2013-02-12 09:13 | Calculated | TF7J10 | TF7J10 - Transformer Fuse: TF7J10 |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 6 | 24580 | 666 | 0.0271 | 0.0002441 | 50 | 5549 | 2012/2013 | February-2013 | 2 | 2013
28656 | SWER Backfeed Report Leaning Pole 1250144 | 2013-02-12 08:48 | 2013-02-12 | 2013-02-12 15:37 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG569-564 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 168 | 24580 | 5160 | 0.20993 | 0.0068348 | 1182.1014 | 108187 | 2012/2013 | February-2013 | 2 | 2013
28659 | Refer 2013 / 44 Replace SWER Pole Off Kuratau/49 | 2013-02-12 10:02 | 2013-02-12 | 2013-02-12 12:35 | Calculated | 5897 | 5897 - Earth Working Link 5897 |  | 406SEG5897-5481 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 153 | 18 | 24580 | 2739 | 0.11143 | 0.0007323 | 115 | 17370 | 2012/2013 | February-2013 | 2 | 2013
28660 | Unknown | 2013-02-12 15:15 | 2013-02-12 | 2013-02-12 18:17 | Calculated | 1528 | 1528 - Fused Link 1528 |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 182 | 12 | 24580 | 2184 | 0.08885 | 0.0004882 | 58 | 10555 | 2012/2013 | February-2013 | 2 | 2013
28661 | Duck | 2013-02-13 07:02 | 2013-02-13 | 2013-02-13 08:05 | Calculated | TF21P1 | TF21P1 - Transformer Fuse: TF21P1 |  | 416SEG5780-6608 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 6 | 24580 | 378 | 0.01538 | 0.0002441 | 30 | 1890 | 2012/2013 | February-2013 | 2 | 2013
28662 | Bird | 2013-02-13 11:52 | 2013-02-13 | 2013-02-13 13:22 | Calculated | TF1892 | TF1892 - Transformer Fuse: TF1892 |  | 114SEG1100 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 90 | 3 | 24580 | 270 | 0.01098 | 0.00012205 | 15 | 1350 | 2012/2013 | February-2013 | 2 | 2013
28663 | TLC Hi-ab vs L/V | 2013-02-13 14:00 | 2013-02-13 | 2013-02-13 14:17 | Calculated | TF179 | TF179 - Transformer Fuse: TF179 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:FOLA | Accidental Contact, Damage or Interference by TLC Staff | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 6 | 24580 | 102 | 0.00415 | 0.0002441 | 50 | 849 | 2012/2013 | February-2013 | 2 | 2013
28664 | Refer 2013 / 46 Replace L/V Panel in Tx10S46 | 2013-02-14 07:57 | 2013-02-14 | 2013-02-14 16:37 | Calculated | 6193 | 6193 - Fused Link 6193 |  | 423SEG6196-5205 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 479 | 116 | 24580 | 32398 | 1.3181 | 0.0047193 | 750 | 284999 | 2012/2013 | February-2013 | 2 | 2013
28665 | Tripped - No Comms | 2013-02-14 16:37 | 2013-02-14 | 2013-02-14 16:55 | Calculated | 5198 | 5198 - Circuit Breaker 5198 |  | No Segment | 505-01 Turangi | Rural C | No Feeder |  |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 1100 | 24580 | 19800 | 0.80553 | 0.044752 | 5350 | 96299 | 2012/2013 | February-2013 | 2 | 2013
28667 | Broken L/V X/arm | 2013-02-15 09:29 | 2013-02-15 | 2013-02-15 11:22 | Calculated | TF1326 | TF1326 - Transformer Fuse: TF1326 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 5 | 24580 | 565 | 0.02299 | 0.00020342 | 25 | 2825 | 2012/2013 | February-2013 | 2 | 2013
28668 | Ducks | 2013-02-16 07:47 | 2013-02-16 | 2013-02-16 10:46 | Calculated | 5705 | 5705 - Fused Link 5705 |  | 415SEG6039-5704 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 7 | 24580 | 1253 | 0.05098 | 0.00028478 | 50 | 8950 | 2012/2013 | February-2013 | 2 | 2013
28669 | Unknown | 2013-02-16 12:15 | 2013-02-16 | 2013-02-16 14:48 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 153 | 1 | 24580 | 153 | 0.00622 | 4.0683e-05 | 5 | 765 | 2012/2013 | February-2013 | 2 | 2013
28670 | Unknown | 2013-02-16 12:39 | 2013-02-16 | 2013-02-16 15:00 | Calculated | TF517 | TF517 - Transformer Fuse: TF517 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 1 | 24580 | 141 | 0.00574 | 4.0683e-05 | 13 | 1833 | 2012/2013 | February-2013 | 2 | 2013
28671 | Unknown | 2013-02-16 16:03 | 2013-02-16 | 2013-02-16 17:00 | Calculated | TF1639 | TF1639 - Transformer Fuse: TF1639 |  | 113SEG1526-1525 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 2 | 24580 | 114 | 0.00464 | 8.1367e-05 | 15 | 855 | 2012/2013 | February-2013 | 2 | 2013
28672 | Unknown | 2013-02-17 06:35 | 2013-02-17 | 2013-02-17 07:42 | Calculated | TF3041 | TF3041 - Transformer Fuse: TF3041 |  | 101SEG261-519 | Caves 101-02 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 1 | 24580 | 67 | 0.00273 | 4.0683e-05 | 50 | 3350 | 2012/2013 | February-2013 | 2 | 2013
28673 | Refer 2013 / 51 Replace Poles | 2013-02-17 08:35 | 2013-02-17 | 2013-02-17 14:29 | Calculated | 361 | 361 - Air Break Switch 361 |  | 102SEG191-361 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 326 | 3 | 24580 | 978 | 0.03979 | 0.00012205 | 1300 | 423800 | 2012/2013 | February-2013 | 2 | 2013
28675 | Unknown | 2013-02-18 08:00 | 2013-02-18 | 2013-02-18 09:20 | Calculated | TF2485 | TF2485 - Transformer Fuse: TF2485 |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 5 | 24580 | 400 | 0.01627 | 0.00020342 | 30 | 2400 | 2012/2013 | February-2013 | 2 | 2013
28676 | Isolate for Fire Brigade | 2013-02-19 00:04 | 2013-02-19 | 2013-02-19 02:10 | Calculated | 5789 | 5789 - Fused Link 5789 |  | 409SEG5452-5789 | Southern 409-03 | Rural D | Southern | Manunui Zone Substation |  | Third Party (includeds unauthorised contractors) | Fire | 3PAR:EFIR:EFIB | Fire (Not Electrical) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 38 | 24580 | 4788 | 0.19479 | 0.001546 | 110 | 13859 | 2012/2013 | February-2013 | 2 | 2013
28677 | Unknown | 2013-02-19 08:33 | 2013-02-19 | 2013-02-19 10:04 | Calculated | TF3Q2 | TF3Q2 - Transformer Fuse: TF3Q2 |  | 124SEG5537-5324 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 3 | 24580 | 273 | 0.01111 | 0.00012205 | 15 | 1365 | 2012/2013 | February-2013 | 2 | 2013
28678 | Broken Tx Earth | 2013-02-19 12:29 | 2013-02-19 | 2013-02-19 13:06 | Calculated | TF1160 | TF1160 - Transformer Fuse: TF1160 |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 2 | 24580 | 74 | 0.00301 | 8.1367e-05 | 10 | 370 | 2012/2013 | February-2013 | 2 | 2013
28679 | Private Line L/V Fault | 2013-02-19 15:13 | 2013-02-19 | 2013-02-19 15:53 | Calculated | TF6J16 | TF6J16 - Transformer Fuse: TF6J16 |  | 402SEG5199-5115 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFPL | Fault on Private Line - Affecting Network | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 40 | 1 | 24580 | 40 | 0.00163 | 4.0683e-05 | 10 | 400 | 2012/2013 | February-2013 | 2 | 2013
28680 | Unknown | 2013-02-19 20:10 | 2013-02-19 | 2013-02-19 21:22 | Calculated | TF3Q5 | TF3Q5 - Transformer Fuse: TF3Q5 |  | 124SEG5537-5324 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 3 | 24580 | 216 | 0.00879 | 0.00012205 | 10 | 719 | 2012/2013 | February-2013 | 2 | 2013
28681 | Refer 2013 / 53 Replace L/V Panel in Tx 10S31 | 2013-02-20 08:04 | 2013-02-20 | 2013-02-20 15:07 | Calculated | 6186 | 6186 - Fused Link 6186 |  | 405SEG6187-6186 | Hirangi 405-02 | Rural C | Hirangi | Awamate Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24580 |  | 0 | 0 |  |  | 2012/2013 | February-2013 | 2 | 2013
28682 | Refer 2013 / 55 Fit New T/O X/arm & DDO's To Pole 221/7/15 | 2013-02-20 09:31 | 2013-02-20 | 2013-02-20 11:05 | Calculated | 265 | 265 - Sectionaliser with Bypass & Links 265 |  | 107SEG262-176 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 13 | 24580 | 1222 | 0.04972 | 0.00052889 | 130 | 12220 | 2012/2013 | February-2013 | 2 | 2013
28683 | Possum x 2 | 2013-02-20 09:58 | 2013-02-20 | 2013-02-20 11:53 | Calculated | TF1512 | TF1512 - Transformer Fuse: TF1512 |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 1 | 24580 | 115 | 0.00468 | 4.0683e-05 | 25 | 2875 | 2012/2013 | February-2013 | 2 | 2013
28684 | Raise L/V After Fire | 2013-02-20 10:52 | 2013-02-20 | 2013-02-20 15:10 | Calculated | TF976 | TF976 - Transformer Fuse: TF976 |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWG1 | Switch-gear Failure Low Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 1 | 24580 | 163 | 0.00663 | 4.0683e-05 | 15 | 2445 | 2012/2013 | February-2013 | 2 | 2013
28685 | Unknown | 2013-02-20 12:31 | 2013-02-20 | 2013-02-20 14:44 | Calculated | TF1892 | TF1892 - Transformer Fuse: TF1892 |  | 114SEG1100 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 133 | 3 | 24580 | 399 | 0.01623 | 0.00012205 | 15 | 1995 | 2012/2013 | February-2013 | 2 | 2013
28686 | Starling | 2013-02-20 16:58 | 2013-02-20 | 2013-02-20 18:08 | Calculated | TF14N02 | TF14N02 - Transformer Fuse: TF14N02 |  | 609SEG5158-5159 | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 70 | 2 | 24580 | 140 | 0.0057 | 8.1367e-05 | 15 | 1050 | 2012/2013 | February-2013 | 2 | 2013
28687 | Broken L/V Neutral | 2013-02-20 20:50 | 2013-02-20 | 2013-02-20 22:17 | Calculated | TF251 | TF251 - Transformer Fuse: TF251 |  | 109SEG345-348 | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 3 | 24580 | 261 | 0.01062 | 0.00012205 | 25 | 2174 | 2012/2013 | February-2013 | 2 | 2013
28688 | L/V Maintenance | 2013-02-21 09:35 | 2013-02-21 | 2013-02-21 16:44 | Calculated | TF2176 | TF2176 - Transformer Fuse: TF2176 |  | 128SEG REG3-2095 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 429 | 13 | 24580 | 5577 | 0.22689 | 0.00052889 | 15 | 6434 | 2012/2013 | February-2013 | 2 | 2013
28689 | Refer 2013 / 57 Isolation For Tree Cutters / Trimmers | 2013-02-22 09:05 | 2013-02-22 | 2013-02-22 16:14 | Calculated | 5932 | 5932 - Earth Working Link 5932 |  | 403SEG5932-5649 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 429 | 8 | 24580 | 3432 | 0.13963 | 0.00032547 | 55 | 23595 | 2012/2013 | February-2013 | 2 | 2013
28690 | Refer 2013 / 58 Relocate Tx 10L1 | 2013-02-22 09:36 | 2013-02-22 | 2013-02-22 13:28 | Calculated | 5319 | 5319 - Fused Link 5319 |  | 409SEG5319-5114 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 232 | 22 | 24580 | 5104 | 0.20765 | 0.00089504 | 226 | 52432 | 2012/2013 | February-2013 | 2 | 2013
28691 | L/V Maintenance | 2013-02-22 10:17 | 2013-02-22 | 2013-02-22 13:58 | Calculated | TF2176 | TF2176 - Transformer Fuse: TF2176 |  | 128SEG REG3-2095 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 13 | 24580 | 2873 | 0.11688 | 0.00052889 | 15 | 3314 | 2012/2013 | February-2013 | 2 | 2013
28692 | Bird @ Tx 6K2 | 2013-02-22 11:31 | 2013-02-22 | 2013-02-22 13:39 | Calculated | 5370 | 5370 - Recloser with Bypass & Links 5370 |  | 402SEG5370-5199 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 78 | 24580 | 9984 | 0.40618 | 0.0031733 | 590 | 75520 | 2012/2013 | February-2013 | 2 | 2013
28693 | L/V Fault | 2013-02-22 12:13 | 2013-02-22 | 2013-02-22 12:55 | Calculated | TF3050 | TF3050 - Transformer Fuse: TF3050 |  | 111SEG322-127 | Maihiihi 111-02 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 2 | 24580 | 84 | 0.00342 | 8.1367e-05 | 30 | 1260 | 2012/2013 | February-2013 | 2 | 2013
28694 | Exposed Earth Mat @ Tx 2q6 | 2013-02-22 14:11 | 2013-02-22 | 2013-02-22 15:10 | Calculated | 1283 | 1283 - Sectionaliser with Bypass & Links 1283 |  | 124SEG1283 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 3 | 24580 | 177 | 0.0072 | 0.00012205 | 38 | 2242 | 2012/2013 | February-2013 | 2 | 2013
28695 | Refer 2013 / 65 Replace Poles | 2013-02-24 08:54 | 2013-02-24 | 2013-02-24 14:08 | Calculated | 191 | 191 - Air Break Switch 191 |  | 102SEG191-361 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 314 | 3 | 24580 | 942 | 0.03832 | 0.00012205 | 1300 | 408200 | 2012/2013 | February-2013 | 2 | 2013
28696 | Tree vs Line - Fire | 2013-02-24 18:30 | 2013-02-24 | 2013-02-25 14:39 | Calculated | 5668 | 5668 - Fused Link 5668 |  | 410SEG5668 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1209 | 13 | 24580 | 15717 | 0.63942 | 0.00052889 | 60 | 72540 | 2012/2013 | February-2013 | 2 | 2013
28697 | Bird | 2013-02-25 08:41 | 2013-02-25 | 2013-02-25 10:28 | Calculated | TF07Q15 | TF07Q15 - Transformer Fuse: TF07Q15 |  | 426SEG5359-5237 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 107 | 1 | 24580 | 107 | 0.00435 | 4.0683e-05 | 15 | 1605 | 2012/2013 | February-2013 | 2 | 2013
28698 | Refer 2013 / 59 Changing Poles & X/arms | 2013-02-25 08:53 | 2013-02-25 | 2013-02-25 14:26 | Calculated | 361 | 361 - Air Break Switch 361 |  | 102SEG191-361 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 9 | 24580 | 2538 | 0.10325 | 0.00036615 | 75 | 21149 | 2012/2013 | February-2013 | 2 | 2013
28699 | Unknown | 2013-02-25 19:33 | 2013-02-25 | 2013-02-25 22:19 | Calculated | TF7L8 | TF7L8 - Transformer Fuse: TF7L8 |  | 408SEG5736-5341 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 1 | 24580 | 166 | 0.00675 | 4.0683e-05 | 15 | 2490 | 2012/2013 | February-2013 | 2 | 2013
28700 | Ducks | 2013-02-26 07:47 | 2013-02-26 | 2013-02-26 08:25 | Calculated | 5705 | 5705 - Fused Link 5705 |  | 415SEG6039-5704 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 7 | 24580 | 266 | 0.01082 | 0.00028478 | 55 | 2090 | 2012/2013 | February-2013 | 2 | 2013
28703 | Fuse Fell out - Vibration | 2013-02-26 20:23 | 2013-02-26 | 2013-02-26 20:58 | Calculated | TF7L8 | TF7L8 - Transformer Fuse: TF7L8 |  | 408SEG5736-5341 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 1 | 24580 | 35 | 0.00142 | 4.0683e-05 | 15 | 525 | 2012/2013 | February-2013 | 2 | 2013
28704 | Magpie | 2013-02-27 08:04 | 2013-02-27 | 2013-02-27 09:45 | Calculated | TF7Q10 | TF7Q10 - Transformer Fuse: TF7Q10 |  | 426SEG5526-5359 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 3 | 24580 | 303 | 0.01233 | 0.00012205 | 15 | 1515 | 2012/2013 | February-2013 | 2 | 2013
28707 | Telecom vs H/V | 2013-02-27 17:44 | 2013-02-27 | 2013-02-27 17:50 | Calculated | 307 | 307 - Air Break Switch 307 |  | 112SEG307-314 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 421 | 24580 | 2526 | 0.10277 | 0.017128 | 2838 | 17027 | 2012/2013 | February-2013 | 2 | 2013
28709 | Fuse Pulled Apart | 2013-02-28 07:18 | 2013-02-28 | 2013-02-28 08:26 | Calculated | TF11J04 | TF11J04 - Transformer Fuse: TF11J04 |  | 409SEG5402-5389 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 68 | 1 | 24580 | 68 | 0.00277 | 4.0683e-05 | 7.5 | 510 | 2012/2013 | February-2013 | 2 | 2013
28710 | Refer 2013 / 62 Replace Pole 1242241 | 2013-02-28 08:35 | 2013-02-28 | 2013-02-28 15:08 | Calculated | 1748 | 1748 - Circuit Breaker 1748 |  | 129SEG216T1-1748 | No Asset Group | Remote Rural F | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 255 | 6 | 24580 | 1530 | 0.06225 | 0.0002441 | 45 | 11475 | 2012/2013 | February-2013 | 2 | 2013
28712 | Upgrade Earth Mat | 2013-02-28 10:34 | 2013-02-28 | 2013-02-28 12:41 | Calculated | TF7E1 | TF7E1 - Transformer Fuse: TF7E1 |  | 413SEG5287-5572 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 127 | 3 | 24580 | 381 | 0.0155 | 0.00012205 | 15 | 1905 | 2012/2013 | February-2013 | 2 | 2013
28714 | Faulty Insulators | 2013-03-01 11:52 | 2013-03-01 | 2013-03-01 14:39 | Calculated | 1615 | 1615 - Sectionaliser with Bypass & Links 1615 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 167 | 17 | 24574 | 2839 | 0.11553 | 0.00069179 | 135 | 22545 | 2012/2013 | March-2013 | 3 | 2013
28715 | Unknown | 2013-03-01 14:54 | 2013-03-01 | 2013-03-01 17:28 | Calculated | TF517 | TF517 - Transformer Fuse: TF517 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 1 | 24574 | 154 | 0.00627 | 4.0693e-05 | 13 | 2002 | 2012/2013 | March-2013 | 3 | 2013
28717 | Bird | 2013-03-02 09:15 | 2013-03-02 | 2013-03-02 12:24 | Calculated | TF517 | TF517 - Transformer Fuse: TF517 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 189 | 1 | 24574 | 189 | 0.00769 | 4.0693e-05 | 13 | 2457 | 2012/2013 | March-2013 | 3 | 2013
28716 | Tree Through Line | 2013-03-02 09:29 | 2013-03-02 | 2013-03-02 12:11 | Calculated | TF3024 | TF3024 - Transformer Fuse: TF3024 |  | 101SEG526 | Caves 101-03 | Urban A | Caves | Hangatiki Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 1 | 24574 | 162 | 0.00659 | 4.0693e-05 | 15 | 2430 | 2012/2013 | March-2013 | 3 | 2013
28718 | Fuse Pulled Apart | 2013-03-03 07:00 | 2013-03-03 | 2013-03-03 08:50 | Calculated | TF2379 | TF2379 - Transformer Fuse: TF2379 |  | 122SEG562 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 2 | 24574 | 220 | 0.00895 | 8.1387e-05 | 25 | 2750 | 2012/2013 | March-2013 | 3 | 2013
28719 | Unknown | 2013-03-03 16:24 | 2013-03-03 | 2013-03-03 18:28 | Calculated | 402 | 402 - Fused Link 402 |  | 129SEG402-725 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 43 | 24574 | 5332 | 0.21698 | 0.0017498 | 615 | 76259 | 2012/2013 | March-2013 | 3 | 2013
28720 | Unknown O/C | 2013-03-04 06:39 | 2013-03-04 | 2013-03-04 06:54 | Calculated | 6005 | 6005 - Recloser 6005 |  | 610SEG6005-6004 | 516-01 Transpower National Park | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 1553 | 24574 | 23295 | 0.94795 | 0.063197 | 8286 | 124289 | 2012/2013 | March-2013 | 3 | 2013
28721 | Refer 2013 / 69 Replacing Poles & X/arms | 2013-03-04 09:02 | 2013-03-04 | 2013-03-04 16:44 | Calculated | 554 | 554 - Air Break Switch 554 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 462 | 15 | 24574 | 6930 | 0.28201 | 0.0006104 | 105 | 48510 | 2012/2013 | March-2013 | 3 | 2013
28722 | Refer 2013 / 70 Fit 3rd DDO @ Pole 24 For New Extension & Tx 1913 | 2013-03-04 09:33 | 2013-03-04 | 2013-03-04 11:29 | Calculated | 1781 | 1781 - Load Break Switch |  | 113SEG1319-1781 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 70 | 19 | 24574 | 1330 | 0.05412 | 0.00077317 | 190 | 13299 | 2012/2013 | March-2013 | 3 | 2013
28724 | Refer 2013 / 73 Changing Poles - Feeder Renewal Project | 2013-03-05 08:44 | 2013-03-05 | 2013-03-05 15:48 | Calculated | 652 | 652 - Load Break Switch 652 |  | 119SEG653-652 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 341 | 29 | 24574 | 9889 | 0.40242 | 0.0011801 | 205 | 69905 | 2012/2013 | March-2013 | 3 | 2013
28723 | Refer 2013 / 72 Replacing Poles & X/arms | 2013-03-05 09:05 | 2013-03-05 | 2013-03-05 15:34 | Calculated | 554 | 554 - Air Break Switch 554 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 389 | 15 | 24574 | 5835 | 0.23745 | 0.0006104 | 105 | 40845 | 2012/2013 | March-2013 | 3 | 2013
28725 | Unknown | 2013-03-05 09:30 | 2013-03-05 | 2013-03-05 10:39 | Calculated | TF7Q8 | TF7Q8 - Transformer Fuse: TF7Q8 |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 2 | 24574 | 138 | 0.00562 | 8.1387e-05 | 15 | 1035 | 2012/2013 | March-2013 | 3 | 2013
28726 | Unknown | 2013-03-07 06:07 | 2013-03-07 | 2013-03-07 06:14 | Calculated | 5152 | 5152 - Circuit Breaker 5152 |  | 514SEG5152 | No Asset Group | Remote Rural F | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24574 |  | 0 | 0 |  |  | 2012/2013 | March-2013 | 3 | 2013
28727 | Unknown | 2013-03-07 08:24 | 2013-03-07 | 2013-03-07 09:47 | Calculated | 5266 | 5266 - Recloser 5266 |  | 413SEG5260-5266 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 83 | 19 | 24574 | 1577 | 0.06417 | 0.00077317 | 110 | 9130 | 2012/2013 | March-2013 | 3 | 2013
28728 | Scheduled Maintenance | 2013-03-07 09:03 | 2013-03-07 | 2013-03-07 15:37 | Calculated | TF2155 | TF2155 - Transformer Fuse: TF2155 |  | 128SEG2083 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 394 | 61 | 24574 | 24034 | 0.97803 | 0.0024823 | 200 | 78799 | 2012/2013 | March-2013 | 3 | 2013
28729 | Refer 2013 / 75 Changing Poles - Feeder Renewal Project | 2013-03-07 09:40 | 2013-03-07 | 2013-03-07 15:43 | Calculated | 652 | 652 - Load Break Switch 652 |  | 119SEG653-652 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 291 | 26 | 24574 | 7566 | 0.30789 | 0.001058 | 195 | 56744 | 2012/2013 | March-2013 | 3 | 2013
28730 | Check All Connections | 2013-03-07 13:19 | 2013-03-07 | 2013-03-07 13:57 | Calculated | TF12K10 | TF12K10 - Transformer Fuse: TF12K10 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 3 | 24574 | 114 | 0.00464 | 0.00012208 | 7.5 | 285 | 2012/2013 | March-2013 | 3 | 2013
28731 | Refer 2013 / 78 Pole Replacements | 2013-03-08 08:36 | 2013-03-08 | 2013-03-08 15:40 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG6617-5949 | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 424 | 2 | 24574 | 848 | 0.03451 | 8.1387e-05 | 65 | 27560 | 2012/2013 | March-2013 | 3 | 2013
28732 | Private Line Fault - Line Low | 2013-03-08 12:47 | 2013-03-08 | 2013-03-08 14:58 | Calculated | TF3I4 | TF3I4 - Transformer Fuse: TF3I4 |  | 421SEG5462-5364 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFPL | Fault on Private Line - Affecting Network | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 1 | 24574 | 131 | 0.00533 | 4.0693e-05 | 15 | 1965 | 2012/2013 | March-2013 | 3 | 2013
28733 | Wind - L/V Clash | 2013-03-09 10:30 | 2013-03-09 | 2013-03-09 11:37 | Calculated | TF1203 | TF1203 - Transformer Fuse: TF1203 |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 3 | 24574 | 201 | 0.00818 | 0.00012208 | 15 | 1005 | 2012/2013 | March-2013 | 3 | 2013
28734 | Wind | 2013-03-09 13:49 | 2013-03-09 | 2013-03-09 16:06 | Calculated | TF3082 | TF3082 - Transformer Fuse: TF3082 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 5 | 24574 | 685 | 0.02787 | 0.00020347 | 60 | 8220 | 2012/2013 | March-2013 | 3 | 2013
28735 | Bird | 2013-03-09 17:47 | 2013-03-09 | 2013-03-09 18:34 | Calculated | 2061 | 2061 - Fused Link 2061 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 2 | 24574 | 94 | 0.00383 | 8.1387e-05 | 45 | 2115 | 2012/2013 | March-2013 | 3 | 2013
28736 | Bird | 2013-03-10 11:56 | 2013-03-10 | 2013-03-10 12:39 | Calculated | TF10K34 | TF10K34 - Transformer Fuse: TF10K34 |  | 409SEG5447-5319 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 43 | 3 | 24574 | 129 | 0.00525 | 0.00012208 | 15 | 645 | 2012/2013 | March-2013 | 3 | 2013
28737 | SWER Backfeed Refer / 80 Replace Faulty Sect 1322 | 2013-03-11 09:29 | 2013-03-11 | 2013-03-11 13:37 | Calculated | 1315 | 1315 - Sectionaliser 1315 |  | 117SEG1315-1326 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 95 | 39 | 24574 | 2392 | 0.09734 | 0.001587 | 243.5 | 14823 | 2012/2013 | March-2013 | 3 | 2013
28738 | Bird | 2013-03-11 10:13 | 2013-03-11 | 2013-03-11 11:04 | Calculated | TF07R10 | TF07R10 - Transformer Fuse: TF7R10 |  | 426SEG5110-5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 2 | 24574 | 102 | 0.00415 | 8.1387e-05 | 7.5 | 382 | 2012/2013 | March-2013 | 3 | 2013
28739 | Replace Tx | 2013-03-11 11:01 | 2013-03-11 | 2013-03-11 13:01 | Calculated | TF2134 | TF2134 - Transformer Fuse: TF2134 |  | 128SEG1623-1540 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 120 | 3 | 24574 | 360 | 0.01465 | 0.00012208 | 15 | 1800 | 2012/2013 | March-2013 | 3 | 2013
28740 | Replace Tx | 2013-03-11 11:34 | 2013-03-11 | 2013-03-11 13:25 | Calculated | TF1254 | TF1254 - Transformer Fuse: TF1254 |  | 128SEG1540 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 111 | 1 | 24574 | 111 | 0.00452 | 4.0693e-05 | 0 | 0 | 2012/2013 | March-2013 | 3 | 2013
28741 | Replace Tx | 2013-03-11 13:27 | 2013-03-11 | 2013-03-11 15:24 | Calculated | TF2133 | TF2133 - Transformer Fuse: TF2133 |  | 128SEG1623-1540 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 2 | 24574 | 234 | 0.00952 | 8.1387e-05 | 15 | 1755 | 2012/2013 | March-2013 | 3 | 2013
28742 | Wind - L/V Clash | 2013-03-11 20:25 | 2013-03-11 | 2013-03-11 21:32 | Calculated | TF454 | TF454 - Transformer Fuse: TF454 |  | 111SEG1148 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 3 | 24574 | 201 | 0.00818 | 0.00012208 | 50 | 3349 | 2012/2013 | March-2013 | 3 | 2013
28743 | Refer 2013 / 81 Identify Cable & Upgrade L/V Panel in Tx 10S36 | 2013-03-12 08:07 | 2013-03-12 | 2013-03-12 20:06 | Calculated | 6189 | 6189 - Load Break Switch 6189 |  | 423SEG6188-6187 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 668 | 325 | 24574 | 112089 | 4.5613 | 0.013225 | 1300 | 413149 | 2012/2013 | March-2013 | 3 | 2013
28744 | SWER Backfeed Refer 2013 / 82 Replace H/V Fuses Tx 7L8 | 2013-03-12 08:22 | 2013-03-12 | 2013-03-12 11:35 | Calculated | 5218 | 5218 - Recloser with Bypass 5218 |  | 408SEG5275-5218 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 129 | 86 | 24574 | 2154 | 0.08765 | 0.0034996 | 613 | 17718 | 2012/2013 | March-2013 | 3 | 2013
28745 | Refer 2013 / 83 Repalce Pole (Tx 5L2) & Lower L/V For Tree Work | 2013-03-12 09:00 | 2013-03-12 | 2013-03-12 16:07 | Calculated | 5267 | 5267 - Fused Link 5267 |  | 421SEG5320-5267 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 408 | 12 | 24574 | 4896 | 0.19923 | 0.00048832 | 90 | 36720 | 2012/2013 | March-2013 | 3 | 2013
28746 | Refer 2013 / 85 Install Propl Pole Between Poles 1241263 & 64 | 2013-03-12 10:03 | 2013-03-12 | 2013-03-12 13:22 | Calculated | 480 | 480 - Air Break Switch 480 |  | 120SEG482-480 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 199 | 10 | 24574 | 1990 | 0.08098 | 0.00040693 | 135 | 26865 | 2012/2013 | March-2013 | 3 | 2013
28747 | Tree vs Lines (Contractor) | 2013-03-12 15:04 | 2013-03-12 | 2013-03-12 16:41 | Calculated | 1313 | 1313 - Fused Link 1313 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 457 | 24574 | 20158 | 0.8203 | 0.018597 | 3056 | 133007 | 2012/2013 | March-2013 | 3 | 2013
28748 | Unknown | 2013-03-12 19:19 | 2013-03-12 | 2013-03-12 20:13 | Calculated | TF11J04 | TF11J04 - Transformer Fuse: TF11J04 |  | 409SEG5402-5389 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 54 | 1 | 24574 | 54 | 0.0022 | 4.0693e-05 | 7.5 | 405 | 2012/2013 | March-2013 | 3 | 2013
28749 | Vehicle vs L/V Pole | 2013-03-13 00:21 | 2013-03-13 | 2013-03-13 00:58 | Calculated | TF7 | TF7 - Transformer Fuse: TF7 |  | 107SEG221-299 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 60 | 24574 | 2220 | 0.09034 | 0.0024416 | 200 | 7399 | 2012/2013 | March-2013 | 3 | 2013
28750 | Unknown E/F | 2013-03-13 05:39 | 2013-03-13 | 2013-03-13 05:46 | Calculated | 788 | 788 - Circuit Breaker 788 |  | 302SEG147-788 | Taharoa B 302-02 | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 320 | 24574 | 960 | 0.03907 | 0.013022 | 2466 | 7397 | 2012/2013 | March-2013 | 3 | 2013
28751 | Unknown | 2013-03-13 07:13 | 2013-03-13 | 2013-03-13 07:55 | Calculated | TF230 | TF230 - Transformer Fuse: TF230 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 6 | 24574 | 252 | 0.01025 | 0.00024416 | 30 | 1260 | 2012/2013 | March-2013 | 3 | 2013
28752 | Unknown | 2013-03-14 07:03 | 2013-03-14 | 2013-03-14 17:34 | Calculated | 1616 | 1616 - Sectionaliser with Bypass & Links 1616 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 631 | 42 | 24574 | 15478 | 0.62985 | 0.0017091 | 325 | 124515 | 2012/2013 | March-2013 | 3 | 2013
28754 | Replace Red Tagged L/V Pole | 2013-03-14 09:36 | 2013-03-14 | 2013-03-14 17:57 | Calculated | TF324 | TF324 - Transformer Fuse: TF324 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 501 | 7 | 24574 | 3507 | 0.14271 | 0.00028485 | 30 | 15029 | 2012/2013 | March-2013 | 3 | 2013
28755 | Upgrade Tx | 2013-03-14 11:58 | 2013-03-14 | 2013-03-14 15:35 | Calculated | TF5L2 | TF5L2 - Transformer Fuse: TF5L2 |  | 402SEG5360-5267 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 217 | 3 | 24574 | 651 | 0.02649 | 0.00012208 | 15 | 3255 | 2012/2013 | March-2013 | 3 | 2013
28756 | Unknown | 2013-03-14 18:13 | 2013-03-14 | 2013-03-14 18:34 | Calculated | TF4056 | TF4056 - Transformer Fuse: TF4056 |  | 409SEG5599-5600 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 21 | 1 | 24574 | 21 | 0.00085 | 4.0693e-05 | 5 | 105 | 2012/2013 | March-2013 | 3 | 2013
28759 | Refer 2013 / 88 Repalce Rotten Wire Poles 245 - 249 | 2013-03-15 08:36 | 2013-03-15 | 2013-03-15 15:35 | Calculated | 2097 | 2097 - Fused Link 2097 |  | 128SEG2095-1635 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 385 | 189 | 24574 | 14328 | 0.58306 | 0.0076911 | 1211 | 71761 | 2012/2013 | March-2013 | 3 | 2013
28757 | L/V Line Down | 2013-03-15 09:00 | 2013-03-15 | 2013-03-15 10:41 | Calculated | T857 | T857 - 3 Phase : 30.00 kVA : polemnt |  | 121SEG753-439 | Huirimu 121-01 | Rural D | Huirimu | Arohena Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 5 | 24574 | 505 | 0.02055 | 0.00020347 | 30 | 3030 | 2012/2013 | March-2013 | 3 | 2013
28761 | Refer 2013 / 90 Pole Replacements | 2013-03-15 09:11 | 2013-03-15 | 2013-03-15 15:17 | Calculated | 5949 | 5949 - Recloser with Bypass 5949 |  | 415SEG6617-5949 | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 366 | 5 | 24574 | 1554 | 0.06324 | 0.00020347 | 115 | 37489 | 2012/2013 | March-2013 | 3 | 2013
28762 | Refer 2013 / 89 Repalce Pole 57/7 | 2013-03-15 09:32 | 2013-03-15 | 2013-03-15 12:29 | Calculated | 5311 | 5311 - Air Break Switch 5311 |  | 409SEG5311-5452 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 177 | 95 | 24574 | 16815 | 0.68426 | 0.0038659 | 435 | 76994 | 2012/2013 | March-2013 | 3 | 2013
28763 | Reconfigure L/V Jumpers | 2013-03-15 09:35 | 2013-03-15 | 2013-03-15 11:35 | Calculated | TF4056 | TF4056 - Transformer Fuse: TF4056 |  | 409SEG5599-5600 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 120 | 1 | 24574 | 120 | 0.00488 | 4.0693e-05 | 5 | 600 | 2012/2013 | March-2013 | 3 | 2013
28764 | Duck | 2013-03-16 19:22 | 2013-03-16 | 2013-03-16 20:29 | Calculated | 458 | 458 - Fused Link 458 |  | 129SEG458 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 7 | 24574 | 469 | 0.01909 | 0.00028485 | 80 | 5360 | 2012/2013 | March-2013 | 3 | 2013
28765 | Fautly L/V Jumper | 2013-03-17 14:16 | 2013-03-17 | 2013-03-17 15:09 | Calculated | TF4036 | TF4036 - Transformer Fuse: TF4036 |  | 402SEG5596-5930 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 53 | 1 | 24574 | 53 | 0.00216 | 4.0693e-05 | 15 | 795 | 2012/2013 | March-2013 | 3 | 2013
28766 | Unknown | 2013-03-17 21:09 | 2013-03-17 | 2013-03-17 23:09 | Calculated | 1230 | 1230 - Fused Link 1230 |  | 103SEG598-714 | Benneydale 103-07 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 27 | 24574 | 3240 | 0.13185 | 0.0010987 | 115 | 13799 | 2012/2013 | March-2013 | 3 | 2013
28767 | Tree Through Line | 2013-03-17 22:14 | 2013-03-17 | 2013-03-18 09:49 | Calculated | 5851 | 5851 - Sectionaliser with Bypass & Links 5851 |  | 421SEG5434-5851 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 695 | 41 | 24574 | 16509 | 0.67181 | 0.0016684 | 285.5 | 115212 | 2012/2013 | March-2013 | 3 | 2013
28768 | Branch On L/V | 2013-03-18 08:42 | 2013-03-18 | 2013-03-18 12:13 | Calculated | TF1838 | TF1838 - Transformer Fuse: TF1838 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 211 | 2 | 24574 | 422 | 0.01717 | 8.1387e-05 | 15 | 3165 | 2012/2013 | March-2013 | 3 | 2013
28769 | Refer 2013 / 91 Straighten L/V Pole & Replace Double X/arm | 2013-03-18 09:04 | 2013-03-18 | 2013-03-18 12:58 | Calculated | 1.18 | 1.18 - Fused Link 1.18 |  | 404SEGF1.18 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 234 | 77 | 24574 | 18018 | 0.73321 | 0.0031334 | 250 | 58499 | 2012/2013 | March-2013 | 3 | 2013
28770 | Faulty Tx | 2013-03-18 16:29 | 2013-03-18 | 2013-03-19 14:35 | Calculated | TF1276 | TF1276 - Transformer Fuse: TF1276 |  | 123SEG469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1326 | 1 | 24574 | 1326 | 0.05396 | 4.0693e-05 | 10 | 13260 | 2012/2013 | March-2013 | 3 | 2013
28771 | Sparking ABS 1702 | 2013-03-18 19:58 | 2013-03-18 | 2013-03-18 20:01 | Calculated | 792 | 792 - Circuit Breaker 792 |  | No Segment | 207-01 Wairere Falls | Rural D | No Feeder |  |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 2043 | 24574 | 6129 | 0.24941 | 0.083137 | 14507 | 43520 | 2012/2013 | March-2013 | 3 | 2013
28772 | Jumper Off @ Tx 850 | 2013-03-19 09:41 | 2013-03-19 | 2013-03-19 10:25 | Calculated | 717 | 717 - Fused Link 717 |  | 116SEG717 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 5 | 24574 | 220 | 0.00895 | 0.00020347 | 35 | 1540 | 2012/2013 | March-2013 | 3 | 2013
28773 | Bolt Down Tx | 2013-03-19 10:27 | 2013-03-19 | 2013-03-19 10:57 | Calculated | TF7D10 | TF7D10 - Transformer Fuse: TF7D10 |  | 413SEG5287-5572 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 30 | 1 | 24574 | 30 | 0.00122 | 4.0693e-05 | 5 | 150 | 2012/2013 | March-2013 | 3 | 2013
28774 | Bolt Down Tx | 2013-03-19 12:50 | 2013-03-19 | 2013-03-19 13:19 | Calculated | TF8F3 | TF8F3 - Transformer Fuse: TF8F3 |  | 413SEG5508 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 29 | 1 | 24574 | 29 | 0.00118 | 4.0693e-05 | 5 | 145 | 2012/2013 | March-2013 | 3 | 2013
28775 | Faulty L/A | 2013-03-20 07:18 | 2013-03-20 | 2013-03-20 13:13 | Calculated | TF1927A | TF1927A - Transformer Fuse: TF1927A |  | 115SEG682-1701 | Mokauiti 115-01 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 355 | 1 | 24574 | 355 | 0.01445 | 4.0693e-05 | 300 | 106500 | 2012/2013 | March-2013 | 3 | 2013
28776 | Refer 2013 / 97 Re-alignment Project | 2013-03-20 09:18 | 2013-03-20 | 2013-03-20 14:31 | Calculated | 5539 | 5539 - Fused Link 5539 |  | 422SEG5539 | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 313 | 5 | 24574 | 1565 | 0.06369 | 0.00020347 | 37.5 | 11737 | 2012/2013 | March-2013 | 3 | 2013
28778 | Unknown | 2013-03-20 13:53 | 2013-03-20 | 2013-03-20 14:33 | Calculated | TF1B8 | TF1B8 - Transformer Fuse: TF1B8 |  | 404SEGF1.27 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 1 | 24574 | 40 | 0.00163 | 4.0693e-05 | 10 | 400 | 2012/2013 | March-2013 | 3 | 2013
28779 | Fuse Pulled Apart | 2013-03-20 19:39 | 2013-03-20 | 2013-03-20 21:15 | Calculated | TF21K12 | TF21K12 - Transformer Fuse: TF21K12 |  | 416SEG5676 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 1 | 24574 | 96 | 0.00391 | 4.0693e-05 | 15 | 1440 | 2012/2013 | March-2013 | 3 | 2013
28784 | Refer 2013 / 99 Changing Poles & X/arms | 2013-03-21 08:42 | 2013-03-21 | 2013-03-21 15:32 | Calculated | 361 | 361 - Air Break Switch 361 |  | 102SEG191-361 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 356 | 9 | 24574 | 3204 | 0.13038 | 0.00036624 | 75 | 26699 | 2012/2013 | March-2013 | 3 | 2013
28783 | Unknown | 2013-03-21 09:10 | 2013-03-21 | 2013-03-21 16:29 | Calculated | TF2220 | TF2220 - Transformer Fuse: TF2220 |  | 128SEG1628 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 439 | 1 | 24574 | 439 | 0.01786 | 4.0693e-05 | 5 | 2195 | 2012/2013 | March-2013 | 3 | 2013
28782 | SWER Backfeed Refer 2013 / 98 Change Tx Pole 7E1, Various X/arms & Insulators | 2013-03-21 09:13 | 2013-03-21 | 2013-03-21 17:06 | Calculated | 5579 | 5579 - Fused Link 5579 |  | 413SEG5579-5571 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 449 | 31 | 24574 | 5002 | 0.20355 | 0.0012615 | 213 | 29940 | 2012/2013 | March-2013 | 3 | 2013
28785 | Refer 2013 / 100 Replce H/V Cable Feeding Tx 2155 | 2013-03-21 11:06 | 2013-03-21 | 2013-03-21 15:34 | Calculated | 2083 | 2083 - Fused Link 2083 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 268 | 61 | 24574 | 16348 | 0.66526 | 0.0024823 | 200 | 53599 | 2012/2013 | March-2013 | 3 | 2013
28786 | Unknown | 2013-03-22 07:56 | 2013-03-22 | 2013-03-22 09:59 | Calculated | TF4J7 | TF4J7 - Transformer Fuse: TF4J7 |  | 421SEG5657-5473 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 123 | 2 | 24574 | 246 | 0.01001 | 8.1387e-05 | 15 | 1845 | 2012/2013 | March-2013 | 3 | 2013
28787 | Faulty Tx | 2013-03-22 08:02 | 2013-03-22 | 2013-03-22 16:02 | Calculated | TF12H09 | TF12H09 - Transformer Fuse: TF12H09 |  | 410SEG5398 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 480 | 1 | 24574 | 480 | 0.01953 | 4.0693e-05 | 10 | 4800 | 2012/2013 | March-2013 | 3 | 2013
28788 | Refer 2013 / 102 Pole Replacements | 2013-03-22 08:11 | 2013-03-22 | 2013-03-22 16:02 | Calculated | 5949 | 5949 - Recloser with Bypass 5949 |  | 415SEG6617-5949 | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 471 | 2 | 24574 | 942 | 0.03833 | 8.1387e-05 | 65 | 30615 | 2012/2013 | March-2013 | 3 | 2013
28789 | Refer 2013 / 94 Upgrade Links & Bypass 570 & 571 | 2013-03-22 09:03 | 2013-03-22 | 2013-03-22 15:16 | Calculated | 5300 | 5300 - Fused Link 5300 |  | 413SEG5300-5570 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 373 | 24 | 24574 | 8560 | 0.34834 | 0.00097664 | 178 | 63416 | 2012/2013 | March-2013 | 3 | 2013
28790 | Refer 2013 / 101 Clean Up of Links 6189 | 2013-03-22 09:04 | 2013-03-22 | 2013-03-22 11:38 | Calculated | 6186 | 6186 - Fused Link 6186 |  | 405SEG6187-6186 | Hirangi 405-02 | Rural C | Hirangi | Awamate Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 232 | 24574 | 9584 | 0.39001 | 0.0094409 | 800 | 32349 | 2012/2013 | March-2013 | 3 | 2013
28791 | Tx Leaking Oil | 2013-03-22 10:18 | 2013-03-22 | 2013-03-22 13:08 | Calculated | TF2029 | TF2029 - Transformer Fuse: TF2029 |  | 115SEG1715 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 3 | 24574 | 510 | 0.02075 | 0.00012208 | 10 | 1699 | 2012/2013 | March-2013 | 3 | 2013
28792 | Fuse Pulled Apart | 2013-03-22 11:20 | 2013-03-22 | 2013-03-22 13:02 | Calculated | TF13J01 | TF13J01 - Transformer Fuse: TF13J01 |  | 410SEG5582 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 102 | 2 | 24574 | 204 | 0.0083 | 8.1387e-05 | 7.5 | 765 | 2012/2013 | March-2013 | 3 | 2013
28793 | Faulty L/A @ Tx 1170 | 2013-03-23 22:29 | 2013-03-23 | 2013-03-23 22:40 | Calculated | 652 | 652 - Load Break Switch 652 |  | 119SEG653-652 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 59 | 24574 | 355 | 0.01445 | 0.0024009 | 1033 | 6697 | 2012/2013 | March-2013 | 3 | 2013
28794 | Unknown | 2013-03-23 22:55 | 2013-03-23 | 2013-03-23 22:59 | Calculated | 796 | 796 - Circuit Breaker 796 |  | 301SEG1418-796 | Taharoa A 301-02 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24574 |  | 0 | 0 |  |  | 2012/2013 | March-2013 | 3 | 2013
28796 | Faulty L/A | 2013-03-24 07:34 | 2013-03-24 | 2013-03-24 10:20 | Calculated | TF1170 | TF1170 - Transformer Fuse: TF1170 |  | 103SEG453-459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 1 | 24574 | 166 | 0.00676 | 4.0693e-05 | 15 | 2490 | 2012/2013 | March-2013 | 3 | 2013
28797 | Bird | 2013-03-24 10:23 | 2013-03-24 | 2013-03-24 11:01 | Calculated | TF1A72 | TF1A72 - Transformer Fuse: TF1A72 |  | 404SEG5022-L1.10 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 3 | 24574 | 114 | 0.00464 | 0.00012208 | 50 | 1899 | 2012/2013 | March-2013 | 3 | 2013
28798 | Combine Harvester vs L/V | 2013-03-24 16:31 | 2013-03-24 | 2013-03-24 18:18 | Calculated | TF1074 | TF1074 - Transformer Fuse: TF1074 |  | 109SEG396-397 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 2 | 24574 | 214 | 0.00871 | 8.1387e-05 | 10 | 1070 | 2012/2013 | March-2013 | 3 | 2013
28799 | Unknown | 2013-03-24 18:45 | 2013-03-24 | 2013-03-24 21:07 | Calculated | TF1838 | TF1838 - Transformer Fuse: TF1838 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 142 | 2 | 24574 | 284 | 0.01156 | 8.1387e-05 | 15 | 2130 | 2012/2013 | March-2013 | 3 | 2013
28795 | Fuse Pulled Apart | 2013-03-24 23:19 | 2013-03-24 | 2013-03-25 00:45 | Calculated | TF12K14 | TF12K14 - Transformer Fuse: TF12K14 |  | 409SEG5934 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 3 | 24574 | 258 | 0.0105 | 0.00012208 | 150 | 12900 | 2012/2013 | March-2013 | 3 | 2013
28800 | Refer 2013 / 103 Changing Poles - Feedr Renewal Project | 2013-03-25 09:17 | 2013-03-25 | 2013-03-25 15:45 | Calculated | REG7X | REG7X - Outgoing Solid Link REG7X |  | 103SEG107-REG7 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 290 | 9 | 24574 | 2610 | 0.10621 | 0.00036624 | 50 | 14500 | 2012/2013 | March-2013 | 3 | 2013
28801 | Refer 2013 / 92 Fix H/V L/V Doors On Tx 16N26 | 2013-03-25 11:58 | 2013-03-25 | 2013-03-25 14:01 | Calculated | 6343 | 6343 - Circuit Breaker 6343 |  | 419SEG6340-6341 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 123 | 1 | 24574 | 123 | 0.00501 | 4.0693e-05 | 200 | 24600 | 2012/2013 | March-2013 | 3 | 2013
28802 | Unknown | 2013-03-25 12:43 | 2013-03-25 | 2013-03-25 15:49 | Calculated | TF1838 | TF1838 - Transformer Fuse: TF1838 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 186 | 2 | 24574 | 372 | 0.01514 | 8.1387e-05 | 15 | 2790 | 2012/2013 | March-2013 | 3 | 2013
28803 | Broken L/V X/arm | 2013-03-25 19:31 | 2013-03-25 | 2013-03-25 20:21 | Calculated | TF721 | TF721 - Transformer Fuse: TF721 |  | 120SEG498-408 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 6 | 24574 | 300 | 0.01221 | 0.00024416 | 25 | 1249 | 2012/2013 | March-2013 | 3 | 2013
28804 | Unknown | 2013-03-26 06:26 | 2013-03-26 | 2013-03-26 07:37 | Calculated | 5455 | 5455 - Recloser with Bypass & Links 5455 |  | 413SEG5454-5455 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 71 | 23 | 24574 | 1633 | 0.06645 | 0.00093595 | 153 | 10863 | 2012/2013 | March-2013 | 3 | 2013
28805 | Refer 2013 / 105 Ohura Renewal - Change Various Poles With Helicopter | 2013-03-26 09:04 | 2013-03-26 | 2013-03-26 15:14 | Calculated | 5287J | 5287J - Incoming Link 5287J |  | 413SEG5288-5287 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 364 | 8 | 24574 | 2912 | 0.1185 | 0.00032555 | 38 | 13832 | 2012/2013 | March-2013 | 3 | 2013
28806 | Refer 2013 / 112 Complete Through Joint On Cable To Tx 4194 | 2013-03-26 12:32 | 2013-03-26 | 2013-03-26 15:24 | Calculated | 6573 | 6573 - Fused Link 6573 |  | 423SEG5198-5881 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 172 | 11 | 24574 | 1892 | 0.07699 | 0.00044763 | 300 | 51599 | 2012/2013 | March-2013 | 3 | 2013
28807 | Bird | 2013-03-26 16:03 | 2013-03-26 | 2013-03-26 17:17 | Calculated | TF10K05 | TF10K05 - Transformer Fuse: TF10K05 |  | 409SEG5403-5662RET | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 74 | 2 | 24574 | 148 | 0.00602 | 8.1387e-05 | 15 | 1110 | 2012/2013 | March-2013 | 3 | 2013
28808 | Refer 2013 / 108 Ohura Renewal - Change Various Poles With Helicopter | 2013-03-27 09:06 | 2013-03-27 | 2013-03-27 16:03 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 398 | 27 | 24574 | 5970 | 0.24294 | 0.0010987 | 193 | 37014 | 2012/2013 | March-2013 | 3 | 2013
28809 | Refer 2013 / 109 Changing Poles - Feeder Renewal Project | 2013-03-27 09:36 | 2013-03-27 | 2013-03-27 15:50 | Calculated | 652 | 652 - Load Break Switch 652 |  | 119SEG653-652 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 285 | 26 | 24574 | 7410 | 0.30154 | 0.001058 | 195 | 55574 | 2012/2013 | March-2013 | 3 | 2013
28810 | Low 11kV Lines | 2013-03-27 11:35 | 2013-03-27 | 2013-03-27 13:26 | Calculated | TF1730 | TF1730 - Transformer Fuse: TF1730 |  | 116SEG1355-1327 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DICL | Conductor Low - Incorrect Clearances | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 2 | 24574 | 222 | 0.00903 | 8.1387e-05 | 15 | 1665 | 2012/2013 | March-2013 | 3 | 2013
28811 | Possum @ Tx 2807 | 2013-03-28 06:48 | 2013-03-28 | 2013-03-28 15:30 | Calculated | TF2807 | TF2807 - Transformer Fuse: TF2807 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 522 | 6 | 24574 | 1387 | 0.05644 | 0.00024416 | 95 | 21669 | 2012/2013 | March-2013 | 3 | 2013
28812 | SWER Backfeed Refer 2013 / 110 Ohura Renewal - Change Various Poles With Helicopter | 2013-03-28 08:48 | 2013-03-28 | 2013-03-28 16:33 | Calculated | 5570 | 5570 - Fused Link 5570 |  | 413SEG5300-5570 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 362 | 11 | 24574 | 3982 | 0.16204 | 0.00044763 | 75 | 27150 | 2012/2013 | March-2013 | 3 | 2013
28813 | Bolt Out of X/arm | 2013-03-28 12:16 | 2013-03-28 | 2013-03-28 13:09 | Calculated | TF8G10 | TF8G10 - Transformer Fuse: TF8G10 |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 53 | 2 | 24574 | 106 | 0.00431 | 8.1387e-05 | 25 | 1325 | 2012/2013 | March-2013 | 3 | 2013
28814 | Bird | 2013-03-28 13:22 | 2013-03-28 | 2013-03-28 14:40 | Calculated | TF4056 | TF4056 - Transformer Fuse: TF4056 |  | 409SEG5599-5600 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 78 | 1 | 24574 | 78 | 0.00317 | 4.0693e-05 | 5 | 390 | 2012/2013 | March-2013 | 3 | 2013
28815 | L/V Fuse Box | 2013-03-28 15:34 | 2013-03-28 | 2013-03-28 16:07 | Calculated | TF7D21 | TF7D21 - Transformer Fuse: TF7D21 |  | 413SEG5996-5758 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 25 | 24574 | 825 | 0.03357 | 0.0010173 | 100 | 3300 | 2012/2013 | March-2013 | 3 | 2013
28816 | Lower 2 Taps | 2013-03-28 16:25 | 2013-03-28 | 2013-03-28 16:49 | Calculated | TF1271 | TF1271 - Transformer Fuse: TF1271 |  | 123SEG493-466 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 4 | 24574 | 96 | 0.00391 | 0.00016277 | 15 | 360 | 2012/2013 | March-2013 | 3 | 2013
28817 | Unknown | 2013-03-30 08:42 | 2013-03-30 | 2013-03-30 09:32 | Calculated | 5847 | 5847 - Recloser w Bypass & Links 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 39 | 24574 | 1950 | 0.07935 | 0.001587 | 343.5 | 17174 | 2012/2013 | March-2013 | 3 | 2013
28818 | Unknown | 2013-03-31 09:31 | 2013-03-31 | 2013-03-31 10:37 | Calculated | 5162 | 5162 - Fused Link 5162 |  | 411SEG5147-5775 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 5 | 24574 | 330 | 0.01343 | 0.00020347 | 45 | 2970 | 2012/2013 | March-2013 | 3 | 2013
28819 | Bird at Tx 7R2 | 2013-03-31 10:04 | 2013-03-31 | 2013-03-31 16:13 | Calculated | 5110 | 5110 - Fused Link 5110 |  | 426SEG5110-5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 369 | 39 | 24574 | 10518 | 0.42801 | 0.001587 | 343.5 | 91211 | 2012/2013 | March-2013 | 3 | 2013
28820 | Broken DDO at Tx 365 | 2013-03-31 22:16 | 2013-03-31 | 2013-04-01 00:38 | Calculated | 394 | 394 - Air Break Switch 394 |  | 122SEG394-618 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 42 | 24574 | 4788 | 0.19484 | 0.0017091 | 510 | 58139 | 2012/2013 | March-2013 | 3 | 2013
28821 | Blown HV Fuse - Unknown Fault | 2013-04-01 09:58 | 2013-04-01 | 2013-04-01 11:01 | Calculated | TF08R03 | TF08R03 - Transformer Fuse: TF8R3 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 1 | 24562 | 63 | 0.00256 | 4.0713e-05 | 5 | 315 | 2013/2014 | April-2013 | 4 | 2013
28823 | Bolt Down Tx | 2013-04-02 10:14 | 2013-04-02 | 2013-04-02 10:41 | Calculated | TF8F2 | TF8F2 - Transformer Fuse: TF8F2 |  | 413SEG5123 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 27 | 3 | 24562 | 81 | 0.0033 | 0.00012214 | 15 | 405 | 2013/2014 | April-2013 | 4 | 2013
28824 | Check L/V Connections | 2013-04-02 13:11 | 2013-04-02 | 2013-04-02 14:47 | Calculated | TF1600 | TF1600 - Transformer Fuse: TF1600 |  | 128SEG1615-1624 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 96 | 1 | 24562 | 96 | 0.00391 | 4.0713e-05 | 15 | 1440 | 2013/2014 | April-2013 | 4 | 2013
28826 | Refer 2013 / 115 Change Poles & X/arms | 2013-04-03 09:34 | 2013-04-03 | 2013-04-03 15:20 | Calculated | 260 | 260 - Fused Link 260 |  | 103SEG669-REG4 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 346 | 22 | 24562 | 7612 | 0.30991 | 0.00089569 | 185.5 | 64182 | 2013/2014 | April-2013 | 4 | 2013
28827 | L/V Line Down | 2013-04-03 09:47 | 2013-04-03 | 2013-04-03 10:57 | Calculated | TF1233 | TF1233 - Transformer Fuse: TF1233 |  | 110SEG390-2144 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 3 | 24562 | 210 | 0.00855 | 0.00012214 | 25 | 1749 | 2013/2014 | April-2013 | 4 | 2013
28828 | Tree Through Line | 2013-04-03 22:03 | 2013-04-03 | 2013-04-03 23:59 | Calculated | 1325 | 1325 - Fused Link 1325 |  | 103SEG1335-1301 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 116 | 4 | 24562 | 464 | 0.01889 | 0.00016285 | 30 | 3480 | 2013/2014 | April-2013 | 4 | 2013
28830 | Unknown | 2013-04-04 02:41 | 2013-04-04 | 2013-04-04 05:46 | Calculated | 446 | 446 - Recloser 446 |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 71 | 24562 | 1136 | 0.04625 | 0.0028906 | 850 | 13599 | 2013/2014 | April-2013 | 4 | 2013
28831 | Fuse Pulled Apart | 2013-04-04 08:12 | 2013-04-04 | 2013-04-04 10:25 | Calculated | TF15J03 | TF15J03 - Transformer Fuse: TF15J03 |  | 410SEG5793-5746 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 133 | 1 | 24562 | 133 | 0.00541 | 4.0713e-05 | 15 | 1995 | 2013/2014 | April-2013 | 4 | 2013
28832 | Refer 2013 / 116 Change Poles & X/arms | 2013-04-04 09:33 | 2013-04-04 | 2013-04-04 15:03 | Calculated | 260 | 260 - Fused Link 260 |  | 103SEG669-REG4 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 330 | 22 | 24562 | 7260 | 0.29558 | 0.00089569 | 185.5 | 61214 | 2013/2014 | April-2013 | 4 | 2013
28833 | Bird | 2013-04-04 09:41 | 2013-04-04 | 2013-04-04 11:21 | Calculated | TF7Q8 | TF7Q8 - Transformer Fuse: TF7Q8 |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 2 | 24562 | 200 | 0.00814 | 8.1427e-05 | 15 | 1500 | 2013/2014 | April-2013 | 4 | 2013
28834 | Trees in Line | 2013-04-04 11:09 | 2013-04-04 | 2013-04-04 13:59 | Calculated | 1335 | 1335 - Sectionaliser 1335 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 170 | 17 | 24562 | 2890 | 0.11766 | 0.00069213 | 148 | 25160 | 2013/2014 | April-2013 | 4 | 2013
28835 | Faulty Tx - Truck vs L/V | 2013-04-04 18:06 | 2013-04-04 | 2013-04-05 00:20 | Calculated | TF150 | TF150 - Transformer Fuse: TF150 |  | 107SEG262-176 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 374 | 5 | 24562 | 1870 | 0.07613 | 0.00020357 | 30 | 11220 | 2013/2014 | April-2013 | 4 | 2013
28836 | Replace Pillar Box | 2013-04-05 09:01 | 2013-04-05 | 2013-04-05 13:30 | Calculated | TF8R20 | TF8R20 - Transformer Fuse: TF8R20 |  | 406SEG6558-5921 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 16 | 24562 | 4304 | 0.17523 | 0.00065141 | 100 | 26900 | 2013/2014 | April-2013 | 4 | 2013
28837 | Refer 2013 / 118 Replace Faulty Tx 4068 (Hit By Digger) | 2013-04-05 09:11 | 2013-04-05 | 2013-04-05 13:34 | Calculated | 6586 | 6586 - Load Break Switch 6586 |  | 415SEG6354-6586 | Turoa 415-03 | Rural B | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24562 |  | 0 | 0 |  |  | 2013/2014 | April-2013 | 4 | 2013
28838 | Refer 2013 / 117 Replace Old insulators | 2013-04-05 10:00 | 2013-04-05 | 2013-04-05 13:42 | Calculated | 5592 | 5592 - Fused Link 5592 |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 222 | 32 | 24562 | 7104 | 0.28923 | 0.0013028 | 268.5 | 59606 | 2013/2014 | April-2013 | 4 | 2013
28839 | Birds | 2013-04-05 18:22 | 2013-04-05 | 2013-04-05 18:41 | Calculated | TF4056 | TF4056 - Transformer Fuse: TF4056 |  | 409SEG5599-5600 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 19 | 1 | 24562 | 19 | 0.00077 | 4.0713e-05 | 5 | 95 | 2013/2014 | April-2013 | 4 | 2013
28840 | Bird Contact - Suspect Spark Gap | 2013-04-05 23:21 | 2013-04-05 | 2013-04-06 09:08 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 587 | 1 | 24562 | 587 | 0.0239 | 4.0713e-05 | 5 | 2935 | 2013/2014 | April-2013 | 4 | 2013
28841 | Unknown | 2013-04-06 09:37 | 2013-04-06 | 2013-04-06 11:11 | Calculated | 5459 | 5459 - Sectionaliser with Bypass & Links 5459 |  | 413SEG5459-5453 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 94 | 58 | 24562 | 5292 | 0.21545 | 0.0023614 | 413 | 37469 | 2013/2014 | April-2013 | 4 | 2013
28842 | Vehicle vs Pole | 2013-04-06 11:17 | 2013-04-06 | 2013-04-07 00:27 | Calculated | 5.19 | 5.19 - Air Break Switch 5.19 |  | 401SEG5.10-6721 | Hakiaha 401-01 | Urban A | Hakiaha | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 645 | 298 | 24562 | 41444 | 1.6873 | 0.012133 | 3780 | 880599 | 2013/2014 | April-2013 | 4 | 2013
28843 | Faulty Transfomer | 2013-04-06 11:40 | 2013-04-06 | 2013-04-06 18:53 | Calculated | TF20L2 | TF20L2 - Transformer Fuse: TF20L2 |  | 414SEG5715-5925RET | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 433 | 42 | 24562 | 18186 | 0.74041 | 0.00171 | 300 | 129899 | 2013/2014 | April-2013 | 4 | 2013
28844 | Unknown E/F | 2013-04-06 16:16 | 2013-04-06 | 2013-04-06 16:21 | Calculated | 594 | 594 - Recloser 594 |  | No Segment | 205-01 Gadsby Road | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 2045 | 24562 | 10225 | 0.41629 | 0.083259 | 14512 | 72560 | 2013/2014 | April-2013 | 4 | 2013
28845 | Birds | 2013-04-07 10:58 | 2013-04-07 | 2013-04-07 13:14 | Calculated | TF10E04 | TF10E04 - Transformer Fuse: TF10E04 |  | 413SEG5647-5646 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 136 | 2 | 24562 | 272 | 0.01107 | 8.1427e-05 | 10 | 1360 | 2013/2014 | April-2013 | 4 | 2013
28846 | Birds | 2013-04-07 16:06 | 2013-04-07 | 2013-04-07 17:13 | Calculated | TF07R10 | TF07R10 - Transformer Fuse: TF7R10 |  | 426SEG5110-5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 2 | 24562 | 134 | 0.00546 | 8.1427e-05 | 7.5 | 502 | 2013/2014 | April-2013 | 4 | 2013
28848 | Birds | 2013-04-08 06:47 | 2013-04-08 | 2013-04-08 20:57 | Calculated | TF4J10 | TF4J10 - Transformer Fuse: TF4J10 |  | 421SEG5669-5342 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 850 | 3 | 24562 | 2550 | 0.10382 | 0.00012214 | 15 | 12750 | 2013/2014 | April-2013 | 4 | 2013
28847 | Birds | 2013-04-08 07:40 | 2013-04-08 | 2013-04-08 09:41 | Calculated | TF07R10 | TF07R10 - Transformer Fuse: TF7R10 |  | 426SEG5110-5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 2 | 24562 | 242 | 0.00985 | 8.1427e-05 | 7.5 | 907 | 2013/2014 | April-2013 | 4 | 2013
28849 | Fuse Pulled Apart | 2013-04-09 12:20 | 2013-04-09 | 2013-04-09 13:50 | Calculated | TF1182 | TF1182 - Transformer Fuse: TF1182 |  | 103SEG197-177 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 3 | 24562 | 270 | 0.01099 | 0.00012214 | 10 | 899 | 2013/2014 | April-2013 | 4 | 2013
28850 | Birds | 2013-04-10 11:19 | 2013-04-10 | 2013-04-10 12:00 | Calculated | 5227 | 5227 - Fused Link 5227 |  | 412SEG5227-5269 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 41 | 8 | 24562 | 328 | 0.01335 | 0.00032571 | 50 | 2050 | 2013/2014 | April-2013 | 4 | 2013
28851 | Change Polymer | 2013-04-10 14:19 | 2013-04-10 | 2013-04-10 15:53 | Calculated | 493 | 493 - Air Break Switch 493 |  | 123SEG493-466 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 104 | 24562 | 9776 | 0.39801 | 0.0042342 | 975 | 91649 | 2013/2014 | April-2013 | 4 | 2013
28852 | Blown HV Fuse - Unknown Fault | 2013-04-10 16:00 | 2013-04-10 | 2013-04-10 16:47 | Calculated | TF4I7 | TF4I7 - Transformer Fuse: TF4I7 |  | 421SEG5586-5659 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 47 | 1 | 24562 | 47 | 0.00191 | 4.0713e-05 | 3 | 141 | 2013/2014 | April-2013 | 4 | 2013
28853 | Replace Sturcture | 2013-04-11 09:36 | 2013-04-11 | 2013-04-11 16:41 | Calculated | TF1031 | TF1031 - Transformer Fuse: TF1031 |  | 112SEG545-326 | Otorohanga 112-05 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 425 | 2 | 24562 | 850 | 0.03461 | 8.1427e-05 | 10 | 4250 | 2013/2014 | April-2013 | 4 | 2013
28855 | Birds | 2013-04-11 09:42 | 2013-04-11 | 2013-04-11 10:38 | Calculated | 764 | 764 - Solid Link 764 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 9 | 24562 | 504 | 0.02052 | 0.00036642 | 50 | 2799 | 2013/2014 | April-2013 | 4 | 2013
28854 | Upgrade Pole & Tx 2952 | 2013-04-11 10:39 | 2013-04-11 | 2013-04-11 16:51 | Calculated | TF2952 | TF2952 - Transformer Fuse: TF2952 |  | 108SEG763-2140 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 372 | 1 | 24562 | 372 | 0.01515 | 4.0713e-05 | 30 | 11160 | 2013/2014 | April-2013 | 4 | 2013
28856 | Refer 2013 / 126 Fit DDO To T/O For Tx 15J3 | 2013-04-12 09:20 | 2013-04-12 | 2013-04-12 14:26 | Calculated | 5746 | 5746 - Solid Link 5746 |  | 410SEG5746-5431 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 270 | 62 | 24562 | 1350 | 0.05496 | 0.0025242 | 371.5 | 10125 | 2013/2014 | April-2013 | 4 | 2013
28858 | Broken Cross Arm | 2013-04-12 09:34 | 2013-04-12 | 2013-04-12 10:52 | Calculated | TF1892 | TF1892 - Transformer Fuse: TF1892 |  | 114SEG1100 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 78 | 3 | 24562 | 234 | 0.00953 | 0.00012214 | 15 | 1170 | 2013/2014 | April-2013 | 4 | 2013
28857 | Tree Cutting | 2013-04-12 09:42 | 2013-04-12 | 2013-04-12 12:15 | Calculated | 466 | 466 - Recloser 466 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 153 | 28 | 24562 | 4284 | 0.17442 | 0.00114 | 235 | 35955 | 2013/2014 | April-2013 | 4 | 2013
28859 | Refer 2013 / 122 Replace Bent Pole 79/38/29 | 2013-04-12 10:01 | 2013-04-12 | 2013-04-12 12:57 | Calculated | 5456 | 5456 - Fused Link 5456 |  | 413SEG5456-5461 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 176 | 18 | 24562 | 3168 | 0.12898 | 0.00073284 | 125 | 22000 | 2013/2014 | April-2013 | 4 | 2013
28861 | Blown HV Fuse - Unknown Fault | 2013-04-12 15:37 | 2013-04-12 | 2013-04-12 17:21 | Calculated | TF1182 | TF1182 - Transformer Fuse: TF1182 |  | 103SEG197-177 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 3 | 24562 | 312 | 0.0127 | 0.00012214 | 10 | 1039 | 2013/2014 | April-2013 | 4 | 2013
28862 | E/F B Phase | 2013-04-12 21:24 | 2013-04-12 | 2013-04-12 21:27 | Calculated | 1020 | 1020 - Recloser with Bypass & Links 1020 |  | 107SEG233-1020 | Oparure 107-03 | Rural C | Oparure | Gadsby Road Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 277 | 24562 | 831 | 0.03383 | 0.011278 | 2357.5 | 7072 | 2013/2014 | April-2013 | 4 | 2013
28863 | Replace Red Tagged LV Pole | 2013-04-13 09:44 | 2013-04-13 | 2013-04-13 14:35 | Calculated | TF620 | TF620 - Transformer Fuse: TF620 |  | 103SEG1230 | Benneydale 103-07 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 291 | 25 | 24562 | 7275 | 0.29619 | 0.0010178 | 100 | 29100 | 2013/2014 | April-2013 | 4 | 2013
28865 | HV Fuse Blown - Old Age | 2013-04-14 14:40 | 2013-04-14 | 2013-04-14 16:22 | Calculated | TF7F1 | TF7F1 - Transformer Fuse: TF7F1 |  | 413SEG5508 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 102 | 1 | 24562 | 102 | 0.00415 | 4.0713e-05 | 10 | 1020 | 2013/2014 | April-2013 | 4 | 2013
28866 | HV Fuse Blown - Birds | 2013-04-14 14:45 | 2013-04-14 | 2013-04-14 16:37 | Calculated | TF8F3 | TF8F3 - Transformer Fuse: TF8F3 |  | 413SEG5508 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 112 | 1 | 24562 | 112 | 0.00456 | 4.0713e-05 | 5 | 560 | 2013/2014 | April-2013 | 4 | 2013
28864 | Faulty DDO | 2013-04-14 15:25 | 2013-04-14 | 2013-04-14 16:45 | Calculated | TF1182 | TF1182 - Transformer Fuse: TF1182 |  | 103SEG197-177 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 3 | 24562 | 240 | 0.00977 | 0.00012214 | 10 | 799 | 2013/2014 | April-2013 | 4 | 2013
28867 | Earth Fault | 2013-04-15 03:59 | 2013-04-15 | 2013-04-15 10:25 | Calculated | 446 | 446 - Recloser 446 |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 172 | 24562 | 12572 | 0.51185 | 0.0070027 | 1725 | 124184 | 2013/2014 | April-2013 | 4 | 2013
28869 | Blown HV Fuse - Unknown Fault | 2013-04-15 09:50 | 2013-04-15 | 2013-04-15 11:13 | Calculated | TF4F10 | TF4F10 - Transformer Fuse: TF4F10 |  | 422SEG5307-5556 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 83 | 1 | 24562 | 83 | 0.00338 | 4.0713e-05 | 7.5 | 622 | 2013/2014 | April-2013 | 4 | 2013
28870 | Refer 2013 / 31 Replace X-Arm & DDO on TX 12K10 | 2013-04-15 10:03 | 2013-04-15 | 2013-04-15 11:35 | Calculated | 5113 | 5113 - Fused Link 5113 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 92 | 33 | 24562 | 3036 | 0.12361 | 0.0013435 | 178 | 16375 | 2013/2014 | April-2013 | 4 | 2013
28871 | Birds | 2013-04-15 17:06 | 2013-04-15 | 2013-04-15 18:07 | Calculated | TF1A72 | TF1A72 - Transformer Fuse: TF1A72 |  | 404SEG5022-L1.10 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 3 | 24562 | 183 | 0.00745 | 0.00012214 | 50 | 3049 | 2013/2014 | April-2013 | 4 | 2013
28872 | Old Age | 2013-04-15 18:46 | 2013-04-15 | 2013-04-15 20:10 | Calculated | TF9L7 | TF9L7 - Transformer Fuse: TF9L7 |  | 408SEG5406 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 84 | 3 | 24562 | 252 | 0.01026 | 0.00012214 | 3 | 252 | 2013/2014 | April-2013 | 4 | 2013
28873 | HV Line On Ground | 2013-04-16 00:55 | 2013-04-16 | 2013-04-16 13:49 | Calculated | 296 | 296 - Recloser with Bypass 296 |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 750 | 169 | 24562 | 27194 | 1.1072 | 0.0068805 | 1185 | 209434 | 2013/2014 | April-2013 | 4 | 2013
28874 | Tripped E/F | 2013-04-16 06:47 | 2013-04-16 | 2013-04-16 08:05 | Calculated | 609 | 609 - Circuit Breaker 609 (Rural Feeder) 609 |  | No Segment | 201-01 Taharoa | Rural D | No Feeder |  |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 116 | 24562 | 9048 | 0.36837 | 0.0047227 | 773 | 60293 | 2013/2014 | April-2013 | 4 | 2013
28875 | Faulty Cable Beyond L 292 | 2013-04-16 10:11 | 2013-04-16 | 2013-04-17 12:53 | Calculated | 292 | 292 - Fused Link 292 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 1602 | 122 | 24562 | 30310 | 1.234 | 0.004967 | 1031 | 264444 | 2013/2014 | April-2013 | 4 | 2013
28876 | Faulty Pin Insulator | 2013-04-16 10:13 | 2013-04-16 | 2013-04-16 14:49 | Calculated | 5740 | 5740 - Sectionaliser with Bypass & Links 5740 |  | 403SEG5740-5546 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 276 | 24 | 24562 | 6624 | 0.26968 | 0.00097712 | 135 | 37259 | 2013/2014 | April-2013 | 4 | 2013
28877 | Tripped - Loose Stay | 2013-04-16 10:13 | 2013-04-16 | 2013-04-16 17:11 | Calculated | 5495 | 5495 - Fused Link 5495 |  | 410SEG5495-5499 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:OIWAWD | Broken Stay Wire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 418 | 41 | 24562 | 15032 | 0.612 | 0.0016692 | 270 | 96689 | 2013/2014 | April-2013 | 4 | 2013
28878 | X-Arm Flipped Over | 2013-04-16 16:03 | 2013-04-16 | 2013-04-16 20:58 | Calculated | 509 | 509 - Fused Link 509 |  | 126SEG509 | Rural 126-02 | Rural D | Rural | Taharoa Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAB | Cross-Arm Bent | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 295 | 117 | 24562 | 19597 | 0.79786 | 0.0047635 | 773 | 129939 | 2013/2014 | April-2013 | 4 | 2013
28879 | Trees | 2013-04-16 18:26 | 2013-04-16 | 2013-04-16 20:59 | Calculated | 2143 | 2143 - Fused Link 2143 |  | 107SEG2143 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 153 | 4 | 24562 | 612 | 0.02492 | 0.00016285 | 20 | 3060 | 2013/2014 | April-2013 | 4 | 2013
28880 | Wind | 2013-04-16 20:32 | 2013-04-16 | 2013-04-16 21:53 | Calculated | 5170 | 5170 - Sectionaliser 5170 |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 81 | 21 | 24562 | 1701 | 0.06925 | 0.00085498 | 188 | 15227 | 2013/2014 | April-2013 | 4 | 2013
28883 | Trees | 2013-04-17 07:12 | 2013-04-17 | 2013-04-17 10:14 | Calculated | TF9C4 | TF9C4 - Transformer Fuse: TF9C4 |  | 413SEG5456-5461 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 182 | 1 | 24562 | 182 | 0.00741 | 4.0713e-05 | 15 | 2730 | 2013/2014 | April-2013 | 4 | 2013
28882 | Private Line Maintenance | 2013-04-17 08:36 | 2013-04-17 | 2013-04-17 09:13 | Calculated | TF1890 | TF1890 - Transformer Fuse: TF1890 |  | 114SEG1122 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 37 | 3 | 24562 | 111 | 0.00452 | 0.00012214 | 15 | 555 | 2013/2014 | April-2013 | 4 | 2013
28884 | H/V Line Down | 2013-04-17 10:21 | 2013-04-17 | 2013-04-17 18:01 | Calculated | 1624 | 1624 - Fused Link 1624 |  | 128SEG1615-1624 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 447 | 42 | 24562 | 7804 | 0.31773 | 0.00171 | 325 | 61975 | 2013/2014 | April-2013 | 4 | 2013
28881 | Faulty Transformer | 2013-04-17 12:53 | 2013-04-17 | 2013-04-17 14:02 | Calculated | TF2300 | TF2300 - Transformer Fuse: TF2300 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 1 | 24562 | 69 | 0.00281 | 4.0713e-05 | 10 | 690 | 2013/2014 | April-2013 | 4 | 2013
28885 | Old Age | 2013-04-17 18:34 | 2013-04-17 | 2013-04-17 19:47 | Calculated | TF10K31 | TF10K31 - Transformer Fuse: TF10K31 |  | 409SEG5403-5662RET | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 73 | 4 | 24562 | 292 | 0.01189 | 0.00016285 | 30 | 2190 | 2013/2014 | April-2013 | 4 | 2013
28886 | Old Age | 2013-04-17 20:00 | 2013-04-17 | 2013-04-17 21:44 | Calculated | TF2104 | TF2104 - Transformer Fuse: TF2104 |  | 115SEG1356-1725 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 104 | 2 | 24562 | 208 | 0.00847 | 8.1427e-05 | 15 | 1560 | 2013/2014 | April-2013 | 4 | 2013
28887 | L/V Work | 2013-04-18 15:34 | 2013-04-18 | 2013-04-18 17:18 | Calculated | TF1232 | TF1232 - Transformer Fuse: TF1232 |  | 103SEG621 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 104 | 2 | 24562 | 208 | 0.00847 | 8.1427e-05 | 10 | 1040 | 2013/2014 | April-2013 | 4 | 2013
28888 | L/V Maintenace | 2013-04-19 09:21 | 2013-04-19 | 2013-04-19 10:23 | Calculated | TF671 | TF671 - Transformer Fuse: TF671 |  | 110SEG323-644 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 62 | 7 | 24562 | 434 | 0.01767 | 0.00028499 | 25 | 1549 | 2013/2014 | April-2013 | 4 | 2013
28890 | Blown HV Fuse - Unknown Fault | 2013-04-19 12:00 | 2013-04-19 | 2013-04-19 14:29 | Calculated | TF09P02 | TF09P02 - Transformer Fuse: TF09P02 |  | 609SEG5839-5163 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 149 | 1 | 24562 | 149 | 0.00607 | 4.0713e-05 | 100 | 14900 | 2013/2014 | April-2013 | 4 | 2013
28889 | Connect New Cable | 2013-04-19 13:17 | 2013-04-19 | 2013-04-19 16:25 | Calculated | 292 | 292 - Fused Link 292 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 188 | 8 | 24562 | 1504 | 0.06123 | 0.00032571 | 73 | 13724 | 2013/2014 | April-2013 | 4 | 2013
28891 | Lightning | 2013-04-20 08:13 | 2013-04-20 | 2013-04-20 18:16 | Calculated | TF2185 | TF2185 - Transformer Fuse: TF2185 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:IBW9EJ | Lightning Damage to Insulators | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 603 | 2 | 24562 | 1206 | 0.0491 | 8.1427e-05 | 10 | 6030 | 2013/2014 | April-2013 | 4 | 2013
28892 | Lightning | 2013-04-21 13:23 | 2013-04-21 | 2013-04-21 14:54 | Calculated | TF1229 | TF1229 - Transformer Fuse: TF1229 |  | 103SEG294-476 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 1 | 24562 | 91 | 0.0037 | 4.0713e-05 | 25 | 2275 | 2013/2014 | April-2013 | 4 | 2013
28893 | Lightning | 2013-04-21 14:28 | 2013-04-21 | 2013-04-21 15:14 | Calculated | 623 | 623 - Fused Link 623 |  | 103SEG293-294 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 5 | 24562 | 230 | 0.00936 | 0.00020357 | 47.5 | 2185 | 2013/2014 | April-2013 | 4 | 2013
28894 | Lightning | 2013-04-21 14:28 | 2013-04-21 | 2013-04-21 15:32 | Calculated | TF2308 | TF2308 - Transformer Fuse: TF2308 |  | 103SEG623 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 2 | 24562 | 128 | 0.00521 | 8.1427e-05 | 15 | 960 | 2013/2014 | April-2013 | 4 | 2013
28896 | Lightning | 2013-04-21 18:03 | 2013-04-21 | 2013-04-21 19:45 | Calculated | TF1432 | TF1432 - Transformer Fuse: TF1432 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 2 | 24562 | 204 | 0.00831 | 8.1427e-05 | 15 | 1530 | 2013/2014 | April-2013 | 4 | 2013
28895 | Lightning | 2013-04-21 18:23 | 2013-04-21 | 2013-04-21 18:26 | Calculated | 754 | 754 - Circuit Breaker 754 |  | 307SEG754-1732 | Gadsby / Wairere 307-01 | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 2045 | 24562 | 6135 | 0.24978 | 0.083259 | 14604.5 | 43813 | 2013/2014 | April-2013 | 4 | 2013
28897 | Lightning | 2013-04-21 18:38 | 2013-04-21 | 2013-04-21 20:18 | Calculated | TF1516 | TF1516 - Transformer Fuse: TF1516 |  | 111SEG373-1727 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 1 | 24562 | 100 | 0.00407 | 4.0713e-05 | 10 | 1000 | 2013/2014 | April-2013 | 4 | 2013
28899 | Lightning | 2013-04-21 19:13 | 2013-04-21 | 2013-04-21 20:21 | Calculated | TF506 | TF506 - Transformer Fuse: TF506 |  | 101SEG274-506 | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 4 | 24562 | 272 | 0.01107 | 0.00016285 | 10 | 680 | 2013/2014 | April-2013 | 4 | 2013
28898 | Lightning | 2013-04-21 19:25 | 2013-04-21 | 2013-04-21 20:20 | Calculated | TF2824 | TF2824 - Transformer Fuse: TF2824 |  | 124SEG457 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 24562 | 55 | 0.00224 | 4.0713e-05 | 50 | 2750 | 2013/2014 | April-2013 | 4 | 2013
28900 | Lightning | 2013-04-21 20:38 | 2013-04-21 | 2013-04-21 23:02 | Calculated | TF12O02 | TF12O02 - Transformer Fuse: TF12O02 |  | 418SEG5584-5591 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 144 | 2 | 24562 | 288 | 0.01173 | 8.1427e-05 | 15 | 2160 | 2013/2014 | April-2013 | 4 | 2013
28901 | Lightning | 2013-04-22 07:02 | 2013-04-22 | 2013-04-22 08:46 | Calculated | TF1670 | TF1670 - Transformer Fuse: TF1670 |  | 116SEG1312-1362 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 2 | 24562 | 208 | 0.00847 | 8.1427e-05 | 15 | 1560 | 2013/2014 | April-2013 | 4 | 2013
28902 | Lightning | 2013-04-22 07:53 | 2013-04-22 | 2013-04-22 09:02 | Calculated | TF763 | TF763 - Transformer Fuse: TF763 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 2 | 24562 | 138 | 0.00562 | 8.1427e-05 | 10 | 690 | 2013/2014 | April-2013 | 4 | 2013
28903 | Lightning | 2013-04-22 08:30 | 2013-04-22 | 2013-04-22 10:14 | Calculated | TF679 | TF679 - Transformer Fuse: TF679 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 1 | 24562 | 104 | 0.00423 | 4.0713e-05 | 10 | 1040 | 2013/2014 | April-2013 | 4 | 2013
28904 | Lightning | 2013-04-22 08:58 | 2013-04-22 | 2013-04-22 10:41 | Calculated | TF733 | TF733 - Transformer Fuse: TF733 |  | 103SEG709-453 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 1 | 24562 | 103 | 0.00419 | 4.0713e-05 | 10 | 1030 | 2013/2014 | April-2013 | 4 | 2013
28905 | Lightning | 2013-04-22 10:03 | 2013-04-22 | 2013-04-22 11:53 | Calculated | TF2922 | TF2922 - Transformer Fuse: TF2922 |  | 101SEG514 | Caves 101-11 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 2 | 24562 | 220 | 0.00896 | 8.1427e-05 | 10 | 1100 | 2013/2014 | April-2013 | 4 | 2013
28906 | Lightning | 2013-04-22 11:35 | 2013-04-22 | 2013-04-22 12:26 | Calculated | TF1586 | TF1586 - Transformer Fuse: TF1586 |  | 116SEG1312-1362 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 1 | 24562 | 51 | 0.00208 | 4.0713e-05 | 3 | 153 | 2013/2014 | April-2013 | 4 | 2013
28907 | Broken Pole | 2013-04-22 13:30 | 2013-04-22 | 2013-04-22 16:40 | Calculated | 5383 | 5383 - Air Break Switch 5383 |  | 409SEG5383-5922 | Southern 409-02 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 170 | 10 | 24562 | 1700 | 0.06921 | 0.00040713 | 125 | 21250 | 2013/2014 | April-2013 | 4 | 2013
28908 | Lightning | 2013-04-22 16:41 | 2013-04-22 | 2013-04-22 17:27 | Calculated | TF968 | TF968 - Transformer Fuse: TF968 |  | 124SEG1764-454 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 1 | 24562 | 46 | 0.00187 | 4.0713e-05 | 5 | 230 | 2013/2014 | April-2013 | 4 | 2013
28909 | Refer 2013 / 136 Change 11KV pole and X-Arms - Pole 1091135 cnr Lurman & Rangiates road | 2013-04-23 08:18 | 2013-04-23 | 2013-04-23 12:19 | Calculated | 349 | 349 - Automated Air Break Switch 349 |  | 109SEG348-522 | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 176 | 40 | 24562 | 7040 | 0.28662 | 0.0016285 | 340 | 59839 | 2013/2014 | April-2013 | 4 | 2013
28910 | Broken Xarm | 2013-04-23 08:24 | 2013-04-23 | 2013-04-23 09:31 | Calculated | 683 | 683 - Circuit Breaker 683 |  | No Segment | 207-01 Wairere Falls | Rural D | No Feeder |  |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 458 | 24562 | 16660 | 0.67828 | 0.018647 | 3056 | 115609 | 2013/2014 | April-2013 | 4 | 2013
28911 | Refer 2013 / 137 Repalce DDO & Arrestor on Tx 06J04 | 2013-04-23 09:38 | 2013-04-23 | 2013-04-23 11:38 | Calculated | 5354 | 5354 - Fused Link 5354 |  | 402SEG5354 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 120 | 7 | 24562 | 840 | 0.0342 | 0.00028499 | 52.5 | 6300 | 2013/2014 | April-2013 | 4 | 2013
28912 | Refer 2013 / 138 Repalce DDO & Arrestor on Tx 4056 | 2013-04-23 13:03 | 2013-04-23 | 2013-04-23 15:12 | Calculated | 5599 | 5599 - Recloser with Bypass & Links 5599 |  | 409SEG5598-5599 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 129 | 27 | 24562 | 3510 | 0.1429 | 0.0010993 | 210 | 27299 | 2013/2014 | April-2013 | 4 | 2013
28915 | 33KV Line Down | 2013-04-23 16:11 | 2013-04-23 | 2013-04-24 17:49 | Calculated | 5125 | 5125 - Air Break Switch 5125 |  | 608SEG5629-5125 | Taumarunui / Kuratau 608-02 | Urban A | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 20 | 4 | 24562 | 80 | 0.00326 | 0.00016285 | 450 | 9000 | 2013/2014 | April-2013 | 4 | 2013
28916 | Unknown | 2013-04-23 21:02 | 2013-04-23 | 2013-04-24 07:24 | Calculated | 5459 | 5459 - Sectionaliser with Bypass & Links 5459 |  | 413SEG5459-5453 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 622 | 24 | 24562 | 14928 | 0.60777 | 0.00097712 | 135 | 83969 | 2013/2014 | April-2013 | 4 | 2013
28917 | H/V Line Down | 2013-04-24 07:48 | 2013-04-24 | 2013-04-24 16:25 | Calculated | TF2822 | TF2822 - Transformer Fuse: TF2822 |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 517 | 1 | 24562 | 517 | 0.02105 | 4.0713e-05 | 15 | 7755 | 2013/2014 | April-2013 | 4 | 2013
28918 | Refer 2013 / 135 11KV Extention & DDO at Pole 44 | 2013-04-24 10:06 | 2013-04-24 | 2013-04-24 14:48 | Calculated | 544 | 544 - Air Break Switch 544 |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 31 | 24562 | 8742 | 0.35592 | 0.0012621 | 260 | 73319 | 2013/2014 | April-2013 | 4 | 2013
28919 | Trees | 2013-04-24 13:25 | 2013-04-24 | 2013-04-24 14:55 | Calculated | 5459 | 5459 - Sectionaliser with Bypass & Links 5459 |  | 413SEG5459-5453 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 90 | 26 | 24562 | 2340 | 0.09527 | 0.0010585 | 142.5 | 12824 | 2013/2014 | April-2013 | 4 | 2013
28920 | Blown HV fuse due to lightning | 2013-04-24 14:51 | 2013-04-24 | 2013-04-24 15:45 | Calculated | TF1484 | TF1484 - Transformer Fuse: TF1484 |  | 107SEG508-1798 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1 | 24562 | 54 | 0.0022 | 4.0713e-05 | 5 | 270 | 2013/2014 | April-2013 | 4 | 2013
28921 | Birds | 2013-04-25 08:28 | 2013-04-25 | 2013-04-25 09:25 | Calculated | 5162 | 5162 - Fused Link 5162 |  | 411SEG5147-5775 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 5 | 24562 | 285 | 0.0116 | 0.00020357 | 45 | 2565 | 2013/2014 | April-2013 | 4 | 2013
28922 | Refer 2013 / 143 Install New Pole | 2013-04-26 10:10 | 2013-04-26 | 2013-04-26 13:05 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 175 | 1 | 24562 | 175 | 0.00712 | 4.0713e-05 | 5 | 875 | 2013/2014 | April-2013 | 4 | 2013
28923 | L/V Repairs | 2013-04-26 10:21 | 2013-04-26 | 2013-04-26 13:58 | Calculated | TF849 | TF849 - Transformer Fuse: TF849 |  | 121SEG724-REG32 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 2 | 24562 | 434 | 0.01767 | 8.1427e-05 | 10 | 2170 | 2013/2014 | April-2013 | 4 | 2013
28924 | L/V Line Down | 2013-04-26 13:00 | 2013-04-26 | 2013-04-26 16:41 | Calculated | TF2530 | TF2530 - Transformer Fuse: TF2530 |  | 110SEG1344 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 7 | 24562 | 517 | 0.02105 | 0.00028499 | 60 | 7080 | 2013/2014 | April-2013 | 4 | 2013
28925 | Old Age | 2013-04-26 20:48 | 2013-04-26 | 2013-04-26 22:01 | Calculated | TF12S4 | TF12S4 - Transformer Fuse: TF12S4 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 1 | 24562 | 73 | 0.00297 | 4.0713e-05 | 7.5 | 547 | 2013/2014 | April-2013 | 4 | 2013
28926 | Birds | 2013-04-27 08:11 | 2013-04-27 | 2013-04-27 09:32 | Calculated | 663 | 663 - Fused Link 663 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 6 | 24562 | 486 | 0.01979 | 0.00024428 | 90 | 7290 | 2013/2014 | April-2013 | 4 | 2013
28927 | Broken Pole | 2013-04-27 10:41 | 2013-04-27 | 2013-04-27 11:36 | Calculated | TF1076 | TF1076 - Transformer Fuse: TF1076 |  | 122SEG595 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 24562 | 55 | 0.00224 | 4.0713e-05 | 7.5 | 412 | 2013/2014 | April-2013 | 4 | 2013
28928 | Refer 2013 / 140 Install New ABS 5967 | 2013-04-28 10:12 | 2013-04-28 | 2013-04-28 14:06 | Calculated | 5.19 | 5.19 - Air Break Switch 5.19 |  | 401SEG5.10-6721 | Hakiaha 401-01 | Urban A | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 234 | 56 | 24562 | 13104 | 0.53351 | 0.0022799 | 1280 | 299519 | 2013/2014 | April-2013 | 4 | 2013
28930 | Refer 2013 / 146 Repalce Red Tagged Pole 67 & Resag / Restrain Low Line Feeding Tx9U6 | 2013-04-29 09:40 | 2013-04-29 | 2013-04-29 15:37 | Calculated | 5245 | 5245 - Solid Link 5245 |  | 417SEG5245-5497 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 357 | 107 | 24562 | 38199 | 1.5552 | 0.0043563 | 735.7143 | 262649 | 2013/2014 | April-2013 | 4 | 2013
28931 | Unknown | 2013-04-29 12:11 | 2013-04-29 | 2013-04-29 14:00 | Calculated | 5440J | 5440J - Incoming Link 5440J |  | 409SEG5439-5440 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 109 | 22 | 24562 | 2398 | 0.09763 | 0.00089569 | 187.5 | 20437 | 2013/2014 | April-2013 | 4 | 2013
28932 | Refer 2013 / 147 Tree Cutting | 2013-04-30 09:00 | 2013-04-30 | 2013-04-30 11:45 | Calculated | TF16H03 | TF16H03 - Transformer Fuse: TF16H03 |  | 410SEG5517-6750 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 165 | 3 | 24562 | 495 | 0.02015 | 0.00012214 | 15 | 2475 | 2013/2014 | April-2013 | 4 | 2013
28934 | Birds | 2013-04-30 09:15 | 2013-04-30 | 2013-04-30 11:18 | Calculated | TF1928 | TF1928 - Transformer Fuse: TF1928 |  | 115SEG1706 | Mokauiti 115-01 | Rural D | Mokauiti | Wairere Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 1 | 24562 | 123 | 0.00501 | 4.0713e-05 | 15 | 1845 | 2013/2014 | April-2013 | 4 | 2013
28936 | Refer 2013 / 145 Replace X-Arms & Pole And Upgrade Earthmat at T08E04 | 2013-04-30 09:31 | 2013-04-30 | 2013-04-30 14:18 | Calculated | 5579 | 5579 - Fused Link 5579 |  | 413SEG5579-5571 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 242 | 26 | 24562 | 1472 | 0.05993 | 0.0010585 | 183 | 8472 | 2013/2014 | April-2013 | 4 | 2013
28933 | Refer 2013 / 141 Straighten SWER Structure | 2013-04-30 09:59 | 2013-04-30 | 2013-04-30 14:38 | Calculated | 5311 | 5311 - Air Break Switch 5311 |  | 409SEG5311-5452 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 263 | 135 | 24562 | 11437 | 0.46564 | 0.0054963 | 757.5 | 86489 | 2013/2014 | April-2013 | 4 | 2013
28935 | Birds | 2013-04-30 11:58 | 2013-04-30 | 2013-04-30 12:58 | Calculated | TF1214 | TF1214 - Transformer Fuse: TF1214 |  | 109SEG1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 3 | 24562 | 180 | 0.00733 | 0.00012214 | 30 | 1800 | 2013/2014 | April-2013 | 4 | 2013
28937 | Faulty Transformer | 2013-04-30 22:39 | 2013-04-30 | 2013-05-01 13:46 | Calculated | 5506 | 5506 - Sectionaliser with Bypass & Links 5506 |  | 413SEG5506 | Ohura 413-03 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 907 | 7 | 24562 | 6349 | 0.25849 | 0.00028499 | 43 | 39001 | 2013/2014 | April-2013 | 4 | 2013
28938 | Refer 2013 / 148 Straighten H Structure, Repace Arms, Install Stays | 2013-05-01 08:33 | 2013-05-01 | 2013-05-01 15:29 | Calculated | 5467 | 5467 - Recloser with Bypass & Links 5467 |  | 402SEG5467-5472 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 321 | 123 | 24529 | 4539 | 0.18505 | 0.0050145 | 1353 | 36400 | 2013/2014 | May-2013 | 5 | 2013
28940 | Faulty Sectionalizer | 2013-05-01 14:45 | 2013-05-01 | 2013-05-01 16:58 | Calculated | 1612 | 1612 - Sectionaliser with Bypass & Links 1612 |  | 128SEG1611-1612 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLI | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 133 | 42 | 24529 | 5586 | 0.22773 | 0.0017123 | 325 | 43225 | 2013/2014 | May-2013 | 5 | 2013
28941 | Birds | 2013-05-02 06:36 | 2013-05-02 | 2013-05-02 07:57 | Calculated | TF1755 | TF1755 - Transformer Fuse: TF1755 |  | 117SEG1316-1314 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 3 | 24529 | 243 | 0.00991 | 0.0001223 | 15 | 1215 | 2013/2014 | May-2013 | 5 | 2013
28943 | Faulty Transformer | 2013-05-02 08:33 | 2013-05-02 | 2013-05-02 16:26 | Calculated | TF1838 | TF1838 - Transformer Fuse: TF1838 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 473 | 2 | 24529 | 946 | 0.03857 | 8.1536e-05 | 15 | 7095 | 2013/2014 | May-2013 | 5 | 2013
28942 | Refer 2013 / 149 Repalce Red Tagged Pole 1231016 | 2013-05-02 09:04 | 2013-05-02 | 2013-05-02 15:02 | Calculated | 786 | 786 - Fused Link 786 |  | 124SEG542-786 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 308 | 42 | 24529 | 12936 | 0.52738 | 0.0017123 | 540 | 166319 | 2013/2014 | May-2013 | 5 | 2013
28944 | Refer 2013 / 150 Metering Testing | 2013-05-02 12:01 | 2013-05-02 | 2013-05-02 13:01 | Calculated | 5709 | 5709 - Air Break Switch 5709 |  | 416SEG5709-5796 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 21 | 24529 | 42 | 0.00171 | 0.00085613 | 455 | 910 | 2013/2014 | May-2013 | 5 | 2013
28945 | Change Transformer | 2013-05-03 09:24 | 2013-05-03 | 2013-05-03 12:38 | Calculated | TF4056 | TF4056 - Transformer Fuse: TF4056 |  | 409SEG5599-5600 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 194 | 1 | 24529 | 194 | 0.00791 | 4.0768e-05 | 5 | 970 | 2013/2014 | May-2013 | 5 | 2013
28946 | Refer 2013 / 151 Replace Pole & Conductor | 2013-05-03 09:38 | 2013-05-03 | 2013-05-03 13:25 | Calculated | 1638 | 1638 - Fused Link 1638 |  | 128SEG1638 | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 227 | 5 | 24529 | 1135 | 0.04627 | 0.00020384 | 45 | 10215 | 2013/2014 | May-2013 | 5 | 2013
28947 | Earth Fault | 2013-05-04 01:51 | 2013-05-04 | 2013-05-04 01:55 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | No Feeder |  |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24529 |  | 0 | 0 |  |  | 2013/2014 | May-2013 | 5 | 2013
28948 | Faulty Polymer at ABS 200 | 2013-05-04 13:54 | 2013-05-04 | 2013-05-04 16:50 | Calculated | 669 | 669 - Recloser with Bypass & Links 669 |  | 103SEG REG14-669 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 473 | 24529 | 12211 | 0.49782 | 0.019283 | 7682 | 177811 | 2013/2014 | May-2013 | 5 | 2013
28949 | Flying Debris | 2013-05-04 15:23 | 2013-05-04 | 2013-05-04 16:32 | Calculated | TF12H07 | TF12H07 - Transformer Fuse: TF12H07 |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:TSRWHR | Wind Borne Material - Non Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 69 | 1 | 24529 | 69 | 0.00281 | 4.0768e-05 | 15 | 1035 | 2013/2014 | May-2013 | 5 | 2013
28950 | Lightining | 2013-05-04 19:36 | 2013-05-04 | 2013-05-04 21:19 | Calculated | TF860 | TF860 - Transformer Fuse: TF860 |  | 122SEG443 | Wharepapa 122-01 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 3 | 24529 | 309 | 0.0126 | 0.0001223 | 15 | 1545 | 2013/2014 | May-2013 | 5 | 2013
28951 | Lightining | 2013-05-04 19:36 | 2013-05-04 | 2013-05-04 21:32 | Calculated | 443 | 443 - Fused Link 443 |  | 122SEG443 | Wharepapa 122-01 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 18 | 24529 | 2088 | 0.08512 | 0.00073383 | 130 | 15080 | 2013/2014 | May-2013 | 5 | 2013
28952 | Unknown | 2013-05-04 21:46 | 2013-05-04 | 2013-05-05 09:59 | Calculated | 5333 | 5333 - Fused Link 5333 |  | 426SEG5333-5532 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 733 | 37 | 24529 | 10720 | 0.43703 | 0.0015084 | 272.5 | 60977 | 2013/2014 | May-2013 | 5 | 2013
28953 | Birds | 2013-05-05 07:57 | 2013-05-05 | 2013-05-05 09:16 | Calculated | 764 | 764 - Solid Link 764 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 9 | 24529 | 711 | 0.02899 | 0.00036691 | 50 | 3949 | 2013/2014 | May-2013 | 5 | 2013
28954 | Broken Jumper @ ABS 295 | 2013-05-05 16:40 | 2013-05-05 | 2013-05-05 18:34 | Calculated | 5295 | 5295 - Air Break Switch 5295 |  | 413SEG5295-5454 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 117 | 24529 | 12054 | 0.49142 | 0.0047699 | 866 | 89016 | 2013/2014 | May-2013 | 5 | 2013
28955 | Trees | 2013-05-06 01:39 | 2013-05-06 | 2013-05-06 02:20 | Calculated | 104 | 104 - Circuit Breaker Rangitoto 104 |  | No Segment | 206-01 Waitete | Urban A | No Feeder |  |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 730 | 24529 | 29930 | 1.2202 | 0.029761 | 5766.5 | 236426 | 2013/2014 | May-2013 | 5 | 2013
28957 | Wind | 2013-05-06 07:49 | 2013-05-06 | 2013-05-06 09:41 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 26 | 24529 | 2912 | 0.11872 | 0.00106 | 330 | 36960 | 2013/2014 | May-2013 | 5 | 2013
28956 | Broken Xarm | 2013-05-06 08:10 | 2013-05-06 | 2013-05-06 12:01 | Calculated | TF990 | TF990 - Transformer Fuse: TF990 |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 231 | 4 | 24529 | 924 | 0.03767 | 0.00016307 | 15 | 3465 | 2013/2014 | May-2013 | 5 | 2013
28958 | Rat on ABS 5253 | 2013-05-07 01:19 | 2013-05-07 | 2013-05-07 10:52 | Calculated | 5254 | 5254 - Circuit Breaker 5254 |  | No Segment | 503-01 Nihiniho | Rural D | No Feeder |  |  | Birds & Animals | Animals | BANI:ANIM:AOTH | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 61 | 24529 | 427 | 0.01741 | 0.0024869 | 358.5 | 2509 | 2013/2014 | May-2013 | 5 | 2013
28960 | Refer 2013 / 155 Replace & Restrain Conductor | 2013-05-07 09:35 | 2013-05-07 | 2013-05-07 14:36 | Calculated | 1.27 | 1.27 - Fused Link 1.27 |  | 404SEGF1.27 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 301 | 6 | 24529 | 1806 | 0.07363 | 0.00024461 | 25 | 7525 | 2013/2014 | May-2013 | 5 | 2013
28959 | Refer 2013 / 152 Replace Poles and X-Arms | 2013-05-07 09:55 | 2013-05-07 | 2013-05-07 15:45 | Calculated | 652 | 652 - Load Break Switch 652 |  | 119SEG653-652 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 333 | 14 | 24529 | 4662 | 0.19006 | 0.00057075 | 160 | 53279 | 2013/2014 | May-2013 | 5 | 2013
28961 | L/V Repairs | 2013-05-07 15:29 | 2013-05-07 | 2013-05-07 16:11 | Calculated | TF9K5 | TF9K5 - Transformer Fuse: TF9K5 |  | 409SEG5134 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 2 | 24529 | 84 | 0.00342 | 8.1536e-05 | 15 | 630 | 2013/2014 | May-2013 | 5 | 2013
28963 | Faulty Lighting Arrestor - Refer USL 421 | 2013-05-08 09:31 | 2013-05-08 | 2013-05-08 12:32 | Calculated | 6005 | 6005 - Recloser 6005 |  | 610SEG6005-6004 | 516-01 Transpower National Park | Rural D | No Feeder |  |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 1631 | 24529 | 68502 | 2.7927 | 0.066493 | 8686 | 364811 | 2013/2014 | May-2013 | 5 | 2013
28962 | Refer 2013 / 153 Replace poles and X-Arms | 2013-05-08 10:00 | 2013-05-08 | 2013-05-08 15:40 | Calculated | 652 | 652 - Load Break Switch 652 |  | 119SEG653-652 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 299 | 14 | 24529 | 4186 | 0.17066 | 0.00057075 | 160 | 47839 | 2013/2014 | May-2013 | 5 | 2013
28964 | Refer USL 422 Replace Broken X-Arm at T 2728 | 2013-05-08 19:04 | 2013-05-08 | 2013-05-08 20:28 | Calculated | 787 | 787 - Load Break Switch 787 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 101 | 24529 | 6868 | 0.28 | 0.0041176 | 1335 | 90779 | 2013/2014 | May-2013 | 5 | 2013
28965 | Blown HV Fuse - Unknown Fault | 2013-05-09 06:24 | 2013-05-09 | 2013-05-09 08:08 | Calculated | TF11S25 | TF11S25 - Transformer Fuse: TF11S25 |  | 424SEG5200-6650 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 39 | 24529 | 4056 | 0.16536 | 0.00159 | 100 | 10399 | 2013/2014 | May-2013 | 5 | 2013
28967 | Old Age | 2013-05-09 10:37 | 2013-05-09 | 2013-05-09 12:10 | Calculated | TF1646 | TF1646 - Transformer Fuse: TF1646 |  | 113SEG1526-1525 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 4 | 24529 | 372 | 0.01517 | 0.00016307 | 15 | 1395 | 2013/2014 | May-2013 | 5 | 2013
28968 | Blown HV Fuse - Unknown Fault | 2013-05-09 12:28 | 2013-05-09 | 2013-05-09 14:10 | Calculated | TF4001 | TF4001 - Transformer Fuse: TF4001 |  | 426SEG5580-5239 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 102 | 1 | 24529 | 102 | 0.00416 | 4.0768e-05 | 15 | 1530 | 2013/2014 | May-2013 | 5 | 2013
28969 | Refer 2013 / 156 Upgrade 15KVA Transformer to 30KVA | 2013-05-10 09:03 | 2013-05-10 | 2013-05-10 12:13 | Calculated | TF8I64 | TF8I64 - Transformer Fuse: TF8I64 |  | 402SEG5482 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 190 | 5 | 24529 | 950 | 0.03873 | 0.00020384 | 30 | 5700 | 2013/2014 | May-2013 | 5 | 2013
28970 | Broken Pole | 2013-05-10 09:46 | 2013-05-10 | 2013-05-10 12:14 | Calculated | TF1076 | TF1076 - Transformer Fuse: TF1076 |  | 122SEG595 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 1 | 24529 | 148 | 0.00603 | 4.0768e-05 | 7.5 | 1110 | 2013/2014 | May-2013 | 5 | 2013
28971 | Refer 2013 / 157 Remove Link & Bypass at Sec 5511 | 2013-05-10 10:19 | 2013-05-10 | 2013-05-10 12:12 | Calculated | 5510 | 5510 - Fused Link 5510 |  | 410SEG5510-5511 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 113 | 39 | 24529 | 4407 | 0.17966 | 0.00159 | 236.5 | 26724 | 2013/2014 | May-2013 | 5 | 2013
28973 | Refer USL 423 Fault Beyond Sec 1531 | 2013-05-10 11:42 | 2013-05-10 | 2013-05-11 10:12 | Calculated | 1531 | 1531 - Sectionaliser 1531 |  | 113SEG1531-1501 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1350 | 18 | 24529 | 24048 | 0.98039 | 0.00073383 | 130 | 173924 | 2013/2014 | May-2013 | 5 | 2013
28972 | Change taps | 2013-05-10 12:08 | 2013-05-10 | 2013-05-10 12:26 | Calculated | TF9K5 | TF9K5 - Transformer Fuse: TF9K5 |  | 409SEG5134 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 18 | 2 | 24529 | 36 | 0.00147 | 8.1536e-05 | 15 | 270 | 2013/2014 | May-2013 | 5 | 2013
28974 | Trees - Made Safe | 2013-05-10 20:00 | 2013-05-10 | 2013-05-11 09:22 | Calculated | TF1378 | TF1378 - Transformer Fuse: TF1378 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 802 | 5 | 24529 | 4010 | 0.16348 | 0.00020384 | 60 | 48120 | 2013/2014 | May-2013 | 5 | 2013
28975 | Blown HV Fuse - Unknown Fault | 2013-05-11 05:03 | 2013-05-11 | 2013-05-11 06:28 | Calculated | TF1320 | TF1320 - Transformer Fuse: TF1320 |  | 122SEG702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 5 | 24529 | 425 | 0.01733 | 0.00020384 | 25 | 2125 | 2013/2014 | May-2013 | 5 | 2013
28976 | Check & Replace | 2013-05-11 15:22 | 2013-05-11 | 2013-05-11 15:25 | Calculated | 265 | 265 - Sectionaliser with Bypass & Links 265 |  | 107SEG262-176 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 13 | 24529 | 39 | 0.00159 | 0.00052998 | 130 | 390 | 2013/2014 | May-2013 | 5 | 2013
28977 | Bird contact with transformer | 2013-05-12 07:38 | 2013-05-12 | 2013-05-12 09:02 | Calculated | TF8G10 | TF8G10 - Transformer Fuse: TF8G10 |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 84 | 2 | 24529 | 168 | 0.00685 | 8.1536e-05 | 25 | 2100 | 2013/2014 | May-2013 | 5 | 2013
28978 | Old Age | 2013-05-12 09:46 | 2013-05-12 | 2013-05-12 10:54 | Calculated | TF9G6 | TF9G6 - Transformer Fuse: TF9G6 |  | 403SEG5887-5322 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 68 | 1 | 24529 | 68 | 0.00277 | 4.0768e-05 | 15 | 1020 | 2013/2014 | May-2013 | 5 | 2013
28979 | Refer 2013 / 159 Replace Faulty Lightining Arrestors | 2013-05-13 10:10 | 2013-05-13 | 2013-05-13 11:48 | Calculated | 5450 | 5450 - Fused Link 5450 |  | 409SEG5138-5235 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 98 | 1 | 24529 | 98 | 0.004 | 4.0768e-05 | 50 | 4900 | 2013/2014 | May-2013 | 5 | 2013
28980 | Refer 2013 / 158 Check Oil Level on TX 10S36 | 2013-05-13 11:06 | 2013-05-13 | 2013-05-13 14:09 | Calculated | 6189 | 6189 - Load Break Switch 6189 |  | 423SEG6188-6187 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 183 | 152 | 24529 | 27816 | 1.134 | 0.0061967 | 550 | 100649 | 2013/2014 | May-2013 | 5 | 2013
28981 | L/V Line Down | 2013-05-13 13:30 | 2013-05-13 | 2013-05-13 16:49 | Calculated | TF1004 | TF1004 - Transformer Fuse: TF1004 |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 4 | 24529 | 796 | 0.03245 | 0.00016307 | 30 | 5970 | 2013/2014 | May-2013 | 5 | 2013
28982 | Old Age | 2013-05-13 17:13 | 2013-05-13 | 2013-05-13 19:00 | Calculated | TF13K16 | TF13K16 - Transformer Fuse: TF13K16 |  | 410SEG5790-5703 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 1 | 24529 | 107 | 0.00436 | 4.0768e-05 | 15 | 1605 | 2013/2014 | May-2013 | 5 | 2013
28983 | Refer 2013 / 160 Replace Poles & X-Arms | 2013-05-14 09:02 | 2013-05-14 | 2013-05-14 15:19 | Calculated | 343 | 343 - Air Break Switch 343 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 377 | 41 | 24529 | 15457 | 0.63015 | 0.0016715 | 400 | 150800 | 2013/2014 | May-2013 | 5 | 2013
28984 | Old Age | 2013-05-14 15:36 | 2013-05-14 | 2013-05-14 18:00 | Calculated | TF2220 | TF2220 - Transformer Fuse: TF2220 |  | 128SEG1628 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 144 | 1 | 24529 | 144 | 0.00587 | 4.0768e-05 | 5 | 720 | 2013/2014 | May-2013 | 5 | 2013
28986 | Old Age | 2013-05-15 07:20 | 2013-05-15 | 2013-05-15 09:37 | Calculated | TF1527 | TF1527 - Transformer Fuse: TF1527 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 2 | 24529 | 274 | 0.01117 | 8.1536e-05 | 30 | 4110 | 2013/2014 | May-2013 | 5 | 2013
28985 | Birds | 2013-05-15 08:06 | 2013-05-15 | 2013-05-15 09:28 | Calculated | 655 | 655 - Fused Link 655 |  | 116SEG655 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 1 | 24529 | 82 | 0.00334 | 4.0768e-05 | 15 | 1230 | 2013/2014 | May-2013 | 5 | 2013
28987 | Change Transformer | 2013-05-15 09:30 | 2013-05-15 | 2013-05-15 10:41 | Calculated | TF2485 | TF2485 - Transformer Fuse: TF2485 |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 5 | 24529 | 355 | 0.01447 | 0.00020384 | 30 | 2130 | 2013/2014 | May-2013 | 5 | 2013
28989 | Change Transformer | 2013-05-15 10:03 | 2013-05-15 | 2013-05-15 11:54 | Calculated | TF917 | TF917 - Transformer Fuse: TF917 |  | 103SEG449 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 111 | 2 | 24529 | 222 | 0.00905 | 8.1536e-05 | 25 | 2775 | 2013/2014 | May-2013 | 5 | 2013
28988 | Refer 2013 / 161 Install New Pole & Tap-Off Links | 2013-05-15 10:06 | 2013-05-15 | 2013-05-15 13:50 | Calculated | 5602 | 5602 - Fused Link 5602 |  | 403SEG5602-5317 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 224 | 10 | 24529 | 2240 | 0.09132 | 0.00040768 | 80 | 17919 | 2013/2014 | May-2013 | 5 | 2013
28990 | Broken Pole | 2013-05-15 17:20 | 2013-05-15 | 2013-05-16 02:16 | Calculated | TF11S14 | TF11S14 - Transformer Fuse: TF11S14 |  | 424SEG6651-6652 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 536 | 84 | 24529 | 45024 | 1.8355 | 0.0034245 | 300 | 160799 | 2013/2014 | May-2013 | 5 | 2013
28991 | Jumper Off on 3 Phase | 2013-05-15 19:17 | 2013-05-15 | 2013-05-15 20:12 | Calculated | 440 | 440 - Recloser with Outgoing Link 440 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 62 | 24529 | 3122 | 0.12728 | 0.0025276 | 630.5 | 28197 | 2013/2014 | May-2013 | 5 | 2013
28993 | Change Faulty Transformer | 2013-05-16 10:40 | 2013-05-16 | 2013-05-16 12:50 | Calculated | TF3H12 | TF3H12 - Transformer Fuse: TF3H12 |  | 421SEG5436-5434 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 130 | 3 | 24529 | 390 | 0.0159 | 0.0001223 | 15 | 1950 | 2013/2014 | May-2013 | 5 | 2013
28994 | LV Checks & Change Taps | 2013-05-16 13:38 | 2013-05-16 | 2013-05-16 15:21 | Calculated | TF1650 | TF1650 - Transformer Fuse: TF1650 |  | 113SEG1532-1533 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 103 | 2 | 24529 | 206 | 0.0084 | 8.1536e-05 | 15 | 1545 | 2013/2014 | May-2013 | 5 | 2013
28995 | Broken Pole | 2013-05-18 11:27 | 2013-05-18 | 2013-05-18 15:28 | Calculated | TF9L6 | TF9L6 - Transformer Fuse: TF9L6 |  | 408SEG5406 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 241 | 5 | 24529 | 1205 | 0.04913 | 0.00020384 | 10 | 2410 | 2013/2014 | May-2013 | 5 | 2013
28996 | Lightning | 2013-05-18 11:35 | 2013-05-18 | 2013-05-18 13:15 | Calculated | 554 | 554 - Fused Link 554 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 15 | 24529 | 1094 | 0.0446 | 0.00061152 | 105 | 7745 | 2013/2014 | May-2013 | 5 | 2013
28997 | Lightning | 2013-05-18 17:39 | 2013-05-18 | 2013-05-18 21:16 | Calculated | TF637 | TF637 - Transformer Fuse: TF637 |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 217 | 2 | 24529 | 434 | 0.01769 | 8.1536e-05 | 25 | 5425 | 2013/2014 | May-2013 | 5 | 2013
28998 | Lightning | 2013-05-19 06:37 | 2013-05-19 | 2013-05-19 07:38 | Calculated | TF10 | TF10 - Transformer Fuse: TF10 |  | 104SEG207-546 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 44 | 24529 | 2684 | 0.10942 | 0.0017938 | 300 | 18299 | 2013/2014 | May-2013 | 5 | 2013
28999 | Lightning | 2013-05-19 10:24 | 2013-05-19 | 2013-05-19 11:45 | Calculated | TF2121 | TF2121 - Transformer Fuse: TF2121 |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 81 | 1 | 24529 | 81 | 0.0033 | 4.0768e-05 | 10 | 810 | 2013/2014 | May-2013 | 5 | 2013
29002 | Tap-Off Fuses Too Small ( HV Fuses blown) | 2013-05-20 09:53 | 2013-05-20 | 2013-05-20 11:45 | Calculated | TF8G10 | TF8G10 - Transformer Fuse: TF8G10 |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 112 | 2 | 24529 | 224 | 0.00913 | 8.1536e-05 | 25 | 2800 | 2013/2014 | May-2013 | 5 | 2013
29000 | Refer 2013 / 165 Treecutting, Pole & Stay Repairs, Install New Pole, Remove Redudant SWER | 2013-05-20 10:03 | 2013-05-20 | 2013-05-20 12:50 | Calculated | 6135 | 6135 - Recloser with Bypass 6135 |  | 417SEG5297-5245 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 167 | 405 | 24529 | 67635 | 2.7574 | 0.016511 | 2155 | 359884 | 2013/2014 | May-2013 | 5 | 2013
29001 | Tree Cutting - Remove HV Fuses for safety | 2013-05-20 10:24 | 2013-05-20 | 2013-05-20 12:33 | Calculated | TF284 | TF284 - Transformer Fuse: TF284 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 129 | 7 | 24529 | 903 | 0.03681 | 0.00028538 | 50 | 6449 | 2013/2014 | May-2013 | 5 | 2013
29003 | Sort Out Labling on RTE - Determine Correct Labling on RTE | 2013-05-20 11:47 | 2013-05-20 | 2013-05-20 12:56 | Calculated | TF3124 | TF3124 - Transformer Fuse: TF3124 |  | 123SEG1027-2113 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 69 | 2 | 24529 | 138 | 0.00563 | 8.1536e-05 | 50 | 3450 | 2013/2014 | May-2013 | 5 | 2013
29005 | Refer 2013 / 169 Changing Poles & X-Arms | 2013-05-21 08:02 | 2013-05-21 | 2013-05-21 16:35 | Calculated | 343 | 343 - Air Break Switch 343 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 486 | 99 | 24529 | 25154 | 1.0255 | 0.004036 | 990 | 254334 | 2013/2014 | May-2013 | 5 | 2013
29006 | Disconnet For Crane | 2013-05-21 08:53 | 2013-05-21 | 2013-05-21 11:55 | Calculated | TF3024 | TF3024 - Transformer Fuse: TF3024 |  | 101SEG526 | Caves 101-03 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 182 | 1 | 24529 | 182 | 0.00742 | 4.0768e-05 | 15 | 2730 | 2013/2014 | May-2013 | 5 | 2013
29007 | HV Line Clash | 2013-05-22 06:00 | 2013-05-22 | 2013-05-22 07:25 | Calculated | 5485 | 5485 - Fused Link 5485 |  | 408SEG5485-5791 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 20 | 24529 | 1700 | 0.06931 | 0.00081536 | 160 | 13600 | 2013/2014 | May-2013 | 5 | 2013
29008 | Refer 2013 / 169 Install New Xiria | 2013-05-22 08:05 | 2013-05-22 | 2013-05-22 16:05 | Calculated | 6418 | 6418 - Load Break Switch 6418 |  | 414SEG5767-6418 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 480 | 144 | 24529 | 49856 | 2.0325 | 0.0058706 | 1100 | 420999 | 2013/2014 | May-2013 | 5 | 2013
29009 | Refer 2013 / 171 Replace Till Box With Xiria | 2013-05-22 08:58 | 2013-05-22 | 2013-05-24 16:47 | Calculated | 5974 | 5974 - Load Break Switch 5974 |  | 419SEG5972-5973 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1205 | 5 | 24529 | 6025 | 0.24563 | 0.00020384 | 2150 | 2590750 | 2013/2014 | May-2013 | 5 | 2013
29010 | Refer 2013 / 166 Repair or Install New Stay | 2013-05-22 09:14 | 2013-05-22 | 2013-05-22 10:26 | Calculated | 5776 | 5776 - Fused Link 5776 |  | 402SEG5776 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 72 | 12 | 24529 | 864 | 0.03522 | 0.00048922 | 85 | 6120 | 2013/2014 | May-2013 | 5 | 2013
29011 | Change Transformer | 2013-05-22 10:23 | 2013-05-22 | 2013-05-22 13:58 | Calculated | 502 | 502 - Solid Link 502 |  | 119SEG502 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 215 | 2 | 24529 | 430 | 0.01753 | 8.1536e-05 | 150 | 32250 | 2013/2014 | May-2013 | 5 | 2013
29012 | Replace L/A | 2013-05-23 09:44 | 2013-05-23 | 2013-05-23 12:50 | Calculated | TF2578 | TF2578 - Transformer Fuse: TF2578 |  | 114SEG1122 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 186 | 1 | 24529 | 186 | 0.00758 | 4.0768e-05 | 7.5 | 1395 | 2013/2014 | May-2013 | 5 | 2013
29013 | SWER Backfeed | 2013-05-23 09:52 | 2013-05-23 | 2013-05-23 16:27 | Calculated | 1259 | 1259 - Solid Link 1259 |  | 117SEG1259-1722 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 5 | 39 | 24529 | 195 | 0.00795 | 0.00159 | 318 | 1590 | 2013/2014 | May-2013 | 5 | 2013
29014 | Lower Tap | 2013-05-23 10:39 | 2013-05-23 | 2013-05-23 11:51 | Calculated | TF1883 | TF1883 - Transformer Fuse: TF1883 |  | 128SEG1524-1261 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 3 | 24529 | 216 | 0.00881 | 0.0001223 | 15 | 1080 | 2013/2014 | May-2013 | 5 | 2013
29015 | Refer 2013 / 185 Replace X-Arms | 2013-05-24 09:34 | 2013-05-24 | 2013-05-24 15:29 | Calculated | 554 | 554 - Fused Link 554 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 355 | 15 | 24529 | 5325 | 0.21709 | 0.00061152 | 105 | 37275 | 2013/2014 | May-2013 | 5 | 2013
29016 | Refer 2013 / 173 Remove Redundant Tx 4Q2 | 2013-05-24 10:02 | 2013-05-24 | 2013-05-24 10:28 | Calculated | 5534 | 5534 - Sectionaliser 5534 |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 26 | 14 | 24529 | 364 | 0.01484 | 0.00057075 | 105 | 2730 | 2013/2014 | May-2013 | 5 | 2013
29017 | Blown HV Fuse - Unknown Fault | 2013-05-24 10:31 | 2013-05-24 | 2013-05-24 11:21 | Calculated | TF6J16 | TF6J16 - Transformer Fuse: TF6J16 |  | 402SEG5199-5115 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 50 | 1 | 24529 | 50 | 0.00204 | 4.0768e-05 | 10 | 500 | 2013/2014 | May-2013 | 5 | 2013
29018 | L/V Fault | 2013-05-26 02:30 | 2013-05-26 | 2013-05-26 04:35 | Calculated | TF719 | TF719 - Transformer Fuse: TF719 |  | 120SEG486-484 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 1 | 24529 | 125 | 0.0051 | 4.0768e-05 | 10 | 1250 | 2013/2014 | May-2013 | 5 | 2013
29019 | Birds | 2013-05-26 06:47 | 2013-05-26 | 2013-05-26 08:40 | Calculated | 609 | 609 - Circuit Breaker 609 (Rural Feeder) 609 |  | No Segment | 201-01 Taharoa | Rural D | No Feeder |  |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 116 | 24529 | 13108 | 0.53439 | 0.0047291 | 773 | 87348 | 2013/2014 | May-2013 | 5 | 2013
29020 | Line Down | 2013-05-26 09:50 | 2013-05-26 | 2013-05-26 11:22 | Calculated | 504 | 504 - Air Break Switch 504 |  | 126SEG504-578 | Rural 126-01 | Rural D | Rural | Taharoa Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 105 | 24529 | 9660 | 0.39382 | 0.0042806 | 590 | 54279 | 2013/2014 | May-2013 | 5 | 2013
29021 | Line Clash | 2013-05-26 11:20 | 2013-05-26 | 2013-05-26 12:46 | Calculated | TF1943 | TF1943 - Transformer Fuse: TF1943 |  | 114SEG1105-1118 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFPL | Fault on Private Line - Affecting Network | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 5 | 24529 | 430 | 0.01753 | 0.00020384 | 50 | 4300 | 2013/2014 | May-2013 | 5 | 2013
29022 | Line Down | 2013-05-27 06:52 | 2013-05-27 | 2013-05-27 19:28 | Calculated | 1628 | 1628 - Air Break Switch 1628 |  | 128SEG1628 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDI | Conductor Failure - Insulated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 756 | 6 | 24529 | 4536 | 0.18492 | 0.00024461 | 60 | 45360 | 2013/2014 | May-2013 | 5 | 2013
29023 | Refer 2013 / 181 Replace Pole 1032091 | 2013-05-27 10:03 | 2013-05-27 | 2013-05-27 12:46 | Calculated | 260 | 260 - Fused Link 260 |  | 103SEG669-REG4 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 163 | 22 | 24529 | 3586 | 0.14619 | 0.0008969 | 190.5 | 31051 | 2013/2014 | May-2013 | 5 | 2013
29024 | Install New Earth Mat | 2013-05-28 10:07 | 2013-05-28 | 2013-05-28 12:12 | Calculated | TF2075 | TF2075 - Transformer Fuse: TF2075 |  | 117SEG1721-1307 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 125 | 3 | 24529 | 375 | 0.01529 | 0.0001223 | 15 | 1875 | 2013/2014 | May-2013 | 5 | 2013
29026 | Duck | 2013-05-29 07:03 | 2013-05-29 | 2013-05-29 07:11 | Calculated | 6063 | 6063 - Circuit Breaker 6063 |  | 404SEG6063-A1.3 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 2229 | 24529 | 17832 | 0.72698 | 0.090872 | 14093.5 | 112747 | 2013/2014 | May-2013 | 5 | 2013
29027 | Refer 2013 / 183 Replace Poles | 2013-05-29 08:14 | 2013-05-29 | 2013-05-29 14:12 | Calculated | 619 | 619 - Air Break Switch 619 |  | 122SEG619-REG35 | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 290 | 87 | 24529 | 25230 | 1.0286 | 0.0035468 | 775 | 224749 | 2013/2014 | May-2013 | 5 | 2013
29028 | Install New Earth Mat | 2013-05-29 10:08 | 2013-05-29 | 2013-05-29 13:45 | Calculated | TF2094 | TF2094 - Transformer Fuse: TF2094 |  | 117SEG1721-1307 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 217 | 5 | 24529 | 1085 | 0.04423 | 0.00020384 | 30 | 6510 | 2013/2014 | May-2013 | 5 | 2013
29029 | Lower Tap | 2013-05-29 15:21 | 2013-05-29 | 2013-05-29 15:49 | Calculated | TF1816 | TF1816 - Transformer Fuse: TF1816 |  | 103SEG1346-1326 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLS | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 28 | 2 | 24529 | 56 | 0.00228 | 8.1536e-05 | 10 | 280 | 2013/2014 | May-2013 | 5 | 2013
29030 | L/V Line Down | 2013-05-30 07:18 | 2013-05-30 | 2013-05-30 10:55 | Calculated | TF886 | TF886 - Transformer Fuse: TF886 |  | 122SEG702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 3 | 24529 | 651 | 0.02654 | 0.0001223 | 30 | 6510 | 2013/2014 | May-2013 | 5 | 2013
29031 | Blown HV Fuse - Unknown Fault | 2013-05-30 07:20 | 2013-05-30 | 2013-05-30 11:11 | Calculated | TF362 | TF362 - Transformer Fuse: TF362 |  | 102SEG1271-336 | Hangatiki East 102-01 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 231 | 2 | 24529 | 462 | 0.01883 | 8.1536e-05 | 15 | 3465 | 2013/2014 | May-2013 | 5 | 2013
29032 | Refer 2013 / 178B Replace Damaged Magnafix Switchgear in the Tavern Kiosk | 2013-05-30 08:00 | 2013-05-30 | 2013-05-30 18:41 | Calculated | 5154 | 5154 - Circuit Breaker 5154 |  | No Segment | 513-01 Tawhai | Rural D | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 641 | 138 | 24529 | 88458 | 3.6063 | 0.005626 | 12065 | 7733665 | 2013/2014 | May-2013 | 5 | 2013
29034 | Replace L/V Pole | 2013-05-30 09:31 | 2013-05-30 | 2013-05-30 14:57 | Calculated | TF1205 | TF1205 - Transformer Fuse: TF1205 |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 326 | 27 | 24529 | 8802 | 0.35884 | 0.0011007 | 100 | 32599 | 2013/2014 | May-2013 | 5 | 2013
29035 | L/V Fault | 2013-05-30 12:26 | 2013-05-30 | 2013-05-30 13:49 | Calculated | TF1921 | TF1921 - Transformer Fuse: TF1921 |  | 117SEG687-1289 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 1 | 24529 | 83 | 0.00338 | 4.0768e-05 | 30 | 2490 | 2013/2014 | May-2013 | 5 | 2013
29036 | Line Down | 2013-05-31 07:13 | 2013-05-31 | 2013-05-31 09:58 | Calculated | 1413 | 1413 - Circuit Breaker 1413 |  | 217SEGT3326-1413 | Taharoa B 302-02 | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 165 | 322 | 24529 | 53130 | 2.166 | 0.013127 | 2486 | 410189 | 2013/2014 | May-2013 | 5 | 2013
29037 | Blown HV Fuse - Unknown Fault | 2013-05-31 07:17 | 2013-05-31 | 2013-05-31 08:13 | Calculated | TF3140 | TF3140 - Transformer Fuse: TF3140 |  | 103SEG200-225 | Benneydale 103-01 | Urban A | Benneydale | Waitete Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24529 |  | 0 | 0 |  |  | 2013/2014 | May-2013 | 5 | 2013
29038 | Clash | 2013-06-01 11:00 | 2013-06-01 | 2013-06-01 12:47 | Calculated | TF2822 | TF2822 - Transformer Fuse: TF2822 |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 1 | 24549 | 107 | 0.00436 | 4.0735e-05 | 15 | 1605 | 2013/2014 | June-2013 | 6 | 2013
29039 | Old Age | 2013-06-04 08:51 | 2013-06-04 | 2013-06-04 10:22 | Calculated | TF3H9 | TF3H9 - Transformer Fuse: TF3H9 |  | 421SEG5434-5851 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 91 | 1 | 24549 | 91 | 0.00371 | 4.0735e-05 | 10 | 910 | 2013/2014 | June-2013 | 6 | 2013
29040 | Install New Earth Mat | 2013-06-04 10:02 | 2013-06-04 | 2013-06-04 12:07 | Calculated | TF1827 | TF1827 - Transformer Fuse: TF1827 |  | 117SEG1728-1260 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 125 | 2 | 24549 | 250 | 0.01018 | 8.147e-05 | 7.5 | 937 | 2013/2014 | June-2013 | 6 | 2013
29041 | L/V Neutral Fault | 2013-06-04 12:53 | 2013-06-04 | 2013-06-04 14:04 | Calculated | TF709 | TF709 - Transformer Fuse: TF709 |  | 118SEG496-1741 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 49 | 24549 | 3479 | 0.14172 | 0.001996 | 200 | 14199 | 2013/2014 | June-2013 | 6 | 2013
29042 | Tree Felled Through Private | 2013-06-04 14:10 | 2013-06-04 | 2013-06-04 14:59 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 26 | 24549 | 1274 | 0.0519 | 0.0010591 | 285 | 13964 | 2013/2014 | June-2013 | 6 | 2013
29043 | Refer 2013 / 187 11KV Extension to New 50KVA Tx 3417 | 2013-06-05 09:40 | 2013-06-05 | 2013-06-05 14:42 | Calculated | 335 | 335 - Air Break Switch 335 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 32 | 24549 | 9664 | 0.39366 | 0.0013035 | 275 | 83049 | 2013/2014 | June-2013 | 6 | 2013
29044 | SWER Backfeed Replace Tube Links & Repair Staywire | 2013-06-05 10:05 | 2013-06-05 | 2013-06-05 12:17 | Calculated | 5499 | 5499 - Fused Link 5499 |  | 410SEG5499-5559 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 110 | 8 | 24549 | 880 | 0.03585 | 0.00032588 | 70 | 7700 | 2013/2014 | June-2013 | 6 | 2013
29045 | Possum | 2013-06-06 08:07 | 2013-06-06 | 2013-06-06 09:23 | Calculated | TF469 | TF469 - Transformer Fuse: TF469 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 4 | 24549 | 304 | 0.01238 | 0.00016294 | 25 | 1900 | 2013/2014 | June-2013 | 6 | 2013
29047 | T11 Buchholz Trip | 2013-06-07 07:17 | 2013-06-07 | 2013-06-07 11:16 | Calculated | 681 | 681 - Incoming Circuit Breaker 681 |  | No Segment | 207-01 Wairere Falls | Rural D | No Feeder |  |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 2045 | 24549 | 90915 | 3.7034 | 0.083303 | 14502 | 649277 | 2013/2014 | June-2013 | 6 | 2013
29048 | Repair L/V Connection | 2013-06-07 10:31 | 2013-06-07 | 2013-06-07 11:14 | Calculated | TF20L34 | TF20L34 - Transformer Fuse: TF20L34 |  | 414SEG6175 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 43 | 89 | 24549 | 3827 | 0.15589 | 0.0036254 | 250 | 10749 | 2013/2014 | June-2013 | 6 | 2013
29049 | Refer 2013 / 193 Cleaning Transformer Room | 2013-06-08 09:11 | 2013-06-08 | 2013-06-08 12:29 | Calculated | TF1927A | TF1927A - Transformer Fuse: TF1927A |  | 115SEG682-1701 | Mokauiti 115-01 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 198 | 1 | 24549 | 198 | 0.00807 | 4.0735e-05 | 300 | 59400 | 2013/2014 | June-2013 | 6 | 2013
29050 | Refer 2013 / 188 Re-instate 300KVA Transformer | 2013-06-09 09:02 | 2013-06-09 | 2013-06-09 11:12 | Calculated | 6442 | 6442 - Circuit Breaker 6642 |  | 414SEG6440-6443 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 130 | 41 | 24549 | 5330 | 0.21712 | 0.0016701 | 200 | 25999 | 2013/2014 | June-2013 | 6 | 2013
29051 | Blown HV Fuse - Unknown Fault | 2013-06-09 09:30 | 2013-06-09 | 2013-06-09 11:04 | Calculated | TF14M03 | TF14M03 - Transformer Fuse: TF14M03 |  | 411SEG5148-5373 | National Park 411-02 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 3 | 24549 | 282 | 0.01149 | 0.0001222 | 100 | 9399 | 2013/2014 | June-2013 | 6 | 2013
29052 | Blown HV Fuse - Unknown Fault | 2013-06-09 16:10 | 2013-06-09 | 2013-06-09 17:35 | Calculated | TF1528 | TF1528 - Transformer Fuse: TF1528 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 3 | 24549 | 255 | 0.01039 | 0.0001222 | 25 | 2124 | 2013/2014 | June-2013 | 6 | 2013
29053 | Unknown | 2013-06-09 18:39 | 2013-06-09 | 2013-06-09 20:05 | Calculated | 241 | 241 - Fused Link 241 |  | 119SEG414-241 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 11 | 24549 | 946 | 0.03854 | 0.00044808 | 235 | 20210 | 2013/2014 | June-2013 | 6 | 2013
29054 | Line Down | 2013-06-10 05:23 | 2013-06-10 | 2013-06-10 10:40 | Calculated | 1325 | 1325 - Fused Link 1325 |  | 103SEG1335-1301 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 317 | 17 | 24549 | 3179 | 0.1295 | 0.00069249 | 148 | 26856 | 2013/2014 | June-2013 | 6 | 2013
29055 | Replace X/arms | 2013-06-10 10:14 | 2013-06-10 | 2013-06-10 15:37 | Calculated | TF4034 | TF4034 - Transformer Fuse: TF4034 |  | 407SEG5868-5126 | Manunui 407-01 (was Affco) | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 323 | 6 | 24549 | 1938 | 0.07894 | 0.00024441 | 30 | 9690 | 2013/2014 | June-2013 | 6 | 2013
29056 | Faulty H/V Connection | 2013-06-10 11:05 | 2013-06-10 | 2013-06-10 12:18 | Calculated | TF1405 | TF1405 - Transformer Fuse: TF1405 |  | 126SEG2121-504 | Rural 126-03 | Rural D | Rural | Taharoa Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 1 | 24549 | 73 | 0.00297 | 4.0735e-05 | 15 | 1095 | 2013/2014 | June-2013 | 6 | 2013
29057 | L/V Line Down | 2013-06-10 13:07 | 2013-06-10 | 2013-06-10 16:48 | Calculated | TF2868 | TF2868 - Transformer Fuse: TF2868 |  | 125SEG268-281 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 1 | 24549 | 221 | 0.009 | 4.0735e-05 | 3 | 663 | 2013/2014 | June-2013 | 6 | 2013
29058 | Unknown | 2013-06-10 23:12 | 2013-06-10 | 2013-06-10 23:28 | Calculated | 796 | 796 - Circuit Breaker 796 |  | 301SEG1418-796 | Taharoa A 301-02 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24549 |  | 0 | 0 |  |  | 2013/2014 | June-2013 | 6 | 2013
29059 | Old Age | 2013-06-11 07:54 | 2013-06-11 | 2013-06-11 08:28 | Calculated | 4.9 | 4.9 - Solid Link 4.9 |  | 402SEGL4.9 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 69 | 24549 | 2346 | 0.09556 | 0.0028107 | 250 | 8499 | 2013/2014 | June-2013 | 6 | 2013
29060 | Refer 2013 / 195 Replace Poles & X-Arms | 2013-06-11 09:04 | 2013-06-11 | 2013-06-11 15:37 | Calculated | 343 | 343 - Air Break Switch 343 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 393 | 41 | 24549 | 16113 | 0.65636 | 0.0016701 | 400 | 157200 | 2013/2014 | June-2013 | 6 | 2013
29061 | Refer 2013 / 198 Replace Private Line H/V Poles & L/V X-Arm | 2013-06-11 09:54 | 2013-06-11 | 2013-06-11 14:37 | Calculated | 1317 | 1317 - Fused Link 1317 |  | 117SEG1317 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 283 | 7 | 24549 | 1981 | 0.0807 | 0.00028514 | 70 | 19809 | 2013/2014 | June-2013 | 6 | 2013
29062 | Refer 2013 / 196 Changing Poles & X-Arms | 2013-06-12 08:06 | 2013-06-12 | 2013-06-12 16:35 | Calculated | 343 | 343 - Air Break Switch 343 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 470 | 99 | 24549 | 24671 | 1.005 | 0.0040328 | 990 | 249594 | 2013/2014 | June-2013 | 6 | 2013
29064 | Broken DDO at Tx645 | 2013-06-12 12:41 | 2013-06-12 | 2013-06-12 13:45 | Calculated | 382 | 382 - Fused Link 382 |  | 111SEG382 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 14 | 24549 | 896 | 0.0365 | 0.00057029 | 125 | 8000 | 2013/2014 | June-2013 | 6 | 2013
29066 | Line Down | 2013-06-12 13:21 | 2013-06-12 | 2013-06-12 18:21 | Calculated | 5936 | 5936 - Fused Link 5936 |  | 408SEG5936-5557 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 300 | 36 | 24549 | 10800 | 0.43994 | 0.0014665 | 161 | 48299 | 2013/2014 | June-2013 | 6 | 2013
29069 | Jumper Off at Pole 2 | 2013-06-15 20:15 | 2013-06-15 | 2013-06-15 21:48 | Calculated | 546 | 546 - Air Break Switch 546 |  | 104SEG546-215 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 61 | 24549 | 2806 | 0.1143 | 0.0024848 | 800 | 36799 | 2013/2014 | June-2013 | 6 | 2013
29070 | Tree in L/V | 2013-06-16 08:21 | 2013-06-16 | 2013-06-16 10:03 | Calculated | TF9L6 | TF9L6 - Transformer Fuse: TF9L6 |  | 408SEG5406 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 102 | 5 | 24549 | 510 | 0.02077 | 0.00020367 | 10 | 1020 | 2013/2014 | June-2013 | 6 | 2013
29071 | Land Slip - Screw Anchor | 2013-06-16 13:29 | 2013-06-16 | 2013-06-16 14:23 | Calculated | 547 | 547 - Fused Link 547 |  | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 54 | 25 | 24549 | 1350 | 0.05499 | 0.0010184 | 270 | 14580 | 2013/2014 | June-2013 | 6 | 2013
29072 | Old Age | 2013-06-16 18:37 | 2013-06-16 | 2013-06-16 20:09 | Calculated | TF1694 | TF1694 - Transformer Fuse: TF1694 |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 3 | 24549 | 276 | 0.01124 | 0.0001222 | 15 | 1380 | 2013/2014 | June-2013 | 6 | 2013
29073 | Upgrade Earth Mat | 2013-06-17 09:49 | 2013-06-17 | 2013-06-17 11:34 | Calculated | TF2578 | TF2578 - Transformer Fuse: TF2578 |  | 114SEG1122 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 105 | 1 | 24549 | 105 | 0.00428 | 4.0735e-05 | 7.5 | 787 | 2013/2014 | June-2013 | 6 | 2013
29074 | Replace Tx Structure | 2013-06-17 10:02 | 2013-06-17 | 2013-06-17 15:54 | Calculated | TF1136 | TF1136 - Transformer Fuse: TF1136 |  | 106SEG112-REG30 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 352 | 3 | 24549 | 1056 | 0.04302 | 0.0001222 | 15 | 5280 | 2013/2014 | June-2013 | 6 | 2013
29075 | Old Age | 2013-06-17 11:36 | 2013-06-17 | 2013-06-17 14:05 | Calculated | TF4Q12 | TF4Q12 - Transformer Fuse: TF4Q12 |  | 426SEG5333-5532 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 1 | 24549 | 149 | 0.00607 | 4.0735e-05 | 7.5 | 1117 | 2013/2014 | June-2013 | 6 | 2013
29076 | Jumper Off L/A at Tx2501 | 2013-06-18 08:10 | 2013-06-18 | 2013-06-18 11:23 | Calculated | 2102 | 2102 - Circuit Breaker Mareatai 11 kV 2102 |  | No Segment | 210-01 Maraetai | Rural D | No Feeder |  |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 575 | 24549 | 24803 | 1.0104 | 0.023423 | 6195 | 258614 | 2013/2014 | June-2013 | 6 | 2013
29077 | L/V Line Down | 2013-06-18 09:54 | 2013-06-18 | 2013-06-18 11:58 | Calculated | TF1121 | TF1121 - Transformer Fuse: TF1121 |  | 107SEG234 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 3 | 24549 | 372 | 0.01515 | 0.0001222 | 15 | 1860 | 2013/2014 | June-2013 | 6 | 2013
29078 | L/V Fault | 2013-06-18 13:03 | 2013-06-18 | 2013-06-18 14:04 | Calculated | TF235 | TF235 - Transformer Fuse: TF235 |  | 111SEG342-544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 3 | 24549 | 183 | 0.00745 | 0.0001222 | 25 | 1524 | 2013/2014 | June-2013 | 6 | 2013
29079 | Refer 2013 / 208 Replace Private Line H/V Poles & L/V X/arm | 2013-06-19 10:00 | 2013-06-19 | 2013-06-19 12:00 | Calculated | 1317 | 1317 - Fused Link 1317 |  | 117SEG1317 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 120 | 7 | 24549 | 840 | 0.03422 | 0.00028514 | 70 | 8399 | 2013/2014 | June-2013 | 6 | 2013
29081 | Disconnect For Safety | 2013-06-20 08:30 | 2013-06-20 | 2013-06-20 12:06 | Calculated | TF1251 | TF1251 - Transformer Fuse: TF1251 |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 216 | 10 | 24549 | 2160 | 0.08799 | 0.00040735 | 30 | 6480 | 2013/2014 | June-2013 | 6 | 2013
29082 | Pole Down | 2013-06-20 12:50 | 2013-06-20 | 2013-06-20 18:06 | Calculated | 714 | 714 - Recloser with Bypass 714 |  | 103SEG598-714 | Benneydale 103-07 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 278 | 340 | 24549 | 7601 | 0.30963 | 0.01385 | 4607 | 73531 | 2013/2014 | June-2013 | 6 | 2013
29083 | Extreme Weather | 2013-06-21 04:56 | 2013-06-21 | 2013-06-21 07:12 | Calculated | 21N11 | 21N11 - 1 Phase : 15.00 kVA : POLEMNT |  | 416SEG5523-5554 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Environmental | WEAT:STQS25:WORC | Cold / Snow Loading | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 151 | 24549 | 20536 | 0.83653 | 0.006151 | 1666 | 226575 | 2013/2014 | June-2013 | 6 | 2013
29084 | Extreme Weather | 2013-06-21 06:20 | 2013-06-21 | 2013-06-21 08:11 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | Environmental | WEAT:STQS25:WORC | Cold / Snow Loading | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 26 | 24549 | 2886 | 0.11756 | 0.0010591 | 285 | 31634 | 2013/2014 | June-2013 | 6 | 2013
29085 | Broken X/arm at Pole 37 | 2013-06-21 07:17 | 2013-06-21 | 2013-06-21 13:25 | Calculated | 5144 | 5144 - Circuit Breaker with Bypass 5144 |  | 411SEG5144-5769 | National Park 411-01 | Rural D | National Park | National Park Zone Substation |  | Weather | Environmental | WEAT:STQS25:WORC | Cold / Snow Loading | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 301 | 604 | 24549 | 79662 | 3.245 | 0.024604 | 16347.5 | 2491700 | 2013/2014 | June-2013 | 6 | 2013
29086 | Line Down | 2013-06-21 08:35 | 2013-06-21 | 2013-06-22 11:40 | Calculated | 5477 | 5477 - Air Break Switch 5477 |  | 609SEG5477-5160 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Environmental | WEAT:STQS25:WORC | Cold / Snow Loading | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 282 | 4 | 24549 | 1119 | 0.04558 | 0.00016294 | 450 | 126000 | 2013/2014 | June-2013 | 6 | 2013
29088 | Upgarde Transformer | 2013-06-21 09:45 | 2013-06-21 | 2013-06-21 11:27 | Calculated | TF206 | TF206 - Transformer Fuse: TF206 |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 13 | 24549 | 1326 | 0.05401 | 0.00052955 | 50 | 5099 | 2013/2014 | June-2013 | 6 | 2013
29089 | Farmer vs L/V | 2013-06-21 11:18 | 2013-06-21 | 2013-06-21 12:17 | Calculated | TF643 | TF643 - Transformer Fuse: TF643 |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 3 | 24549 | 177 | 0.00721 | 0.0001222 | 25 | 1474 | 2013/2014 | June-2013 | 6 | 2013
29090 | Extreme Weather | 2013-06-21 11:19 | 2013-06-21 | 2013-06-21 16:47 | Calculated | 5162 | 5162 - Fused Link 5162 |  | 411SEG5147-5775 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Weather | Environmental | WEAT:STQS25:WORC | Cold / Snow Loading | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 328 | 5 | 24549 | 1640 | 0.06681 | 0.00020367 | 45 | 14760 | 2013/2014 | June-2013 | 6 | 2013
29093 | Extreme Weather | 2013-06-21 13:37 | 2013-06-21 | 2013-06-21 15:31 | Calculated | TF21M3 | TF21M3 - Transformer Fuse: TF21M3 |  | 416SEG6118-5961 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Environmental | WEAT:STQS25:WORC | Cold / Snow Loading | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 1 | 24549 | 114 | 0.00464 | 4.0735e-05 | 15 | 1710 | 2013/2014 | June-2013 | 6 | 2013
29091 | Extreme Weather | 2013-06-21 13:44 | 2013-06-21 | 2013-06-21 15:42 | Calculated | TF385 | TF385 - Transformer Fuse: TF385 |  | 109SEG341-587 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Environmental | WEAT:STQS25:WORC | Cold / Snow Loading | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 2 | 24549 | 236 | 0.00961 | 8.147e-05 | 30 | 3540 | 2013/2014 | June-2013 | 6 | 2013
29092 | Extreme Weather | 2013-06-21 14:45 | 2013-06-21 | 2013-06-21 15:21 | Calculated | TF15L09 | TF15L09 - Transformer Fuse: TF15L09 |  | 411SEG5147-5775 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Weather | Environmental | WEAT:STQS25:WORC | Cold / Snow Loading | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 1 | 24549 | 36 | 0.00147 | 4.0735e-05 | 30 | 1080 | 2013/2014 | June-2013 | 6 | 2013
29094 | Truck vs Pole | 2013-06-22 04:45 | 2013-06-22 | 2013-06-22 12:35 | Calculated | 5718 | 5718 - Air Break Switch 5718 |  | 416SEG5718-5677 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 446 | 647 | 24549 | 63550 | 2.5887 | 0.026355 | 5576 | 466804 | 2013/2014 | June-2013 | 6 | 2013
29095 | Unknown Earth Fault | 2013-06-22 19:45 | 2013-06-22 | 2013-06-22 19:55 | Calculated | 796 | 796 - Circuit Breaker 796 |  | 301SEG1418-796 | Taharoa A 301-02 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24549 |  | 0 | 0 |  |  | 2013/2014 | June-2013 | 6 | 2013
29096 | Line Clash | 2013-06-23 13:09 | 2013-06-23 | 2013-06-23 14:31 | Calculated | TF23M01 | TF23M01 - Transformer Fuse: TF23M01 |  | 416SEG5686 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 3 | 24549 | 246 | 0.01002 | 0.0001222 | 10 | 819 | 2013/2014 | June-2013 | 6 | 2013
29097 | Line Clash (Horse in Paddock) | 2013-06-23 19:30 | 2013-06-23 | 2013-06-23 20:30 | Calculated | TF7D1 | TF7D1 - Transformer Fuse: TF7D1 |  | 413SEG5509 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AFAR | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 3 | 24549 | 180 | 0.00733 | 0.0001222 | 15 | 900 | 2013/2014 | June-2013 | 6 | 2013
29098 | Refer 2012 / 213 Change X/arms & Poles | 2013-06-24 09:15 | 2013-06-24 | 2013-06-24 15:45 | Calculated | 2164 | 2164 - Fused Link 2164 |  | 110SEG642-343 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 390 | 6 | 24549 | 2340 | 0.09532 | 0.00024441 | 45 | 17550 | 2013/2014 | June-2013 | 6 | 2013
29099 | L/V Fault | 2013-06-24 09:25 | 2013-06-24 | 2013-06-24 12:25 | Calculated | TF4G3 | TF4G3 - Transformer Fuse: TF4G3 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 180 | 16 | 24549 | 1046 | 0.04261 | 0.00065176 | 135 | 8580 | 2013/2014 | June-2013 | 6 | 2013
29100 | Refer 2013 / 214 Repalce Rusty TX915 | 2013-06-24 10:10 | 2013-06-24 | 2013-06-24 12:00 | Calculated | 459 | 459 - Air Break Switch 459 |  | 103SEG453-459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 110 | 6 | 24549 | 660 | 0.02689 | 0.00024441 | 65 | 7150 | 2013/2014 | June-2013 | 6 | 2013
29101 | Replace Faulty Insulator | 2013-06-24 11:51 | 2013-06-24 | 2013-06-24 13:31 | Calculated | 142 | 142 - (RC) Air Break Switch 142 |  | 301SEG140-142 | Taharoa A 301-01 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Asset Related | Insulator | FAIL:FINS2:FIND1 | Insulator - Dust - Tracking | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24549 |  | 0 | 0 |  |  | 2013/2014 | June-2013 | 6 | 2013
29102 | Unknown | 2013-06-24 12:22 | 2013-06-24 | 2013-06-24 14:15 | Calculated | 755 | 755 - Fused Link 755 |  | 101SEG752-755 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 6 | 24549 | 630 | 0.02566 | 0.00024441 | 60 | 6300 | 2013/2014 | June-2013 | 6 | 2013
29103 | Old Age | 2013-06-24 12:23 | 2013-06-24 | 2013-06-24 18:30 | Calculated | TF2213 | TF2213 - Transformer Fuse: TF2213 |  | 128SEG1631 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 367 | 1 | 24549 | 367 | 0.01495 | 4.0735e-05 | 15 | 5505 | 2013/2014 | June-2013 | 6 | 2013
29105 | L/V Maintenace | 2013-06-25 09:32 | 2013-06-25 | 2013-06-25 15:11 | Calculated | TF2193 | TF2193 - Transformer Fuse: TF2193 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 339 | 27 | 24549 | 9153 | 0.37285 | 0.0010998 | 100 | 33899 | 2013/2014 | June-2013 | 6 | 2013
29106 | L/V Maintenace | 2013-06-25 09:53 | 2013-06-25 | 2013-06-25 16:32 | Calculated | TF2267 | TF2267 - Transformer Fuse: TF2267 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 399 | 28 | 24549 | 11172 | 0.45509 | 0.0011406 | 100 | 39899 | 2013/2014 | June-2013 | 6 | 2013
29107 | Refer 2013 / 215 Replace Faulty Link | 2013-06-25 10:02 | 2013-06-25 | 2013-06-25 11:21 | Calculated | 5588 | 5588 - Air Break Switch 5588 |  | 426SEG5588-5583 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 79 | 33 | 24549 | 2134 | 0.08693 | 0.0013443 | 245 | 15509 | 2013/2014 | June-2013 | 6 | 2013
29108 | Cable Fault To Tx10S42 | 2013-06-25 12:52 | 2013-06-25 | 2013-06-25 21:35 | Calculated | TF10S42 | TF10S42 - Transformer Fuse: TF10S42 |  | 423SEG5209-6180 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 523 | 142 | 24549 | 50346 | 2.0508 | 0.0057843 | 450 | 161749 | 2013/2014 | June-2013 | 6 | 2013
29109 | Refer 2013 / 216 Dismantle SWER To Tx 1817 | 2013-06-26 09:35 | 2013-06-26 | 2013-06-26 10:45 | Calculated | 1346 | 1346 - Sectionaliser 1346 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 70 | 7 | 24549 | 490 | 0.01996 | 0.00028514 | 57.5 | 4024 | 2013/2014 | June-2013 | 6 | 2013
29110 | Upgrade Earth Mat | 2013-06-26 09:41 | 2013-06-26 | 2013-06-26 11:58 | Calculated | TF2079 | TF2079 - Transformer Fuse: TF2079 |  | 117SEG2179 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 137 | 2 | 24549 | 274 | 0.01116 | 8.147e-05 | 10 | 1370 | 2013/2014 | June-2013 | 6 | 2013
29111 | D/C Gen Set & R/C Cable | 2013-06-26 17:03 | 2013-06-26 | 2013-06-26 18:36 | Calculated | 6198 | 6198 - Fused Link 6198 |  | 423SEG6197-6198 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 93 | 142 | 24549 | 13206 | 0.53794 | 0.0057843 | 450 | 41849 | 2013/2014 | June-2013 | 6 | 2013
29112 | SWER Backfeed | 2013-06-27 09:01 | 2013-06-27 | 2013-06-27 16:07 | Calculated | 1259 | 1259 - Solid Link 1259 |  | 117SEG1259-1722 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 348 | 42 | 24549 | 1396 | 0.05687 | 0.0017109 | 335.5 | 10615 | 2013/2014 | June-2013 | 6 | 2013
29113 | SWER Backfeed - Refer 2013 / 218 Repalce Faulty Link 936 | 2013-06-27 09:08 | 2013-06-27 | 2013-06-27 13:34 | Calculated | 5557 | 5557 - Solid Link 5557 |  | 408SEG5557-5380 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 72 | 49 | 24549 | 1668 | 0.06795 | 0.001996 | 246 | 10264 | 2013/2014 | June-2013 | 6 | 2013
29114 | Lower Tap | 2013-06-27 13:40 | 2013-06-27 | 2013-06-27 13:45 | Calculated | TF915 | TF915 - Transformer Fuse: TF915 |  | 103SEG459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 5 | 2 | 24549 | 10 | 0.00041 | 8.147e-05 | 10 | 50 | 2013/2014 | June-2013 | 6 | 2013
29115 | Jumper Off @ Tap Off | 2013-06-28 09:21 | 2013-06-28 | 2013-06-28 10:56 | Calculated | TF2246 | TF2246 - Transformer Fuse: TF2246 |  | 115SEG1707-1648 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 2 | 24549 | 190 | 0.00774 | 8.147e-05 | 30 | 2850 | 2013/2014 | June-2013 | 6 | 2013
29116 | Upgrade Tx | 2013-06-28 10:18 | 2013-06-28 | 2013-06-28 14:49 | Calculated | TF590 | TF590 - Transformer Fuse: TF590 |  | 109SEG348-522 | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 271 | 2 | 24549 | 542 | 0.02208 | 8.147e-05 | 25 | 6775 | 2013/2014 | June-2013 | 6 | 2013
29117 | C Phase E/F in Ripple Plant | 2013-06-29 06:25 | 2013-06-29 | 2013-06-29 06:29 | Calculated | 732 | 732 - Circuit Breaker Atiamuri 33 kV Supply 732 |  | No Segment | 215-01 Atiamuri | Rural C | No Feeder |  |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 4 | 2545 | 24549 | 10180 | 0.41468 | 0.10367 | 28602.5868 | 114410 | 2013/2014 | June-2013 | 6 | 2013
29118 | Unknown | 2013-06-29 11:31 | 2013-06-29 | 2013-06-29 14:00 | Calculated | 5731 | 5731 - Fused Link 5731 |  | 609SEG5731 | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24549 |  | 0 | 0 |  |  | 2013/2014 | June-2013 | 6 | 2013
29119 | Unknown E/F | 2013-06-30 02:58 | 2013-06-30 | 2013-06-30 03:02 | Calculated | 109 | 109 - Recloser with bypass 109 |  | 101SEG110-109 | Caves 101-09 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 98 | 24549 | 392 | 0.01597 | 0.003992 | 791 | 3163 | 2013/2014 | June-2013 | 6 | 2013
29120 | Refer 2013 / 220 Upgrade Insulator @ Tx 8G8 to 18KV | 2013-07-01 09:05 | 2013-07-01 | 2013-07-01 11:23 | Calculated | 5443 | 5443 - Fused Link 5443 |  | 403SEG5766-5460 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 138 | 4 | 24550 | 552 | 0.02248 | 0.00016293 | 45 | 6210 | 2013/2014 | July-2013 | 7 | 2013
29121 | Unknown | 2013-07-01 09:21 | 2013-07-01 | 2013-07-01 14:28 | Calculated | 5733 | 5733 - Fused Link 5733 |  | 609SEG5163-5544 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24550 |  | 0 | 0 |  |  | 2013/2014 | July-2013 | 7 | 2013
29122 | Digger vs Line | 2013-07-01 15:03 | 2013-07-01 | 2013-07-01 16:12 | Calculated | 5768 | 5768 - Recloser with Bypass 5768 |  | 408SEG5384-5116 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 69 | 24550 | 4761 | 0.19393 | 0.0028106 | 391 | 26978 | 2013/2014 | July-2013 | 7 | 2013
29123 | Refer 2013 / 221 Changing Poles & X-Arms | 2013-07-02 09:02 | 2013-07-02 | 2013-07-02 15:56 | Calculated | 1722 | 1722 - Fused Link 1722 |  | 117SEG1722-1721 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 414 | 19 | 24550 | 7866 | 0.32041 | 0.00077393 | 143 | 59202 | 2013/2014 | July-2013 | 7 | 2013
29124 | Old Age | 2013-07-02 09:12 | 2013-07-02 | 2013-07-02 11:54 | Calculated | TF15L12 | TF15L12 - Transformer Fuse: TF15L12 |  | 411SEG5769-5147 | National Park 411-01 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 2 | 24550 | 324 | 0.0132 | 8.1466e-05 | 15 | 2430 | 2013/2014 | July-2013 | 7 | 2013
29125 | Bird | 2013-07-02 11:20 | 2013-07-02 | 2013-07-02 13:32 | Calculated | TF6J17 | TF6J17 - Transformer Fuse: TF6J17 |  | 402SEG5354 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 132 | 1 | 24550 | 132 | 0.00538 | 4.0733e-05 | 7.5 | 990 | 2013/2014 | July-2013 | 7 | 2013
29126 | Private Line Down (P 28) | 2013-07-02 14:27 | 2013-07-02 | 2013-07-03 13:30 | Calculated | 1542 | 1542 - Fused Link 1542 |  | 113SEG1543 | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFPL | Fault on Private Line - Affecting Network | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1340 | 22 | 24550 | 9908 | 0.40358 | 0.00089613 | 138 | 67242 | 2013/2014 | July-2013 | 7 | 2013
29127 | Fell Out - Vibration | 2013-07-03 09:05 | 2013-07-03 | 2013-07-03 10:33 | Calculated | TF3Q2 | TF3Q2 - Transformer Fuse: TF3Q2 |  | 124SEG5537-5324 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 3 | 24550 | 264 | 0.01075 | 0.0001222 | 15 | 1320 | 2013/2014 | July-2013 | 7 | 2013
29128 | Pole Slip | 2013-07-03 12:51 | 2013-07-03 | 2013-07-03 15:08 | Calculated | 547 | 547 - Fused Link 547 |  | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOL1 | Pole Leaning | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 25 | 24550 | 3425 | 0.13951 | 0.0010183 | 270 | 36990 | 2013/2014 | July-2013 | 7 | 2013
29129 | Refer 2012 / 234 Replace 2 Poles, Tx 6H15, H/V X/arm & Earthing | 2013-07-04 09:10 | 2013-07-04 | 2013-07-04 16:29 | Calculated | 5339 | 5339 - Fused Link 5339 |  | 402SEG5339 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 439 | 10 | 24550 | 4390 | 0.17882 | 0.00040733 | 75 | 32925 | 2013/2014 | July-2013 | 7 | 2013
29131 | Change DDO | 2013-07-04 09:56 | 2013-07-04 | 2013-07-04 11:16 | Calculated | 1119 | 1119 - Fused Link 1119 |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 5 | 24550 | 400 | 0.01629 | 0.00020367 | 30 | 2400 | 2013/2014 | July-2013 | 7 | 2013
29132 | Refer 2013 / 223 Replace faulty TX 9D5 | 2013-07-04 10:05 | 2013-07-04 | 2013-07-04 14:52 | Calculated | 5562 | 5562 - Fused Link 5562 |  | 413SEG5577-5456 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 287 | 5 | 24550 | 1435 | 0.05845 | 0.00020367 | 28 | 8036 | 2013/2014 | July-2013 | 7 | 2013
29133 | Faulty L/A | 2013-07-04 15:49 | 2013-07-04 | 2013-07-04 16:47 | Calculated | TF1572 | TF1572 - Transformer Fuse: TF1572 |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 2 | 24550 | 116 | 0.00473 | 8.1466e-05 | 15 | 870 | 2013/2014 | July-2013 | 7 | 2013
29134 | Over Current | 2013-07-04 19:26 | 2013-07-04 | 2013-07-04 21:00 | Calculated | 349 | 349 - Automated Air Break Switch 349 |  | 109SEG348-522 | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 949 | 24550 | 27873 | 1.1354 | 0.038656 | 9407.5 | 243417 | 2013/2014 | July-2013 | 7 | 2013
29135 | Faulty L/A | 2013-07-05 09:22 | 2013-07-05 | 2013-07-05 10:08 | Calculated | TF1572 | TF1572 - Transformer Fuse: TF1572 |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 2 | 24550 | 92 | 0.00375 | 8.1466e-05 | 15 | 690 | 2013/2014 | July-2013 | 7 | 2013
29136 | Earth Mat Upgrade | 2013-07-05 09:43 | 2013-07-05 | 2013-07-05 12:18 | Calculated | TF2638 | TF2638 - Transformer Fuse: TF2638 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 155 | 1 | 24550 | 155 | 0.00631 | 4.0733e-05 | 25 | 3875 | 2013/2014 | July-2013 | 7 | 2013
29137 | Faulty Insulator | 2013-07-05 12:40 | 2013-07-05 | 2013-07-05 13:54 | Calculated | 5924 | 5924 - Earth Working Link 5924 |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 3 | 24550 | 222 | 0.00904 | 0.0001222 | 30 | 2220 | 2013/2014 | July-2013 | 7 | 2013
29138 | Unknown - Generation island | 2013-07-06 09:15 | 2013-07-06 | 2013-07-06 09:21 | Calculated | 594 | 594 - Recloser 594 |  | No Segment | 205-01 Gadsby Road | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24550 |  | 0 | 0 |  |  | 2013/2014 | July-2013 | 7 | 2013
29139 | Wind | 2013-07-06 18:00 | 2013-07-06 | 2013-07-06 19:20 | Calculated | TF6J14 | TF6J14 - Transformer Fuse: TF6J14 |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 2 | 24550 | 160 | 0.00652 | 8.1466e-05 | 10 | 800 | 2013/2014 | July-2013 | 7 | 2013
29140 | Faulty Tx | 2013-07-06 19:45 | 2013-07-06 | 2013-07-07 11:18 | Calculated | 06J14 | 06J14 - 1 Phase : 10.00 kVA : POLEMNT |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 933 | 2 | 24550 | 1866 | 0.07601 | 8.1466e-05 | 10 | 9330 | 2013/2014 | July-2013 | 7 | 2013
29141 | Vehicle vs Stay Wire | 2013-07-07 21:20 | 2013-07-07 | 2013-07-07 23:28 | Calculated | TF2185 | TF2185 - Transformer Fuse: TF2185 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 128 | 2 | 24550 | 256 | 0.01043 | 8.1466e-05 | 10 | 1280 | 2013/2014 | July-2013 | 7 | 2013
29142 | Refer 2013 / 227 Replace Structure & Install G/M Tx 1A50 | 2013-07-08 08:34 | 2013-07-08 | 2013-07-08 15:50 | Calculated | 4.7 | 4.7 - Solid Link 4.7 |  | 402SEGL4.7 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 436 | 19 | 24550 | 8284 | 0.33743 | 0.00077393 | 100 | 43599 | 2013/2014 | July-2013 | 7 | 2013
29143 | Old Age | 2013-07-08 13:42 | 2013-07-08 | 2013-07-08 14:57 | Calculated | TF1315 | TF1315 - Transformer Fuse: TF1315 |  | 109SEG337-2229 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 24550 | 75 | 0.00305 | 4.0733e-05 | 25 | 1875 | 2013/2014 | July-2013 | 7 | 2013
29144 | Blown HV Fuse - Unknown Fault | 2013-07-09 08:44 | 2013-07-09 | 2013-07-09 09:50 | Calculated | TF1982 | TF1982 - Transformer Fuse: TF1982 |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 2 | 24550 | 132 | 0.00538 | 8.1466e-05 | 10 | 660 | 2013/2014 | July-2013 | 7 | 2013
29145 | Refer 2013 / 228 Replace Pole 1143088 | 2013-07-09 09:33 | 2013-07-09 | 2013-07-09 15:29 | Calculated | 1100 | 1100 - Sectionaliser with Incoming Link 1100 |  | 114SEG1127-1100 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 356 | 13 | 24550 | 4628 | 0.18851 | 0.00052953 | 90 | 32039 | 2013/2014 | July-2013 | 7 | 2013
29146 | Refer 2013 / 229 Reconfigure L/A's & Upgrade Earth Mat @ Tx 8I64 | 2013-07-09 10:05 | 2013-07-09 | 2013-07-09 12:56 | Calculated | 482 | 482 - Air Break Switch 482 |  | 120SEG482-480 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 171 | 10 | 24550 | 1710 | 0.06965 | 0.00040733 | 200 | 34199 | 2013/2014 | July-2013 | 7 | 2013
29147 | Swan / Clash | 2013-07-09 21:09 | 2013-07-09 | 2013-07-09 22:27 | Calculated | 763 | 763 - Fused Link 763 |  | 108SEG763-2140 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 2 | 24550 | 156 | 0.00635 | 8.1466e-05 | 600 | 46800 | 2013/2014 | July-2013 | 7 | 2013
29148 | Refer 2013 / 231 Install Vertical ABS For Private Spur To G/M Tx | 2013-07-10 09:52 | 2013-07-10 | 2013-07-10 13:58 | Calculated | 377 | 377 - Fused Link 377 |  | 122SEG392-568 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 246 | 18 | 24550 | 4428 | 0.18037 | 0.0007332 | 145 | 35670 | 2013/2014 | July-2013 | 7 | 2013
29149 | Unknown | 2013-07-10 12:28 | 2013-07-10 | 2013-07-10 14:21 | Calculated | T342 | T342 - 1 Phase : 10.00 kVA : POLEMNT |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 3 | 24550 | 339 | 0.01381 | 0.0001222 | 10 | 1129 | 2013/2014 | July-2013 | 7 | 2013
29150 | Lighting - Burnt Out Fuse | 2013-07-10 20:51 | 2013-07-10 | 2013-07-10 21:45 | Calculated | 1315 | 1315 - Sectionaliser 1315 |  | 117SEG1315-1326 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 54 | 14 | 24550 | 756 | 0.03079 | 0.00057026 | 97.5 | 5265 | 2013/2014 | July-2013 | 7 | 2013
29153 | Refer 2013 / 232 Restrain & Install H/V Fuses @ Pole 1081015 | 2013-07-11 09:02 | 2013-07-11 | 2013-07-11 11:58 | Calculated | 764 | 764 - Solid Link 764 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 176 | 9 | 24550 | 1584 | 0.06452 | 0.0003666 | 50 | 8799 | 2013/2014 | July-2013 | 7 | 2013
29155 | Snow | 2013-07-11 10:27 | 2013-07-11 | 2013-07-11 13:28 | Calculated | TF20M5 | TF20M5 - Transformer Fuse: TF20M5 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | Environmental | WEAT:STQS25:WORC | Cold / Snow Loading | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 181 | 2 | 24550 | 362 | 0.01475 | 8.1466e-05 | 15 | 2715 | 2013/2014 | July-2013 | 7 | 2013
29156 | Vehicle vs Line / L/V Line Down | 2013-07-11 11:58 | 2013-07-11 | 2013-07-11 12:58 | Calculated | TF1196 | TF1196 - Transformer Fuse: TF1196 |  | 107SEG1020-515 | Oparure 107-03 | Rural C | Oparure | Gadsby Road Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 8 | 24550 | 480 | 0.01955 | 0.00032587 | 30 | 1800 | 2013/2014 | July-2013 | 7 | 2013
29157 | Faulty Tx 20M1 | 2013-07-11 16:05 | 2013-07-11 | 2013-07-12 12:22 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1217 | 26 | 24550 | 8619 | 0.35108 | 0.0010591 | 285 | 161659 | 2013/2014 | July-2013 | 7 | 2013
29159 | Scheduled Maintenance | 2013-07-12 12:52 | 2013-07-12 | 2013-07-12 14:51 | Calculated | TF1667 | TF1667 - Transformer Fuse: TF1667 |  | 116SEG1312-1362 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 3 | 24550 | 357 | 0.01454 | 0.0001222 | 15 | 1785 | 2013/2014 | July-2013 | 7 | 2013
29160 | Tree on line poles 38 - 39 | 2013-07-12 17:53 | 2013-07-12 | 2013-07-12 21:12 | Calculated | 5623 | 5623 - Electronic Sectionaliser 5623 |  | 409SEG5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 15 | 24550 | 2985 | 0.12159 | 0.000611 | 72.5 | 14427 | 2013/2014 | July-2013 | 7 | 2013
29161 | Another Tree on Line | 2013-07-13 07:19 | 2013-07-13 | 2013-07-13 09:16 | Calculated | 5623 | 5623 - Electronic Sectionaliser 5623 |  | 409SEG5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 15 | 24550 | 1755 | 0.07149 | 0.000611 | 72.5 | 8482 | 2013/2014 | July-2013 | 7 | 2013
29162 | Vehicle vs Pole 29 | 2013-07-13 17:40 | 2013-07-13 | 2013-07-13 22:03 | Calculated | TF20K4 | TF20K4 - Transformer Fuse: TF20K4 |  | 416SEG5672-5718 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 263 | 27 | 24550 | 7101 | 0.28925 | 0.0010998 | 175 | 46025 | 2013/2014 | July-2013 | 7 | 2013
29163 | Wind / Trees | 2013-07-14 17:38 | 2013-07-14 | 2013-07-14 18:53 | Calculated | TF1982 | TF1982 - Transformer Fuse: TF1982 |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 2 | 24550 | 150 | 0.00611 | 8.1466e-05 | 10 | 750 | 2013/2014 | July-2013 | 7 | 2013
29165 | Wind / Falling Trees | 2013-07-14 19:00 | 2013-07-14 | 2013-07-16 15:20 | Calculated | 5590 | 5590 - Fused Link 5590 |  | 418SEG5590-5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 2660 | 70 | 24550 | 19572 | 0.79723 | 0.0028513 | 346 | 185786 | 2013/2014 | July-2013 | 7 | 2013
29164 | Line Down @ Pole 32/53 | 2013-07-14 20:20 | 2013-07-14 | 2013-07-15 01:00 | Calculated | 09P01 | 09P01 - 1 Phase : 25.00 kVA : POLEMNT |  | 426SEG5240-5242 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 280 | 40 | 24550 | 14688 | 0.59829 | 0.0016293 | 212.5 | 78802 | 2013/2014 | July-2013 | 7 | 2013
29166 | Wind | 2013-07-14 20:41 | 2013-07-14 | 2013-07-14 21:38 | Calculated | 5599 | 5599 - Recloser with Bypass & Links 5599 |  | 409SEG5598-5599 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 57 | 31 | 24550 | 1767 | 0.07198 | 0.0012627 | 275 | 15674 | 2013/2014 | July-2013 | 7 | 2013
29167 | Wind / Clash | 2013-07-14 22:06 | 2013-07-14 | 2013-07-14 22:42 | Calculated | TF492 | TF492 - Transformer Fuse: TF492 |  | 109SEG302 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 2 | 24550 | 72 | 0.00293 | 8.1466e-05 | 25 | 900 | 2013/2014 | July-2013 | 7 | 2013
29168 | Unknown | 2013-07-15 00:58 | 2013-07-15 | 2013-07-15 08:08 | Calculated | 440 | 440 - Recloser with Outgoing Link 440 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 281 | 49 | 24550 | 13769 | 0.56086 | 0.0019959 | 355.5 | 99895 | 2013/2014 | July-2013 | 7 | 2013
29169 | Jumper Off @ Links 207 | 2013-07-15 01:17 | 2013-07-15 | 2013-07-15 01:52 | Calculated | 5207 | 5207 - Air Break Switch 5207 |  | 424SEG5200-6650 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 45 | 24550 | 1575 | 0.06415 | 0.001833 | 500 | 17499 | 2013/2014 | July-2013 | 7 | 2013
29170 | Conductor Clash | 2013-07-15 08:17 | 2013-07-15 | 2013-07-15 10:45 | Calculated | TF1203 | TF1203 - Transformer Fuse: TF1203 |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 3 | 24550 | 444 | 0.01809 | 0.0001222 | 15 | 2220 | 2013/2014 | July-2013 | 7 | 2013
29171 | Refer 2013 / 241 Change poles & X/arms | 2013-07-15 09:31 | 2013-07-15 | 2013-07-15 12:50 | Calculated | 390 | 390 - Air Break Switch 390 |  | 110SEG390-2144 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 199 | 19 | 24550 | 3781 | 0.15401 | 0.00077393 | 185 | 36814 | 2013/2014 | July-2013 | 7 | 2013
29172 | More Trees Through Line | 2013-07-15 10:58 | 2013-07-15 | 2013-07-15 11:01 | Calculated | 5584 | 5584 - Recloser with Bypass & Links 5584 |  | 418SEG5584-5591 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 3 | 70 | 24550 | 210 | 0.00855 | 0.0028513 | 346 | 1037 | 2013/2014 | July-2013 | 7 | 2013
29173 | L/V fault / make Safe | 2013-07-15 11:40 | 2013-07-15 | 2013-07-15 12:34 | Calculated | TF9K1 | TF9K1 - Transformer Fuse: TF9K1 |  | 409SEG5412-5861 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1 | 24550 | 54 | 0.0022 | 4.0733e-05 | 15 | 810 | 2013/2014 | July-2013 | 7 | 2013
29174 | Faulty Transformer | 2013-07-15 11:49 | 2013-07-15 | 2013-07-15 15:41 | Calculated | TF2819 | TF2819 - Transformer Fuse: TF2819 |  | 120SEG416-479 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 232 | 1 | 24550 | 232 | 0.00945 | 4.0733e-05 | 10 | 2320 | 2013/2014 | July-2013 | 7 | 2013
29175 | Broken Pole | 2013-07-15 14:51 | 2013-07-15 | 2013-07-15 16:30 | Calculated | 5412 | 5412 - Fused Link 5412 |  | 409SEG5412-5861 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 2 | 24550 | 198 | 0.00807 | 8.1466e-05 | 30 | 2970 | 2013/2014 | July-2013 | 7 | 2013
29176 | Unknown Fault | 2013-07-15 16:47 | 2013-07-15 | 2013-07-16 15:20 | Calculated | 5739 | 5739 - Sectionaliser with Bypass & Links 5739 |  | 421SEG5436-5434 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1353 | 2 | 24550 | 2706 | 0.11022 | 8.1466e-05 | 3 | 4059 | 2013/2014 | July-2013 | 7 | 2013
29177 | Refer 2013 / 242 Changing Poles & X/arms SWER Backfeed | 2013-07-16 09:02 | 2013-07-16 | 2013-07-16 16:03 | Calculated | 1722 | 1722 - Fused Link 1722 |  | 117SEG1722-1721 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 356 | 39 | 24550 | 7115 | 0.28982 | 0.0015886 | 313 | 60385 | 2013/2014 | July-2013 | 7 | 2013
29179 | Refer 2013 / 244 Changing Poles & X/Arms | 2013-07-17 09:03 | 2013-07-17 | 2013-07-17 14:31 | Calculated | 1722 | 1722 - Fused Link 1722 |  | 117SEG1722-1721 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 328 | 19 | 24550 | 6232 | 0.25385 | 0.00077393 | 143 | 46904 | 2013/2014 | July-2013 | 7 | 2013
29180 | Refer 2013 / 245 Restrain 11kV Line @ Pole 1241260 & Replace Sleeves | 2013-07-17 10:07 | 2013-07-17 | 2013-07-17 10:57 | Calculated | TF2544 | TF2544 - Transformer Fuse: TF2544 |  | 129SEG434-426 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 50 | 9 | 24550 | 450 | 0.01833 | 0.0003666 | 130 | 6500 | 2013/2014 | July-2013 | 7 | 2013
29181 | Broken X/arm Sect 5534 | 2013-07-17 10:18 | 2013-07-17 | 2013-07-17 12:42 | Calculated | 5537 | 5537 - Fused Link 5537 |  | 124SEG5537-5324 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 31 | 24550 | 4464 | 0.18183 | 0.0012627 | 212.5 | 30599 | 2013/2014 | July-2013 | 7 | 2013
29183 | Replace Tx Structure | 2013-07-18 09:34 | 2013-07-18 | 2013-07-18 15:26 | Calculated | TF2094 | TF2094 - Transformer Fuse: TF2094 |  | 117SEG1721-1307 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 352 | 5 | 24550 | 1760 | 0.07169 | 0.00020367 | 30 | 10560 | 2013/2014 | July-2013 | 7 | 2013
29182 | Refer 2013 / 239 Reworks | 2013-07-18 09:53 | 2013-07-18 | 2013-07-18 15:52 | Calculated | REG7J | REG7J - Incoming Solid Link REG7J |  | 103SEG107-REG7 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 271 | 29 | 24550 | 7859 | 0.32012 | 0.0011813 | 5202 | 55555 | 2013/2014 | July-2013 | 7 | 2013
29184 | Refer 2013 / 246 Replacing L/A's & Polymers | 2013-07-18 10:17 | 2013-07-18 | 2013-07-18 12:44 | Calculated | 752 | 752 - Fused Link 752 |  | 101SEG291-752 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 147 | 6 | 24550 | 882 | 0.03593 | 0.0002444 | 60 | 8820 | 2013/2014 | July-2013 | 7 | 2013
29185 | Trees | 2013-07-18 14:55 | 2013-07-18 | 2013-07-18 19:14 | Calculated | 5590 | 5590 - Fused Link 5590 |  | 418SEG5590-5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 259 | 70 | 24550 | 7672 | 0.31251 | 0.0028513 | 346 | 43465 | 2013/2014 | July-2013 | 7 | 2013
29186 | Refer 2013 / 247 Replace Pole 1242245 With Bulldozer | 2013-07-19 10:10 | 2013-07-19 | 2013-07-19 14:50 | Calculated | 1749 | 1749 - Solid Links 1749 |  | 129SEG1749-2204 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 216 | 6 | 24550 | 1296 | 0.05279 | 0.0002444 | 45 | 9720 | 2013/2014 | July-2013 | 7 | 2013
29190 | Refer 2013 / 243 Remove Redundant Tx 7D18 | 2013-07-19 12:03 | 2013-07-19 | 2013-07-19 12:37 | Calculated | 5283 | 5283 - Fused Link 5283 |  | 413SEG5283-5507 | Ohura 413-03 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 34 | 19 | 24550 | 646 | 0.02631 | 0.00077393 | 143 | 4861 | 2013/2014 | July-2013 | 7 | 2013
29192 | Treecutting | 2013-07-20 09:12 | 2013-07-20 | 2013-07-20 15:08 | Calculated | TF979 | TF979 - Transformer Fuse: TF979 |  | 120SEG667 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 356 | 3 | 24550 | 1068 | 0.0435 | 0.0001222 | 65 | 23140 | 2013/2014 | July-2013 | 7 | 2013
29193 | Birds | 2013-07-21 14:28 | 2013-07-21 | 2013-07-21 15:25 | Calculated | TF2711 | TF2711 - Transformer Fuse: TF2711 |  | 129SEG447 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 2 | 24550 | 114 | 0.00464 | 8.1466e-05 | 50 | 2850 | 2013/2014 | July-2013 | 7 | 2013
29195 | Vehicle vs Line | 2013-07-22 16:05 | 2013-07-22 | 2013-07-22 20:51 | Calculated | TF8J46 | TF8J46 - Transformer Fuse: TF8J46 |  | 408SEG5390-5621 | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 286 | 38 | 24550 | 10868 | 0.44269 | 0.0015479 | 250 | 71499 | 2013/2014 | July-2013 | 7 | 2013
29194 | Change Tx | 2013-07-22 16:30 | 2013-07-22 | 2013-07-22 16:59 | Calculated | TF1830 | TF1830 - Transformer Fuse: TF1830 |  | 117SEG1296-1273 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 29 | 3 | 24550 | 87 | 0.00354 | 0.0001222 | 10 | 289 | 2013/2014 | July-2013 | 7 | 2013
29196 | Refer 2013 / 251 Replace Poles & X/arms | 2013-07-23 09:05 | 2013-07-23 | 2013-07-23 15:14 | Calculated | 1312 | 1312 - Air Break Switch 1312 |  | 116SEG1312-1362 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 369 | 46 | 24550 | 16974 | 0.69141 | 0.0018737 | 448 | 165311 | 2013/2014 | July-2013 | 7 | 2013
29197 | Refer 2013 / 252 Install 2 New Tx's - Tx 3418 & 3419 | 2013-07-23 09:31 | 2013-07-23 | 2013-07-23 13:40 | Calculated | TF1267 | TF1267 - Transformer Fuse TF1267 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 249 | 15 | 24550 | 3735 | 0.15214 | 0.000611 | 130 | 32370 | 2013/2014 | July-2013 | 7 | 2013
29198 | Line Down | 2013-07-23 10:26 | 2013-07-23 | 2013-07-23 12:08 | Calculated | TF241 | TF241 - Transformer Fuse: TF241 |  | 111SEG339-346 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 5 | 24550 | 510 | 0.02077 | 0.00020367 | 25 | 2550 | 2013/2014 | July-2013 | 7 | 2013
29199 | Faulty L/A | 2013-07-23 11:46 | 2013-07-23 | 2013-07-23 12:15 | Calculated | TF2711 | TF2711 - Transformer Fuse: TF2711 |  | 129SEG447 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 2 | 24550 | 58 | 0.00236 | 8.1466e-05 | 50 | 1450 | 2013/2014 | July-2013 | 7 | 2013
29200 | Refer 2013 / 254Replace Pole 1041056 (ABS523) | 2013-07-24 09:08 | 2013-07-24 | 2013-07-24 15:55 | Calculated | 523 | 523 - Air Break Switch 523 |  | 104SEG523 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 407 | 65 | 24550 | 26455 | 1.0776 | 0.0026477 | 375 | 152624 | 2013/2014 | July-2013 | 7 | 2013
29201 | Faulty L/A at ABS 5357 | 2013-07-24 10:18 | 2013-07-24 | 2013-07-24 11:45 | Calculated | 1.41 | 1.41 - Air Break Switch 1.41 |  | 404SEGA1.41-5357 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 1720 | 24550 | 58808 | 2.3954 | 0.070061 | 10461.5 | 355386 | 2013/2014 | July-2013 | 7 | 2013
29202 | Old Age | 2013-07-24 23:04 | 2013-07-24 | 2013-07-24 23:45 | Calculated | TF866 | TF866 - Transformer Fuse: TF866 |  | 107SEG384-706 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 3 | 24550 | 123 | 0.00501 | 0.0001222 | 15 | 615 | 2013/2014 | July-2013 | 7 | 2013
29203 | L/V Maintenance | 2013-07-25 10:27 | 2013-07-25 | 2013-07-25 14:05 | Calculated | TF15L05 | TF15L05 - Transformer Fuse: TF15L05 |  | 411SEG5147-5775 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 218 | 1 | 24550 | 218 | 0.00888 | 4.0733e-05 | 75 | 16350 | 2013/2014 | July-2013 | 7 | 2013
29204 | Repair Staywire | 2013-07-25 11:47 | 2013-07-25 | 2013-07-25 14:26 | Calculated | TF696 | TF696 - Transformer Fuse: TF696 |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Pole | FAIL:FPOL2:OIWAWD | Broken Stay Wire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 3 | 24550 | 477 | 0.01943 | 0.0001222 | 30 | 4770 | 2013/2014 | July-2013 | 7 | 2013
29205 | Faulty Insulator Pole 148 | 2013-07-25 15:05 | 2013-07-25 | 2013-07-25 15:19 | Calculated | 268 | 268 - Air Break Switch 268 |  | 125SEG268-281 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 96 | 24550 | 1344 | 0.05475 | 0.0039104 | 798 | 11171 | 2013/2014 | July-2013 | 7 | 2013
29206 | Refer 2013 / 257 Replace Burnt Tx Pole - Tx 2201 | 2013-07-26 09:03 | 2013-07-26 | 2013-07-26 12:23 | Calculated | TF2201 | TF2201 - Transformer Fuse: TF2201 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 200 | 143 | 24550 | 16368 | 0.66672 | 0.0058248 | 863.5 | 97591 | 2013/2014 | July-2013 | 7 | 2013
29207 | Solid Link Fell Out | 2013-07-26 12:07 | 2013-07-26 | 2013-07-26 12:52 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 26 | 24550 | 1170 | 0.04766 | 0.0010591 | 330 | 14850 | 2013/2014 | July-2013 | 7 | 2013
29208 | Vehicle vs Pole | 2013-07-29 07:49 | 2013-07-29 | 2013-07-29 16:32 | Calculated | TF10S16 | TF10S16 - Transformer Fuse: TF10S16 |  | 424SEG6651-6652 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 523 | 100 | 24550 | 35636 | 1.4516 | 0.0040733 | 500 | 198699 | 2013/2014 | July-2013 | 7 | 2013
29209 | L/V maintenance | 2013-07-29 09:30 | 2013-07-29 | 2013-07-29 14:25 | Calculated | TF445 | TF445 - Transformer Fuse: TF445 |  | 105SEG204-202 | Te Kuiti Town 105-01 | Urban A | Te Kuiti Town | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 295 | 21 | 24550 | 6195 | 0.25234 | 0.0008554 | 200 | 58999 | 2013/2014 | July-2013 | 7 | 2013
29210 | Unknown | 2013-07-29 10:31 | 2013-07-29 | 2013-07-29 11:49 | Calculated | 5440 | 5440 - Recloser with Bypass & Links 5440 |  | 409SEG5439-5440 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 78 | 22 | 24550 | 1716 | 0.0699 | 0.00089613 | 187.5 | 14625 | 2013/2014 | July-2013 | 7 | 2013
29211 | Refer 2013 / 662 Install New Tx 3422 On Pole 4 | 2013-07-30 09:32 | 2013-07-30 | 2013-07-30 12:04 | Calculated | 292 | 292 - Air Break Switch 292 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 152 | 8 | 24550 | 1216 | 0.04953 | 0.00032587 | 78 | 11856 | 2013/2014 | July-2013 | 7 | 2013
29212 | Connect Gen Set | 2013-07-30 13:10 | 2013-07-30 | 2013-07-30 14:07 | Calculated | TF4237 | TF4237 - Transformer Fuse: TF4237 |  | 421SEG5874-6730 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 57 | 1 | 24550 | 57 | 0.00232 | 4.0733e-05 | 50 | 2850 | 2013/2014 | July-2013 | 7 | 2013
29213 | Magpie | 2013-07-30 17:03 | 2013-07-30 | 2013-07-30 17:45 | Calculated | TF12K11 | TF12K11 - Transformer Fuse: TF12K11 |  | 409SEG5335-5113 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 1 | 24550 | 42 | 0.00171 | 4.0733e-05 | 3 | 126 | 2013/2014 | July-2013 | 7 | 2013
29214 | Jumper Off at ABS 5150 | 2013-07-30 18:22 | 2013-07-30 | 2013-07-30 20:19 | Calculated | 6121 | 6121 - Circuit Breaker 6121 |  | 426SEG6121-5150 | Waihaha 426-01 | Rural D | Waihaha | Kuratau Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 221 | 24550 | 25857 | 1.0532 | 0.009002 | 1673.5 | 195799 | 2013/2014 | July-2013 | 7 | 2013
29215 | SWER Backfeed Refer 2013 / 263 | 2013-07-31 08:07 | 2013-07-31 | 2013-07-31 16:06 | Calculated | 5659 | 5659 - Fused Link 5659 |  | 421SEG5659-5656 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 341 | 264 | 24550 | 24784 | 1.0095 | 0.010754 | 1954 | 162337 | 2013/2014 | July-2013 | 7 | 2013
29216 | Dead bird at Transformer | 2013-07-31 15:16 | 2013-07-31 | 2013-07-31 15:30 | Calculated | TF4J11 | TF4J11 - Transformer Fuse: TF4J11 |  | 421SEG5342-5792 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 14 | 1 | 24550 | 14 | 0.00057 | 4.0733e-05 | 10 | 140 | 2013/2014 | July-2013 | 7 | 2013
29217 | Remove Genset | 2013-08-01 09:31 | 2013-08-01 | 2013-08-01 10:31 | Calculated | TF4237 | TF4237 - Transformer Fuse: TF4237 |  | 421SEG5874-6730 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 60 | 1 | 24551 | 60 | 0.00244 | 4.0732e-05 | 50 | 3000 | 2013/2014 | August-2013 | 8 | 2013
29218 | CB 802 Tripped | 2013-08-01 14:31 | 2013-08-01 | 2013-08-01 14:33 | Calculated | 802 | 802 - Circuit Breaker 802 |  | No Segment | 203-01 Te Waireka Road | Urban A | No Feeder |  |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 3026 | 24551 | 6052 | 0.24651 | 0.12325 | 26854 | 53708 | 2013/2014 | August-2013 | 8 | 2013
29219 | Commissioning Fault | 2013-08-01 15:15 | 2013-08-01 | 2013-08-01 15:17 | Calculated | 1784 | 1784 - Circuit Breaker 1784 |  | No Segment | No Asset Group | Remote Rural F | No Feeder |  |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 1346 | 24551 | 2692 | 0.10965 | 0.054825 | 14412.5 | 28824 | 2013/2014 | August-2013 | 8 | 2013
29221 | Refer 2013 / 266 Replace Poles & X/arms | 2013-08-02 09:04 | 2013-08-02 | 2013-08-02 15:05 | Calculated | 1312 | 1312 - Air Break Switch 1312 |  | 116SEG1312-1362 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 361 | 46 | 24551 | 16606 | 0.67639 | 0.0018737 | 448 | 161727 | 2013/2014 | August-2013 | 8 | 2013
29222 | Blown HV Fuse - Unknown Fault | 2013-08-02 16:19 | 2013-08-02 | 2013-08-02 17:20 | Calculated | TF3417 | TF3417 - Transformer Fuse: TF3417 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 2 | 24551 | 122 | 0.00497 | 8.1463e-05 | 50 | 3050 | 2013/2014 | August-2013 | 8 | 2013
29223 | Faulty Tx | 2013-08-04 12:41 | 2013-08-04 | 2013-08-04 14:54 | Calculated | TF1733 | TF1733 - Transformer Fuse: TF1733 |  | 116SEG1305 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 2 | 24551 | 266 | 0.01083 | 8.1463e-05 | 10 | 1330 | 2013/2014 | August-2013 | 8 | 2013
29224 | Upgrade Tx | 2013-08-05 09:35 | 2013-08-05 | 2013-08-05 11:15 | Calculated | TF1684 | TF1684 - Transformer Fuse: TF1684 |  | 110SEG2164 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 100 | 2 | 24551 | 200 | 0.00815 | 8.1463e-05 | 30 | 3000 | 2013/2014 | August-2013 | 8 | 2013
29225 | Refer 2013 / 270 Replace Pole 125/110 For New Extension | 2013-08-05 10:30 | 2013-08-05 | 2013-08-05 12:25 | Calculated | 371 | 371 - Air Break Switch 371 |  | 122SEG371-633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 115 | 45 | 24551 | 5175 | 0.21079 | 0.0018329 | 265 | 30474 | 2013/2014 | August-2013 | 8 | 2013
29226 | Burnt Fuse Holder | 2013-08-05 17:46 | 2013-08-05 | 2013-08-05 19:17 | Calculated | 402 | 402 - Fused Link 402 |  | 129SEG402-725 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 43 | 24551 | 3913 | 0.15938 | 0.0017515 | 615 | 55964 | 2013/2014 | August-2013 | 8 | 2013
29227 | Refer 2013 / 272 line Renewal Project | 2013-08-06 09:01 | 2013-08-06 | 2013-08-06 15:48 | Calculated | 1511 | 1511 - Air Break Switch 1511 |  | 113SEG1511-2207 | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 399 | 62 | 24551 | 24738 | 1.0076 | 0.0025254 | 458 | 182742 | 2013/2014 | August-2013 | 8 | 2013
29228 | Refer 2013 / 271 Replace Poles & X/arms | 2013-08-06 09:03 | 2013-08-06 | 2013-08-06 14:10 | Calculated | 1313 | 1313 - Fused Link 1313 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 307 | 27 | 24551 | 8289 | 0.33762 | 0.0010998 | 250 | 76749 | 2013/2014 | August-2013 | 8 | 2013
29229 | L/V Line Down | 2013-08-06 14:15 | 2013-08-06 | 2013-08-06 17:10 | Calculated | TF214 | TF214 - Transformer Fuse: TF214 |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 4 | 24551 | 700 | 0.02851 | 0.00016293 | 30 | 5250 | 2013/2014 | August-2013 | 8 | 2013
29230 | New L/V Stay Wire | 2013-08-07 10:00 | 2013-08-07 | 2013-08-07 10:55 | Calculated | TF235 | TF235 - Transformer Fuse: TF235 |  | 111SEG342-544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 55 | 4 | 24551 | 220 | 0.00896 | 0.00016293 | 55 | 3024 | 2013/2014 | August-2013 | 8 | 2013
29231 | Magpie | 2013-08-07 14:33 | 2013-08-07 | 2013-08-07 16:36 | Calculated | TF9L6 | TF9L6 - Transformer Fuse: TF9L6 |  | 408SEG5406 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 123 | 5 | 24551 | 615 | 0.02505 | 0.00020366 | 10 | 1230 | 2013/2014 | August-2013 | 8 | 2013
29232 | Faulty Transformer | 2013-08-08 08:23 | 2013-08-08 | 2013-08-08 13:26 | Calculated | TF801 | TF801 - Transformer Fuse: TF801 |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 303 | 3 | 24551 | 909 | 0.03702 | 0.00012219 | 25 | 7574 | 2013/2014 | August-2013 | 8 | 2013
29233 | Refer 2013 / 274 Repalce 4 Poles - Te Anga / Marakopa | 2013-08-08 08:42 | 2013-08-08 | 2013-08-08 17:04 | Calculated | TF640 | TF640 - Transformer Fuse T640 |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 455 | 174 | 24551 | 39906 | 1.6254 | 0.0070873 | 1230 | 377089 | 2013/2014 | August-2013 | 8 | 2013
29234 | Digger vs L/V | 2013-08-08 09:50 | 2013-08-08 | 2013-08-08 11:24 | Calculated | TF238 | TF238 - Transformer Fuse: TF238 |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 3 | 24551 | 282 | 0.01149 | 0.00012219 | 15 | 1410 | 2013/2014 | August-2013 | 8 | 2013
29235 | L/V fault | 2013-08-08 16:41 | 2013-08-08 | 2013-08-08 18:30 | Calculated | TF807 | TF807 - Transformer Fuse: TF807 |  | 119SEG420 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 4 | 24551 | 436 | 0.01776 | 0.00016293 | 50 | 5450 | 2013/2014 | August-2013 | 8 | 2013
29236 | Old Age | 2013-08-08 18:53 | 2013-08-08 | 2013-08-08 20:07 | Calculated | TF1541 | TF1541 - Transformer Fuse: TF1541 |  | 111SEG579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 1 | 24551 | 74 | 0.00301 | 4.0732e-05 | 25 | 1850 | 2013/2014 | August-2013 | 8 | 2013
29237 | Refer 2013 / 276 Replace Structure - Tx 1759 | 2013-08-09 09:34 | 2013-08-09 | 2013-08-09 14:03 | Calculated | 1317 | 1317 - Fused Link 1317 |  | 117SEG1317 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 7 | 24551 | 1883 | 0.0767 | 0.00028512 | 70 | 18829 | 2013/2014 | August-2013 | 8 | 2013
29238 | Refer 2013 / 275 Replace Link 1325 With Electronic Sectionaliser | 2013-08-09 10:18 | 2013-08-09 | 2013-08-09 12:00 | Calculated | 1335 | 1335 - Sectionaliser 1335 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 102 | 17 | 24551 | 1734 | 0.07063 | 0.00069244 | 148 | 15096 | 2013/2014 | August-2013 | 8 | 2013
29239 | Blown HV Fuse - Unknown Fault | 2013-08-09 12:37 | 2013-08-09 | 2013-08-09 13:44 | Calculated | TF10S17 | TF10S17 - Transformer Fuse: TF10S17 |  | 424SEG6559 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 13 | 24551 | 871 | 0.03548 | 0.00052951 | 50 | 3349 | 2013/2014 | August-2013 | 8 | 2013
29240 | Burnt Out Fuse Carrier | 2013-08-09 17:06 | 2013-08-09 | 2013-08-09 18:53 | Calculated | TF4152 | TF4152 - Transformer Fuse: TF4152 |  | 424SEG6559 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 16 | 24551 | 1712 | 0.06973 | 0.0006517 | 90 | 9629 | 2013/2014 | August-2013 | 8 | 2013
29241 | Unknown | 2013-08-10 07:39 | 2013-08-10 | 2013-08-10 08:56 | Calculated | 1724 | 1724 - Sectionaliser with Bypass & LInks 1724 |  | 115SEG1723-1724 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 77 | 14 | 24551 | 1078 | 0.04391 | 0.00057024 | 128 | 9856 | 2013/2014 | August-2013 | 8 | 2013
29242 | Refer 2013 / 279 Straighten Tunanui SWER Sub Structure | 2013-08-12 08:50 | 2013-08-12 | 2013-08-12 14:22 | Calculated | 5311 | 5311 - Air Break Switch 5311 |  | 409SEG5311-5452 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 174 | 473 | 24551 | 7626 | 0.31062 | 0.019266 | 3312 | 57802 | 2013/2014 | August-2013 | 8 | 2013
29243 | Scheduled Maintenance | 2013-08-12 09:41 | 2013-08-12 | 2013-08-12 11:51 | Calculated | TO2630 | TO2630 - TAP OFF FUSE - T2630 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 130 | 2 | 24551 | 260 | 0.01059 | 8.1463e-05 | 10 | 1300 | 2013/2014 | August-2013 | 8 | 2013
29244 | Old Age | 2013-08-13 12:51 | 2013-08-13 | 2013-08-13 13:54 | Calculated | TF7H4 | TF7H4 - Transformer Fuse: TF7H4 |  | 402SEG5781 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 4 | 24551 | 252 | 0.01026 | 0.00016293 | 15 | 945 | 2013/2014 | August-2013 | 8 | 2013
29246 | Refer 2013 / 280 Change L/A & Crimp Jumper | 2013-08-14 09:35 | 2013-08-14 | 2013-08-14 11:04 | Calculated | 2139 | 2139 - Fused Link 2139 |  | 113SEG1336-1337 | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 89 | 2 | 24551 | 178 | 0.00725 | 8.1463e-05 | 35 | 3115 | 2013/2014 | August-2013 | 8 | 2013
29247 | Lightning | 2013-08-14 15:31 | 2013-08-14 | 2013-08-14 16:24 | Calculated | TF8I71 | TF8I71 - Transformer Fuse: TF8I71 |  | 403SEG5795-5280 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 1 | 24551 | 53 | 0.00216 | 4.0732e-05 | 15 | 795 | 2013/2014 | August-2013 | 8 | 2013
29248 | Birds | 2013-08-15 06:50 | 2013-08-15 | 2013-08-15 07:57 | Calculated | 648 | 648 - fused link : 648 |  | 111SEG648 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 9 | 24551 | 603 | 0.02456 | 0.00036658 | 70 | 4689 | 2013/2014 | August-2013 | 8 | 2013
29249 | Refer 2013 / 281 Replace Poles & X/arms | 2013-08-15 09:04 | 2013-08-15 | 2013-08-15 14:57 | Calculated | 1313 | 1313 - Fused Link 1313 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 353 | 27 | 24551 | 9531 | 0.38821 | 0.0010998 | 250 | 88249 | 2013/2014 | August-2013 | 8 | 2013
29250 | Wind | 2013-08-15 14:46 | 2013-08-15 | 2013-08-15 15:23 | Calculated | TF711 | TF711 - Transformer Fuse: TF711 |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 3 | 24551 | 111 | 0.00452 | 0.00012219 | 25 | 924 | 2013/2014 | August-2013 | 8 | 2013
29251 | Unknown | 2013-08-16 01:05 | 2013-08-16 | 2013-08-16 02:00 | Calculated | 232 | 232 - Fused Link 232 |  | 101SEG519-232 | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 3 | 24551 | 165 | 0.00672 | 0.00012219 | 60 | 3300 | 2013/2014 | August-2013 | 8 | 2013
29252 | Refer 2013 / 282 Pole & X/arm Changes | 2013-08-16 09:07 | 2013-08-16 | 2013-08-16 16:00 | Calculated | 5932 | 5932 - Earth Working Link 5932 |  | 403SEG5932-5649 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 413 | 8 | 24551 | 3304 | 0.13458 | 0.00032585 | 55 | 22715 | 2013/2014 | August-2013 | 8 | 2013
29254 | Refer 2013 / 283 Replace X/arms & Tx 1866 (Rusty Lid) | 2013-08-16 09:30 | 2013-08-16 | 2013-08-16 12:50 | Calculated | 1519 | 1519 - Recloser 1519 |  | 113SEG1519-1541 | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 198 | 23 | 24551 | 2592 | 0.10558 | 0.00093683 | 148 | 16572 | 2013/2014 | August-2013 | 8 | 2013
29255 | Faulty Disc Insulator @ Pole | 2013-08-16 13:32 | 2013-08-16 | 2013-08-16 18:19 | Calculated | 5820 | 5820 - Circuit Breaker 5820 |  | 421SEG5820-5821 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 210 | 249 | 24551 | 51462 | 2.0961 | 0.010142 | 1869 | 384209 | 2013/2014 | August-2013 | 8 | 2013
29256 | Old Age | 2013-08-16 23:18 | 2013-08-16 | 2013-08-17 02:00 | Calculated | TF2310 | TF2310 - Transformer Fuse: TF2310 |  | 124SEG558 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 2 | 24551 | 324 | 0.0132 | 8.1463e-05 | 15 | 2430 | 2013/2014 | August-2013 | 8 | 2013
29257 | Old Age | 2013-08-17 07:23 | 2013-08-17 | 2013-08-17 09:02 | Calculated | TF20L35 | TF20L35 - Transformer Fuse: TF20L35 |  | 103SEG453- Temp Link between Pole 544 & Pole 538 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 54 | 24551 | 5346 | 0.21775 | 0.0021995 | 300 | 29699 | 2013/2014 | August-2013 | 8 | 2013
29258 | L/V Line Down | 2013-08-17 16:12 | 2013-08-17 | 2013-08-17 17:20 | Calculated | TF739 | TF739 - Transformer Fuse: TF739 |  | 120SEG481-422 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 5 | 24551 | 340 | 0.01385 | 0.00020366 | 25 | 1700 | 2013/2014 | August-2013 | 8 | 2013
29259 | Possum at pole 1161080 | 2013-08-20 02:36 | 2013-08-20 | 2013-08-20 03:54 | Calculated | 683 | 683 - Circuit Breaker 683 |  | No Segment | 207-01 Wairere Falls | Rural D | No Feeder |  |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 459 | 24551 | 35802 | 1.4583 | 0.018696 | 3056 | 238367 | 2013/2014 | August-2013 | 8 | 2013
29260 | Blown HV Fuse - Unknown Fault | 2013-08-20 05:37 | 2013-08-20 | 2013-08-20 06:30 | Calculated | TF176 | TF176 - Transformer Fuse: TF176 |  | 102SEG1271-336 | Hangatiki East 102-01 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 3 | 24551 | 159 | 0.00648 | 0.00012219 | 50 | 2649 | 2013/2014 | August-2013 | 8 | 2013
29261 | Refer 2013 / 285 Replace Poles & X/arms | 2013-08-20 09:02 | 2013-08-20 | 2013-08-20 15:54 | Calculated | 341 | 341 - Fused Link 341 |  | 109SEG341-587 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 412 | 39 | 24551 | 16068 | 0.65447 | 0.0015885 | 355 | 146259 | 2013/2014 | August-2013 | 8 | 2013
29262 | Blown HV Tap off Fuse - Unknown Fault | 2013-08-20 15:40 | 2013-08-20 | 2013-08-20 19:30 | Calculated | TO08G10 | TO08G10 - TAP OFF Fuse: TF8G10 |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 230 | 2 | 24551 | 460 | 0.01874 | 8.1463e-05 | 25 | 5750 | 2013/2014 | August-2013 | 8 | 2013
29263 | L/V Maintenance | 2013-08-21 09:30 | 2013-08-21 | 2013-08-21 13:29 | Calculated | TF1873 | TF1873 - Transformer Fuse: TF1873 |  | 113SEG1520 | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 239 | 8 | 24551 | 1912 | 0.07788 | 0.00032585 | 50 | 11950 | 2013/2014 | August-2013 | 8 | 2013
29264 | Connect New Earth Bank | 2013-08-21 09:32 | 2013-08-21 | 2013-08-21 13:41 | Calculated | TF1666 | TF1666 - Transformer Fuse: TF1666 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 249 | 3 | 24551 | 747 | 0.03043 | 0.00012219 | 25 | 6224 | 2013/2014 | August-2013 | 8 | 2013
29265 | L/V Maintenance | 2013-08-21 09:41 | 2013-08-21 | 2013-08-21 14:42 | Calculated | TF2155 | TF2155 - Transformer Fuse: TF2155 |  | 128SEG2083 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 301 | 61 | 24551 | 18361 | 0.74787 | 0.0024846 | 200 | 60199 | 2013/2014 | August-2013 | 8 | 2013
29266 | Magpie at Pole 16 | 2013-08-21 13:29 | 2013-08-21 | 2013-08-22 08:33 | Calculated | 10C03 | 10C03 - 1 Phase : 15.00 kVA : POLEMNT |  | 413SEG5456-5461 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 815 | 23 | 24551 | 15675 | 0.63847 | 0.00093683 | 158 | 108508 | 2013/2014 | August-2013 | 8 | 2013
29267 | Damaged SWER Earth | 2013-08-22 12:22 | 2013-08-22 | 2013-08-22 13:55 | Calculated | TF6P3 | TF6P3 - Transformer Fuse: TF6P3 |  | 426SEG5239 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDI | Conductor Failure - Insulated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 93 | 1 | 24551 | 93 | 0.00379 | 4.0732e-05 | 15 | 1395 | 2013/2014 | August-2013 | 8 | 2013
29268 | Old Age | 2013-08-26 18:23 | 2013-08-26 | 2013-08-26 20:07 | Calculated | TF620 | TF620 - Transformer Fuse: TF620 |  | 103SEG1230 | Benneydale 103-07 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 25 | 24551 | 2600 | 0.1059 | 0.0010183 | 100 | 10400 | 2013/2014 | August-2013 | 8 | 2013
29269 | Private Line tree work | 2013-08-27 08:24 | 2013-08-27 | 2013-08-27 14:06 | Calculated | 558 | 558 - Fused Link 558 |  | 124SEG558 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 4 | 24551 | 1368 | 0.05572 | 0.00016293 | 45 | 15390 | 2013/2014 | August-2013 | 8 | 2013
29270 | Install L/A | 2013-08-27 09:00 | 2013-08-27 | 2013-08-27 10:25 | Calculated | TF2289 | TF2289 - Transformer Fuse: TF2289 |  | 116SEG1375 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 85 | 1 | 24551 | 85 | 0.00346 | 4.0732e-05 | 15 | 1275 | 2013/2014 | August-2013 | 8 | 2013
29271 | Refer 2013 / 291 Northern Feeder Renewal Project | 2013-08-27 09:11 | 2013-08-27 | 2013-08-27 15:10 | Calculated | 5777 | 5777 - Fused Link 5777 |  | 402SEG5797-5777 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 359 | 12 | 24551 | 4308 | 0.17547 | 0.00048878 | 85 | 30515 | 2013/2014 | August-2013 | 8 | 2013
29272 | Low L/V Lines | 2013-08-27 09:25 | 2013-08-27 | 2013-08-27 10:50 | Calculated | TF1480 | TF1480 - Transformer Fuse: TF1480 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DICL | Conductor Low - Incorrect Clearances | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 3 | 24551 | 255 | 0.01039 | 0.00012219 | 30 | 2550 | 2013/2014 | August-2013 | 8 | 2013
29273 | Change Transformer | 2013-08-27 13:02 | 2013-08-27 | 2013-08-27 14:37 | Calculated | TF850 | TF850 - Transformer Fuse: TF850 |  | 116SEG717 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 2 | 24551 | 190 | 0.00774 | 8.1463e-05 | 15 | 1425 | 2013/2014 | August-2013 | 8 | 2013
29274 | Refer 2013 / 292 Install New L/A & Insulators On Tx 5I10 | 2013-08-28 09:01 | 2013-08-28 | 2013-08-28 11:30 | Calculated | 5553 | 5553 - Fused Link 5553 |  | 402SEG5553 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 149 | 2 | 24551 | 298 | 0.01214 | 8.1463e-05 | 15 | 2235 | 2013/2014 | August-2013 | 8 | 2013
29275 | Shut - Replace Transformer Structure | 2013-08-28 09:56 | 2013-08-28 | 2013-08-28 14:37 | Calculated | TF520 | TF520 - Transformer Fuse: TF520 |  | 125SEG296-583 | Coast 125-04 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 281 | 2 | 24551 | 562 | 0.02289 | 8.1463e-05 | 25 | 7025 | 2013/2014 | August-2013 | 8 | 2013
29276 | Private Line Tree Cutting | 2013-08-28 10:02 | 2013-08-28 | 2013-08-28 10:47 | Calculated | 563 | 563 - Air Break Switch 563 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 25 | 24551 | 1125 | 0.04582 | 0.0010183 | 230 | 10350 | 2013/2014 | August-2013 | 8 | 2013
29277 | Solid Link Fallen Out | 2013-08-28 21:30 | 2013-08-28 | 2013-08-28 23:23 | Calculated | 5294 | 5294 - Fused Link 5294 |  | 413SEG5294-5298 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 106 | 24551 | 11978 | 0.48788 | 0.0043175 | 775.5 | 87631 | 2013/2014 | August-2013 | 8 | 2013
29278 | Upgrade Earthing | 2013-08-29 09:16 | 2013-08-29 | 2013-08-29 12:01 | Calculated | TF4I5 | TF4I5 - Transformer Fuse: TF4I5 |  | 402SEG5171 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 165 | 2 | 24551 | 330 | 0.01344 | 8.1463e-05 | 10 | 1650 | 2013/2014 | August-2013 | 8 | 2013
29279 | Replace Structure | 2013-08-29 09:35 | 2013-08-29 | 2013-08-29 13:02 | Calculated | TF1461 | TF1461 - Transformer Fuse: TF1461 |  | 107SEG508-1798 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 207 | 2 | 24551 | 414 | 0.01686 | 8.1463e-05 | 10 | 2070 | 2013/2014 | August-2013 | 8 | 2013
29280 | Private Line Tree Cutting | 2013-08-29 10:38 | 2013-08-29 | 2013-08-29 12:37 | Calculated | TF17H04 | TF17H04 - Transformer Fuse: TF17H04 |  | 410SEG5510-5511 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 119 | 6 | 24551 | 714 | 0.02908 | 0.00024439 | 10 | 1189 | 2013/2014 | August-2013 | 8 | 2013
29281 | Wind | 2013-08-30 02:49 | 2013-08-30 | 2013-08-30 04:40 | Calculated | TF3335 | TF3335 - Transformer Fuse TF3335 |  | 111SEG551 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 9 | 24551 | 909 | 0.03702 | 0.00036658 | 75 | 7575 | 2013/2014 | August-2013 | 8 | 2013
29282 | Refer 2013 / 295 Change poles & X/arms | 2013-08-30 09:02 | 2013-08-30 | 2013-08-30 14:15 | Calculated | 587 | 587 - Fused Link 587 |  | 109SEG587-2218 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 313 | 13 | 24551 | 4069 | 0.16574 | 0.00052951 | 100 | 31299 | 2013/2014 | August-2013 | 8 | 2013
29283 | Refer 2013 / 296 Re-Bind Conductor @ Tx 13F3 | 2013-08-30 10:18 | 2013-08-30 | 2013-08-30 12:16 | Calculated | 5668 | 5668 - Fused Link 5668 |  | 410SEG5668 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 118 | 13 | 24551 | 1534 | 0.06248 | 0.00052951 | 60 | 7080 | 2013/2014 | August-2013 | 8 | 2013
29284 | Cable Fault | 2013-08-31 16:39 | 2013-08-31 | 2013-09-03 17:48 | Calculated | 5773 | 5773 - Recloser 5773 |  | 419SEG5773-5998 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 1525 | 42 | 24551 | 29113 | 1.1858 | 0.0017107 | 2140 | 1230204 | 2013/2014 | August-2013 | 8 | 2013
29286 | Broken Fuse Holder | 2013-09-01 07:59 | 2013-09-01 | 2013-09-01 13:39 | Calculated | TF5I5 | TF5I5 - Transformer Fuse: TF5I5 |  | 402SEG5782 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 340 | 4 | 24514 | 1360 | 0.05548 | 0.00016317 | 25 | 8500 | 2013/2014 | September-2013 | 9 | 2013
29288 | Unknown Earth Fault | 2013-09-01 21:42 | 2013-09-01 | 2013-09-01 21:46 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 443 | 24514 | 1653 | 0.06743 | 0.018071 | 5774 | 19807 | 2013/2014 | September-2013 | 9 | 2013
29290 | Refer 2013 / 297 Install New L/A's @Tx 2602 Below DDO's | 2013-09-02 09:19 | 2013-09-02 | 2013-09-02 12:11 | Calculated | 717 | 717 - Fused Link 717 |  | 116SEG717 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 172 | 5 | 24514 | 860 | 0.03508 | 0.00020397 | 35 | 6020 | 2013/2014 | September-2013 | 9 | 2013
29291 | Faulty Tx 17N5 | 2013-09-02 10:58 | 2013-09-02 | 2013-09-03 10:11 | Calculated | 6148 | 6148 - Load Break Switch 6148 |  | 415SEG6598RET | Turoa 415-03 | Rural B | Turoa | Direct from Ohakune Supply |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24514 |  | 0 | 0 |  |  | 2013/2014 | September-2013 | 9 | 2013
29292 | Unknown | 2013-09-02 18:55 | 2013-09-02 | 2013-09-02 20:21 | Calculated | 5986 | 5986 - Fused Link 5986 |  | 402SEG5986 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 29 | 24514 | 2494 | 0.10174 | 0.001183 | 250 | 21499 | 2013/2014 | September-2013 | 9 | 2013
29293 | Refer 2013 / 298 Deviate 11kV Line Away from Slip | 2013-09-03 09:16 | 2013-09-03 | 2013-09-03 16:38 | Calculated | 116 | 116 - Recloser with Bypass 116 |  | 109SEG541-116 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 380 | 45 | 24514 | 4113 | 0.16778 | 0.0018357 | 430.5 | 31375 | 2013/2014 | September-2013 | 9 | 2013
29297 | Refer 2013 / 302 Installing New Pole & ABS (New Site For ABS 394) | 2013-09-04 09:10 | 2013-09-04 | 2013-09-04 11:08 | Calculated | 618 | 618 - Air Break Switch 618 |  | 122SEG618-367 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 46 | 24514 | 2668 | 0.10884 | 0.0018765 | 265 | 15369 | 2013/2014 | September-2013 | 9 | 2013
29298 | Refer 2013 / 304 Replace 11kV Pole | 2013-09-04 09:34 | 2013-09-04 | 2013-09-04 11:45 | Calculated | 426 | 426 - Recloser 426 |  | 129SEG434-426 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 64 | 72 | 24514 | 4608 | 0.18797 | 0.0029371 | 795 | 50880 | 2013/2014 | September-2013 | 9 | 2013
29299 | Incorrect Tx Size Installed | 2013-09-04 13:39 | 2013-09-04 | 2013-09-04 15:12 | Calculated | TF2690 | TF2690 - Transformer Fuse: TF2690 |  | 113SEG1508 | Mahoenui 113-07 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLI | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 2 | 24514 | 186 | 0.00759 | 8.1586e-05 | 5 | 465 | 2013/2014 | September-2013 | 9 | 2013
29301 | Tree On Line | 2013-09-05 08:52 | 2013-09-05 | 2013-09-05 12:35 | Calculated | 5582 | 5582 - Fused Link 5582 |  | 410SEG5582 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 222 | 24 | 24514 | 3378 | 0.1378 | 0.00097903 | 155 | 20760 | 2013/2014 | September-2013 | 9 | 2013
29302 | Faulty Disc Insulator @ Pole | 2013-09-05 08:53 | 2013-09-05 | 2013-09-05 19:20 | Calculated | 5396 | 5396 - Sectionaliser 5396 |  | 410SEG5597-5396 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 368 | 71 | 24514 | 21402 | 0.87305 | 0.0028963 | 438 | 134212 | 2013/2014 | September-2013 | 9 | 2013
29300 | Refer 2013 / 306 Replace Poles & X/arms | 2013-09-05 09:01 | 2013-09-05 | 2013-09-05 14:37 | Calculated | 341 | 341 - Fused Link 341 |  | 109SEG341-587 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 336 | 39 | 24514 | 13104 | 0.53455 | 0.0015909 | 355 | 119279 | 2013/2014 | September-2013 | 9 | 2013
29303 | X/arm Now Vertical | 2013-09-05 13:22 | 2013-09-05 | 2013-09-05 15:41 | Calculated | 209 | 209 - Fused Link 209 |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAB | Cross-Arm Bent | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 56 | 24514 | 7784 | 0.31753 | 0.0022844 | 565 | 78534 | 2013/2014 | September-2013 | 9 | 2013
29304 | Fautly DDO | 2013-09-06 08:16 | 2013-09-06 | 2013-09-06 11:29 | Calculated | TF1910 | TF1910 - Transformer Fuse: TF1910 |  | 116SEG1355-1327 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 3 | 24514 | 579 | 0.02362 | 0.00012238 | 30 | 5790 | 2013/2014 | September-2013 | 9 | 2013
29305 | Refer 2013 / 309 Replace Poles & X/arms | 2013-09-06 09:02 | 2013-09-06 | 2013-09-06 13:30 | Calculated | 234 | 234 - Fused Link 234 |  | 107SEG234 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 268 | 17 | 24514 | 4556 | 0.18585 | 0.00069348 | 107.5 | 28809 | 2013/2014 | September-2013 | 9 | 2013
29306 | Refer 2013 / 307 Replace Poles & X/arms | 2013-09-06 09:03 | 2013-09-06 | 2013-09-06 15:40 | Calculated | 5782 | 5782 - Fused Link 5782 |  | 402SEG5782 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 397 | 6 | 24514 | 2382 | 0.09717 | 0.00024476 | 55 | 21835 | 2013/2014 | September-2013 | 9 | 2013
29307 | Private Line Maintenace | 2013-09-06 10:04 | 2013-09-06 | 2013-09-06 11:19 | Calculated | TF14L05 | TF14L05 - Transformer Fuse: TF14L05 |  | 411SEG5144-5769 | National Park 411-01 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 75 | 5 | 24514 | 375 | 0.0153 | 0.00020397 | 500 | 37500 | 2013/2014 | September-2013 | 9 | 2013
29308 | Fuse failure due to old age | 2013-09-06 12:11 | 2013-09-06 | 2013-09-06 14:34 | Calculated | TF12H13 | TF12H13 - Transformer Fuse: TF12H13 |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 143 | 2 | 24514 | 286 | 0.01167 | 8.1586e-05 | 10 | 1430 | 2013/2014 | September-2013 | 9 | 2013
29310 | Refer 2013 / 310 Western Feeder Upgrade - Pole Replacements | 2013-09-09 09:08 | 2013-09-09 | 2013-09-09 15:10 | Calculated | 6033 | 6033 - Fused Link 6033 |  | 403SEG6033-5316 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 362 | 27 | 24514 | 9774 | 0.39871 | 0.0011014 | 180 | 65159 | 2013/2014 | September-2013 | 9 | 2013
29309 | Maintenance | 2013-09-09 09:09 | 2013-09-09 | 2013-09-09 10:10 | Calculated | TO1867 | TO1867 - TAP OFF FUSES: T1867 |  | 113SEG2207-1336 | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 61 | 4 | 24514 | 244 | 0.00995 | 0.00016317 | 15 | 915 | 2013/2014 | September-2013 | 9 | 2013
29311 | Maintenance | 2013-09-09 12:02 | 2013-09-09 | 2013-09-09 13:20 | Calculated | TF1869 | TF1869 - Transformer Fuse: TF1869 |  | 113SEG2207-1336 | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 78 | 3 | 24514 | 234 | 0.00955 | 0.00012238 | 30 | 2340 | 2013/2014 | September-2013 | 9 | 2013
29312 | Old Age | 2013-09-09 17:50 | 2013-09-09 | 2013-09-09 18:39 | Calculated | TF8I18 | TF8I18 - Transformer Fuse: TF8I18 |  | 403SEG5522 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 1 | 24514 | 49 | 0.002 | 4.0793e-05 | 15 | 735 | 2013/2014 | September-2013 | 9 | 2013
29313 | Refer 2013 / 311 Replace Complete Strucutre & L/V X/arms at Tx4I5 | 2013-09-10 09:03 | 2013-09-10 | 2013-09-10 15:35 | Calculated | 5171 | 5171 - Fused Link 5171 |  | 402SEG5171 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 392 | 4 | 24514 | 1568 | 0.06396 | 0.00016317 | 35 | 13720 | 2013/2014 | September-2013 | 9 | 2013
29314 | Refer 2013 / 312 Run 3rd Phase & Upgrade Tx 1596 | 2013-09-10 09:36 | 2013-09-10 | 2013-09-10 13:29 | Calculated | 1261 | 1261 - Air Break Switch 1261 |  | 128SEG1261 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 233 | 8 | 24514 | 1864 | 0.07604 | 0.00032634 | 85 | 19805 | 2013/2014 | September-2013 | 9 | 2013
29315 | Upgrade Of SCADA Software | 2013-09-10 11:07 | 2013-09-10 | 2013-09-10 13:45 | Calculated | TPHangatiki CB272 | TPHangatiki CB272 - 33kV Minimum Oil Circuit Breaker TP272 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 86 | 13006 | 24514 | 268189 | 10.9402 | 0.53055 | 112791.5 | 2274466 | 2013/2014 | September-2013 | 9 | 2013
29316 | Old Age | 2013-09-11 10:09 | 2013-09-11 | 2013-09-11 11:15 | Calculated | TF352 | TF352 - Transformer Fuse: TF352 |  | 112SEG353-391 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 19 | 24514 | 1254 | 0.05115 | 0.00077507 | 200 | 13199 | 2013/2014 | September-2013 | 9 | 2013
29317 | Tree Through Line | 2013-09-11 10:35 | 2013-09-11 | 2013-09-11 14:10 | Calculated | 5623 | 5623 - Electronic Sectionaliser 5623 |  | 409SEG5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 215 | 15 | 24514 | 3225 | 0.13156 | 0.0006119 | 72.5 | 15587 | 2013/2014 | September-2013 | 9 | 2013
29318 | Extreme Weather - line down | 2013-09-11 20:12 | 2013-09-11 | 2013-09-12 13:03 | Calculated | T2218 | T2218 - 1 Phase : 15.00 kVA : POLEMNT |  | 128SEG1628 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1011 | 44 | 24514 | 33407 | 1.3628 | 0.0017949 | 305.5 | 225782 | 2013/2014 | September-2013 | 9 | 2013
29319 | Wind | 2013-09-12 06:29 | 2013-09-12 | 2013-09-12 09:37 | Calculated | 5340 | 5340 - Solid Link 5340 |  | 417SEG5340 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 188 | 1 | 24514 | 188 | 0.00767 | 4.0793e-05 | 15 | 2820 | 2013/2014 | September-2013 | 9 | 2013
29323 | Change Transformer | 2013-09-12 09:33 | 2013-09-12 | 2013-09-12 10:14 | Calculated | TF2518 | TF2518 - Transformer Fuse: TF2518 |  | 113SEG1511-2207 | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 41 | 1 | 24514 | 41 | 0.00167 | 4.0793e-05 | 5 | 205 | 2013/2014 | September-2013 | 9 | 2013
29324 | Bird | 2013-09-13 09:14 | 2013-09-13 | 2013-09-13 12:05 | Calculated | TF9K5 | TF9K5 - Transformer Fuse: TF9K5 |  | 409SEG5134 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 2 | 24514 | 342 | 0.01395 | 8.1586e-05 | 15 | 2565 | 2013/2014 | September-2013 | 9 | 2013
29326 | Overloaded | 2013-09-13 16:43 | 2013-09-13 | 2013-09-13 17:41 | Calculated | TF517 | TF517 - Transformer Fuse: TF517 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 1 | 24514 | 58 | 0.00237 | 4.0793e-05 | 13 | 754 | 2013/2014 | September-2013 | 9 | 2013
29327 | Bird / Reconfigure Jumper | 2013-09-15 13:34 | 2013-09-15 | 2013-09-15 16:49 | Calculated | TO08G10 | TO08G10 - TAP OFF Fuse: TF8G10 |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 195 | 2 | 24514 | 390 | 0.01591 | 8.1586e-05 | 25 | 4875 | 2013/2014 | September-2013 | 9 | 2013
29328 | Unknown | 2013-09-16 05:23 | 2013-09-16 | 2013-09-16 05:28 | Calculated | 440 | 440 - Recloser with Outgoing Link 440 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 48 | 24514 | 240 | 0.00979 | 0.0019581 | 355.5 | 1777 | 2013/2014 | September-2013 | 9 | 2013
29329 | Faulty Link 6003 | 2013-09-16 06:10 | 2013-09-16 | 2013-09-16 12:04 | Calculated | 5010 | 5010 - Air Break Switch 5010 |  | 424SEG5010-T4172 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 354 | 189 | 24514 | 52357 | 2.1358 | 0.0077099 | 950 | 247744 | 2013/2014 | September-2013 | 9 | 2013
29330 | Blown HV Fuse - Unknown Fault | 2013-09-16 06:55 | 2013-09-16 | 2013-09-16 12:20 | Calculated | TF7J8 | TF7J8 - Transformer Fuse: TF7J8 |  | 402SEG5930-5756 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 250 | 77 | 24514 | 11108 | 0.45313 | 0.0031411 | 575 | 84645 | 2013/2014 | September-2013 | 9 | 2013
29331 | Upgrade Earth Mat | 2013-09-16 09:44 | 2013-09-16 | 2013-09-16 10:52 | Calculated | TF6H12 | TF6H12 - Transformer Fuse: TF6H12 |  | 402SEG5472-5343 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 68 | 6 | 24514 | 408 | 0.01664 | 0.00024476 | 30 | 2040 | 2013/2014 | September-2013 | 9 | 2013
29332 | Refer 2013 / 319 Trim Trees Around Tx 1615 | 2013-09-16 10:30 | 2013-09-16 | 2013-09-16 14:27 | Calculated | 335 | 335 - Air Break Switch 335 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 237 | 32 | 24514 | 7584 | 0.30937 | 0.0013054 | 325 | 77024 | 2013/2014 | September-2013 | 9 | 2013
29333 | Upgrade Earth Mat | 2013-09-16 12:23 | 2013-09-16 | 2013-09-16 15:57 | Calculated | TF5I04 | TF5I04 - Transformer Fuse: TF5I04 |  | 402SEG5446-5797 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 214 | 1 | 24514 | 214 | 0.00873 | 4.0793e-05 | 15 | 3210 | 2013/2014 | September-2013 | 9 | 2013
29334 | Unknown | 2013-09-16 12:44 | 2013-09-16 | 2013-09-16 13:12 | Calculated | 5536 | 5536 - Sectionaliser 5536 |  | 124SEG5536 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 11 | 24514 | 308 | 0.01256 | 0.00044872 | 77.5 | 2170 | 2013/2014 | September-2013 | 9 | 2013
29335 | Old Age | 2013-09-16 14:01 | 2013-09-16 | 2013-09-16 15:33 | Calculated | TF9R29 | TF9R29 - Transformer Fuse: TF9R29 |  | 406SEG5896 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 6 | 24514 | 552 | 0.02252 | 0.00024476 | 50 | 4599 | 2013/2014 | September-2013 | 9 | 2013
29337 | SWER Backfeed Refer 2013 / 314 Western Feeder Upgrade - Pole Replacements | 2013-09-17 08:52 | 2013-09-17 | 2013-09-17 16:15 | Calculated | 5932 | 5932 - Earth Working Link 5932 |  | 403SEG5932-5649 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 391 | 18 | 24514 | 3906 | 0.15934 | 0.00073427 | 110 | 21504 | 2013/2014 | September-2013 | 9 | 2013
29338 | Refer 2013 / 320 Fit T/O Fuses For Tx2260 & 1369 | 2013-09-17 10:02 | 2013-09-17 | 2013-09-17 12:32 | Calculated | 575 | 575 - Fused Link 575 |  | 107SEG575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 150 | 13 | 24514 | 1950 | 0.07955 | 0.00053031 | 150 | 22499 | 2013/2014 | September-2013 | 9 | 2013
29339 | Cable Fault | 2013-09-17 10:11 | 2013-09-17 | 2013-09-17 22:18 | Calculated | TF16N06 | TF16N06 - Transformer Fuse: TF16N06 |  | 419SEG5866-6338 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 727 | 39 | 24514 | 11887 | 0.48491 | 0.0015909 | 1640 | 486969 | 2013/2014 | September-2013 | 9 | 2013
29341 | Refer 2013 / 315 Upgrade Earth Mat @ Tx 4l10 & replace Various Insulators | 2013-09-18 09:08 | 2013-09-18 | 2013-09-18 15:19 | Calculated | 5345 | 5345 - Fused Link 5345 |  | 402SEG5345 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 370 | 6 | 24514 | 2224 | 0.09072 | 0.00024476 | 30 | 11121 | 2013/2014 | September-2013 | 9 | 2013
29344 | Refer 2013 / 316 Northern Feeder Renewals - Poles & X/arms etc | 2013-09-19 09:02 | 2013-09-19 | 2013-09-19 13:35 | Calculated | 5798 | 5798 - Fused Link 5798 |  | 402SEG5798 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 273 | 11 | 24514 | 3003 | 0.1225 | 0.00044872 | 55 | 15015 | 2013/2014 | September-2013 | 9 | 2013
29345 | Maintenance | 2013-09-19 12:07 | 2013-09-19 | 2013-09-19 12:52 | Calculated | TF3120 | TF3120 - Transformer Fuse: TF3120 |  | 109SEG589-559 | Gravel Scoop 109-01 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24514 |  | 0 | 0 |  |  | 2013/2014 | September-2013 | 9 | 2013
29346 | Connect Cable & Disconnect Gen Set | 2013-09-19 13:07 | 2013-09-19 | 2013-09-19 14:01 | Calculated | 5773 | 5773 - Recloser 5773 |  | 419SEG5773-5998 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 54 | 19 | 24514 | 1026 | 0.04185 | 0.00077507 | 775 | 41849 | 2013/2014 | September-2013 | 9 | 2013
29347 | Old Age | 2013-09-20 02:37 | 2013-09-20 | 2013-09-20 04:37 | Calculated | TF11P01 | TF11P01 - Transformer Fuse: TF11P01 |  | 609SEG1347(ECNZ) | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 120 | 1 | 24514 | 120 | 0.0049 | 4.0793e-05 | 250 | 30000 | 2013/2014 | September-2013 | 9 | 2013
29349 | Dead Duck Found | 2013-09-20 08:11 | 2013-09-20 | 2013-09-20 10:53 | Calculated | TF7Q4 | TF7Q4 - Transformer Fuse: TF7Q4 |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 1 | 24514 | 162 | 0.00661 | 4.0793e-05 | 10 | 1620 | 2013/2014 | September-2013 | 9 | 2013
29348 | Refer 2013 / 317 Northern Feeder Renewals - Replace Poles | 2013-09-20 08:24 | 2013-09-20 | 2013-09-20 16:39 | Calculated | 5776 | 5776 - Fused Link 5776 |  | 402SEG5776 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 431 | 12 | 24514 | 5172 | 0.21098 | 0.00048952 | 29497.7857 | 36635 | 2013/2014 | September-2013 | 9 | 2013
29350 | Faulty Cable To Tx 10R13 | 2013-09-20 15:56 | 2013-09-20 | 2013-09-20 19:15 | Calculated | TF10R13 | TF10R13 - Transformer Fuse: TF10R13 |  | 405SEG5519-5488 | Hirangi 405-01 | Rural B | Hirangi | Awamate Zone Substation (Containerised) |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV SWER | 9000 |  | 99 | 22 | 24514 | 2009 | 0.08195 | 0.00089745 | 87.5 | 8024 | 2013/2014 | September-2013 | 9 | 2013
29351 | Stock Rubbing - L/V Clash | 2013-09-20 18:56 | 2013-09-20 | 2013-09-20 20:28 | Calculated | TF241 | TF241 - Transformer Fuse: TF241 |  | 111SEG339-346 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AFAR | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 5 | 24514 | 460 | 0.01876 | 0.00020397 | 25 | 2300 | 2013/2014 | September-2013 | 9 | 2013
29352 | Wind | 2013-09-21 12:19 | 2013-09-21 | 2013-09-21 13:10 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 26 | 24514 | 1326 | 0.05409 | 0.0010606 | 330 | 16830 | 2013/2014 | September-2013 | 9 | 2013
29353 | Lightning | 2013-09-21 15:23 | 2013-09-21 | 2013-09-21 17:08 | Calculated | TF419 | TF419 - Transformer Fuse: TF419 |  | 122SEG768 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 2 | 24514 | 210 | 0.00857 | 8.1586e-05 | 25 | 2625 | 2013/2014 | September-2013 | 9 | 2013
29354 | Lightning | 2013-09-21 15:34 | 2013-09-21 | 2013-09-21 17:25 | Calculated | TF568 | TF568 - Transformer Fuse: TF568 |  | 122SEG619-REG35 | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 2 | 24514 | 222 | 0.00906 | 8.1586e-05 | 10 | 1110 | 2013/2014 | September-2013 | 9 | 2013
29355 | Lightning | 2013-09-21 15:42 | 2013-09-21 | 2013-09-21 17:49 | Calculated | TF297 | TF297 - Transformer Fuse: TF297 |  | 122SEG366-398 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 3 | 24514 | 381 | 0.01554 | 0.00012238 | 15 | 1905 | 2013/2014 | September-2013 | 9 | 2013
29356 | Lightning | 2013-09-21 17:04 | 2013-09-21 | 2013-09-21 17:42 | Calculated | TF2586 | TF2586 - Transformer Fuse: TF2586 |  | 123SEG528 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 1 | 24514 | 38 | 0.00155 | 4.0793e-05 | 10 | 380 | 2013/2014 | September-2013 | 9 | 2013
29357 | Lightning | 2013-09-21 19:10 | 2013-09-21 | 2013-09-21 20:06 | Calculated | TF742 | TF742 - Transformer Fuse: TF742 |  | 129SEG434-426 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 2 | 24514 | 112 | 0.00457 | 8.1586e-05 | 15 | 840 | 2013/2014 | September-2013 | 9 | 2013
29359 | Lightning | 2013-09-21 21:11 | 2013-09-21 | 2013-09-21 23:52 | Calculated | TF2632 | TF2632 - Transformer Fuse: TF2632 |  | 103SEG225-560 | Benneydale 103-02 | Urban A | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 2 | 24514 | 322 | 0.01314 | 8.1586e-05 | 100 | 16100 | 2013/2014 | September-2013 | 9 | 2013
29358 | Lightning-Suspect Faulty Tx | 2013-09-21 21:27 | 2013-09-21 | 2013-09-22 11:12 | Calculated | TF610 | TF610 - Transformer Fuse: TF610 |  | 122SEG366-398 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 825 | 2 | 24514 | 1650 | 0.06731 | 8.1586e-05 | 10 | 8250 | 2013/2014 | September-2013 | 9 | 2013
29360 | Lightning | 2013-09-21 22:16 | 2013-09-21 | 2013-09-22 00:26 | Calculated | TF1481 | TF1481 - Transformer Fuse: TF1481 |  | 103SEG560-107 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 3 | 24514 | 390 | 0.01591 | 0.00012238 | 25 | 3249 | 2013/2014 | September-2013 | 9 | 2013
29361 | Wind | 2013-09-22 05:29 | 2013-09-22 | 2013-09-22 06:52 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 26 | 24514 | 2158 | 0.08803 | 0.0010606 | 330 | 27390 | 2013/2014 | September-2013 | 9 | 2013
29362 | Lightning | 2013-09-22 07:10 | 2013-09-22 | 2013-09-22 11:20 | Calculated | TF24 | TF24 - Transformer Fuse: TF24 |  | 103SEG731-REG14 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 250 | 2 | 24514 | 500 | 0.0204 | 8.1586e-05 | 15 | 3750 | 2013/2014 | September-2013 | 9 | 2013
29363 | Lightning | 2013-09-22 07:10 | 2013-09-22 | 2013-09-22 11:20 | Calculated | TF27 | TF27 - Transformer Fuse: TF27 |  | 103SEG REG14-669 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 250 | 2 | 24514 | 500 | 0.0204 | 8.1586e-05 | 30 | 7500 | 2013/2014 | September-2013 | 9 | 2013
29364 | Lightning | 2013-09-22 07:10 | 2013-09-22 | 2013-09-22 11:20 | Calculated | TF679 | TF679 - Transformer Fuse: TF679 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 250 | 1 | 24514 | 250 | 0.0102 | 4.0793e-05 | 10 | 2500 | 2013/2014 | September-2013 | 9 | 2013
29365 | Wind | 2013-09-22 07:32 | 2013-09-22 | 2013-09-22 07:46 | Calculated | 5409 | 5409 - Recloser with Bypass 5409 |  | 426SEG5409-5333 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 37 | 24514 | 518 | 0.02113 | 0.0015093 | 272.5 | 3814 | 2013/2014 | September-2013 | 9 | 2013
29366 | Lightning | 2013-09-22 08:37 | 2013-09-22 | 2013-09-22 10:19 | Calculated | TF6Q8 | TF6Q8 - Transformer Fuse: TF6Q8 |  | 426SEG5588-5583 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 2 | 24514 | 204 | 0.00832 | 8.1586e-05 | 10 | 1020 | 2013/2014 | September-2013 | 9 | 2013
29367 | Lightning | 2013-09-22 08:53 | 2013-09-22 | 2013-09-22 10:36 | Calculated | TF1343 | TF1343 - Transformer Fuse: TF1343 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 1 | 24514 | 103 | 0.0042 | 4.0793e-05 | 10 | 1030 | 2013/2014 | September-2013 | 9 | 2013
29368 | Lightning | 2013-09-22 09:40 | 2013-09-22 | 2013-09-22 12:17 | Calculated | TF2957 | TF2957 - Transformer Fuse: TF2957 |  | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 1 | 24514 | 157 | 0.0064 | 4.0793e-05 | 30 | 4710 | 2013/2014 | September-2013 | 9 | 2013
29372 | Lightning | 2013-09-22 09:53 | 2013-09-22 | 2013-09-22 12:59 | Calculated | TF1397 | TF1397 - Transformer Fuse: TF1397 |  | 106SEG173 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 2 | 24514 | 372 | 0.01518 | 8.1586e-05 | 15 | 2790 | 2013/2014 | September-2013 | 9 | 2013
29369 | Lightning | 2013-09-22 10:23 | 2013-09-22 | 2013-09-22 11:35 | Calculated | TF582 | TF582 - Transformer Fuse: TF582 |  | 103SEG520-228 | Benneydale 103-03 | Urban A | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 1 | 24514 | 72 | 0.00294 | 4.0793e-05 | 750 | 54000 | 2013/2014 | September-2013 | 9 | 2013
29370 | Lightning | 2013-09-22 11:40 | 2013-09-22 | 2013-09-22 12:10 | Calculated | TF16 | TF16 - Transformer Fuse: TF16 |  | 103SEG228-226 | Benneydale 103-03 | Urban A | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 1 | 24514 | 30 | 0.00122 | 4.0793e-05 | 30 | 900 | 2013/2014 | September-2013 | 9 | 2013
29371 | Lightning | 2013-09-22 11:49 | 2013-09-22 | 2013-09-22 13:41 | Calculated | TF1387 | TF1387 - Transformer Fuse: TF1387 |  | 103SEG728 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 3 | 24514 | 336 | 0.01371 | 0.00012238 | 10 | 1119 | 2013/2014 | September-2013 | 9 | 2013
29373 | Tree On Line - No Access | 2013-09-22 13:44 | 2013-09-22 | 2013-09-23 16:53 | Calculated | TF7I39 | TF7I39 - Transformer Fuse: TF7I39 |  | 402SEG5637 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1629 | 2 | 24514 | 3258 | 0.1329 | 8.1586e-05 | 30 | 48870 | 2013/2014 | September-2013 | 9 | 2013
29374 | Line Down | 2013-09-22 18:37 | 2013-09-22 | 2013-09-24 15:24 | Calculated | 5668 | 5668 - Fused Link 5668 |  | 410SEG5668 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1683 | 71 | 24514 | 35385 | 1.4435 | 0.0028963 | 438 | 175817 | 2013/2014 | September-2013 | 9 | 2013
29375 | Lightning | 2013-09-23 06:10 | 2013-09-23 | 2013-09-23 08:10 | Calculated | TF12O05 | TF12O05 - Transformer Fuse: TF12O05 |  | 418SEG5590-5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 120 | 1 | 24514 | 120 | 0.0049 | 4.0793e-05 | 15 | 1800 | 2013/2014 | September-2013 | 9 | 2013
29376 | Lightning | 2013-09-23 06:45 | 2013-09-23 | 2013-09-23 07:56 | Calculated | TF198 | TF198 - Transformer Fuse: TF198 |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 3 | 24514 | 213 | 0.00869 | 0.00012238 | 30 | 2130 | 2013/2014 | September-2013 | 9 | 2013
29377 | Branch On Line | 2013-09-23 06:48 | 2013-09-23 | 2013-09-23 10:46 | Calculated | 1335 | 1335 - Sectionaliser 1335 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 238 | 17 | 24514 | 4046 | 0.16505 | 0.00069348 | 148 | 35224 | 2013/2014 | September-2013 | 9 | 2013
29378 | Lightning | 2013-09-23 08:06 | 2013-09-23 | 2013-09-23 09:52 | Calculated | TF1503 | TF1503 - Transformer Fuse: TF1503 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 2 | 24514 | 212 | 0.00865 | 8.1586e-05 | 15 | 1590 | 2013/2014 | September-2013 | 9 | 2013
29379 | Lightning | 2013-09-23 08:59 | 2013-09-23 | 2013-09-23 10:22 | Calculated | TF2676 | TF2676 - Transformer Fuse: TF2676 |  | 106SEG224-361 | Rangitoto 106-07 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 2 | 24514 | 166 | 0.00677 | 8.1586e-05 | 15 | 1245 | 2013/2014 | September-2013 | 9 | 2013
29380 | Lightning | 2013-09-23 09:52 | 2013-09-23 | 2013-09-23 12:27 | Calculated | TF1290 | TF1290 - Transformer Fuse: TF1290 |  | 109SEG2041-2228 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 1 | 24514 | 155 | 0.00632 | 4.0793e-05 | 5 | 775 | 2013/2014 | September-2013 | 9 | 2013
29381 | Slip - Exposed L/V Cables | 2013-09-23 11:01 | 2013-09-23 | 2013-09-23 11:51 | Calculated | TF464 | TF464 - Transformer Fuse: TF464 |  | 106SEG590 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOL1 | Pole Leaning | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 51 | 24514 | 2550 | 0.10402 | 0.0020804 | 300 | 14999 | 2013/2014 | September-2013 | 9 | 2013
29382 | Faulty Tx 2229 | 2013-09-23 12:48 | 2013-09-23 | 2013-09-23 18:25 | Calculated | TF2229 | TF2229 - Transformer Fuse: TF2229 |  | 128SEG1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 337 | 44 | 24514 | 4032 | 0.16448 | 0.0017949 | 305.5 | 33605 | 2013/2014 | September-2013 | 9 | 2013
29383 | Old Age | 2013-09-23 13:46 | 2013-09-23 | 2013-09-23 14:40 | Calculated | 5742 | 5742 - Fused Link 5742 |  | 404SEG5742 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 2 | 24514 | 108 | 0.00441 | 8.1586e-05 | 30 | 1620 | 2013/2014 | September-2013 | 9 | 2013
29384 | Lightning | 2013-09-23 14:06 | 2013-09-23 | 2013-09-23 17:05 | Calculated | TF2844 | TF2844 - Transformer Fuse: TF2844 |  | 129SEG1749-2204 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 3 | 24514 | 537 | 0.02191 | 0.00012238 | 15 | 2685 | 2013/2014 | September-2013 | 9 | 2013
29386 | Blown HV Fuse - Unknown Fault | 2013-09-23 14:46 | 2013-09-23 | 2013-09-23 16:16 | Calculated | TF9C2 | TF9C2 - Transformer Fuse: TF9C2 |  | 413SEG5456-5461 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 90 | 2 | 24514 | 180 | 0.00734 | 8.1586e-05 | 15 | 1350 | 2013/2014 | September-2013 | 9 | 2013
29387 | Blown HV Fuse - Unknown Fault | 2013-09-23 16:24 | 2013-09-23 | 2013-09-23 17:16 | Calculated | TF4161 | TF4161 - Transformer Fuse: TF4161 |  | 415SEGREG28-6788 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 2 | 24514 | 104 | 0.00424 | 8.1586e-05 | 50 | 2600 | 2013/2014 | September-2013 | 9 | 2013
29388 | Suspect Bird Strike | 2013-09-24 06:41 | 2013-09-24 | 2013-09-24 08:47 | Calculated | TF520 | TF520 - Transformer Fuse: TF520 |  | 125SEG296-583 | Coast 125-04 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 2 | 24514 | 252 | 0.01028 | 8.1586e-05 | 30 | 3780 | 2013/2014 | September-2013 | 9 | 2013
29389 | Wind | 2013-09-24 08:52 | 2013-09-24 | 2013-09-24 12:50 | Calculated | TF2722 | TF2722 - Transformer Fuse: TF2722 |  | 109SEG2041-2228 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 238 | 1 | 24514 | 238 | 0.00971 | 4.0793e-05 | 15 | 3570 | 2013/2014 | September-2013 | 9 | 2013
29390 | Change Tx | 2013-09-24 09:00 | 2013-09-24 | 2013-09-24 14:55 | Calculated | TF11S4 | TF11S4 - Transformer Fuse: TF11S4 |  | 424SEG5207-6657 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 355 | 6 | 24514 | 2130 | 0.08689 | 0.00024476 | 100 | 35499 | 2013/2014 | September-2013 | 9 | 2013
29391 | Refer 2013 / 324 Replace Poles & X/arms | 2013-09-24 09:02 | 2013-09-24 | 2013-09-24 14:17 | Calculated | 234 | 234 - Fused Link 234 |  | 107SEG234 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 315 | 17 | 24514 | 5355 | 0.21845 | 0.00069348 | 107.5 | 33862 | 2013/2014 | September-2013 | 9 | 2013
29392 | Faulty Tx - Bulldozer Job | 2013-09-24 09:11 | 2013-09-24 | 2013-09-25 12:38 | Calculated | TF2815 | TF2815 - Transformer Fuse: TF2815 |  | 103SEG REG14-669 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1647 | 1 | 24514 | 1647 | 0.06719 | 4.0793e-05 | 15 | 24705 | 2013/2014 | September-2013 | 9 | 2013
29393 | Wind | 2013-09-24 09:58 | 2013-09-24 | 2013-09-24 14:28 | Calculated | 717 | 717 - Fused Link 717 |  | 116SEG717 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 270 | 5 | 24514 | 1350 | 0.05507 | 0.00020397 | 35 | 9450 | 2013/2014 | September-2013 | 9 | 2013
29395 | Wind - L/V Line Down | 2013-09-24 19:23 | 2013-09-24 | 2013-09-24 21:37 | Calculated | TF1474 | TF1474 - Transformer Fuse: TF1474 |  | 125SEG281-298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 6 | 24514 | 804 | 0.0328 | 0.00024476 | 30 | 4020 | 2013/2014 | September-2013 | 9 | 2013
29396 | Floating Insulator @Tx 215 | 2013-09-24 20:53 | 2013-09-24 | 2013-09-25 00:04 | Calculated | 545 | 545 - Air Break Switch 545 |  | 112SEG545-326 | Otorohanga 112-05 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 163 | 24514 | 16711 | 0.68169 | 0.0066493 | 1603 | 160602 | 2013/2014 | September-2013 | 9 | 2013
29397 | Faulty Tx | 2013-09-24 21:00 | 2013-09-24 | 2013-09-25 12:57 | Calculated | TF520 | TF520 - Transformer Fuse: TF520 |  | 125SEG296-583 | Coast 125-04 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 957 | 2 | 24514 | 1914 | 0.07808 | 8.1586e-05 | 25 | 23925 | 2013/2014 | September-2013 | 9 | 2013
29398 | Wind | 2013-09-24 21:45 | 2013-09-24 | 2013-09-24 21:55 | Calculated | 127 | 127 - Recloser 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 601 | 24514 | 6010 | 0.24517 | 0.024517 | 6692.5 | 66924 | 2013/2014 | September-2013 | 9 | 2013
29399 | Wind | 2013-09-24 21:49 | 2013-09-24 | 2013-09-24 23:33 | Calculated | 2144 | 2144 - Fused Link 2144 |  | 110SEG390-2144 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 6 | 24514 | 624 | 0.02545 | 0.00024476 | 65 | 6760 | 2013/2014 | September-2013 | 9 | 2013
29400 | Wind - L/V Clashing | 2013-09-24 22:16 | 2013-09-24 | 2013-09-24 23:38 | Calculated | TF11 | TF11 - Transformer Fuse: TF11 |  | 104SEG214-639 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 47 | 24514 | 3854 | 0.15722 | 0.0019173 | 100 | 8199 | 2013/2014 | September-2013 | 9 | 2013
29401 | Pole Down | 2013-09-24 23:41 | 2013-09-24 | 2013-09-25 17:22 | Calculated | 1512 | 1512 - Recloser 1512 |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1019 | 172 | 24514 | 48176 | 1.9652 | 0.0070164 | 1153 | 310635 | 2013/2014 | September-2013 | 9 | 2013
29403 | Wind - Poles 8 & 9 Down | 2013-09-25 01:09 | 2013-09-25 | 2013-09-25 14:06 | Calculated | 5408 | 5408 - Fused Link 5408 |  | 426SEG5408-5296 | Waihaha 426-02 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 777 | 243 | 24514 | 83899 | 3.4225 | 0.0099127 | 1853.5 | 684205 | 2013/2014 | September-2013 | 9 | 2013
29404 | Faulty Tx | 2013-09-25 02:20 | 2013-09-25 | 2013-09-25 19:01 | Calculated | TF5G7 | TF5G7 - Transformer Fuse: TF5G7 |  | 422SEG6555-5728 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1001 | 2 | 24514 | 2002 | 0.08167 | 8.1586e-05 | 10 | 10010 | 2013/2014 | September-2013 | 9 | 2013
29405 | Wind | 2013-09-25 02:41 | 2013-09-25 | 2013-09-25 06:05 | Calculated | 5475 | 5475 - Recloser with Bypass & Links 5475 |  | 421SEG5470-5475 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 204 | 43 | 24514 | 8772 | 0.35784 | 0.0017541 | 315 | 64260 | 2013/2014 | September-2013 | 9 | 2013
29406 | Wind | 2013-09-25 04:51 | 2013-09-25 | 2013-09-25 06:26 | Calculated | TF1042 | TF1042 - Transformer Fuse: TF1042 |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 3 | 24514 | 285 | 0.01163 | 0.00012238 | 50 | 4749 | 2013/2014 | September-2013 | 9 | 2013
29407 | Wind | 2013-09-25 05:11 | 2013-09-25 | 2013-09-25 06:37 | Calculated | TF1787 | TF1787 - Transformer Fuse: TF1787 |  | 117SEG1315-1326 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 86 | 5 | 24514 | 430 | 0.01754 | 0.00020397 | 15 | 1290 | 2013/2014 | September-2013 | 9 | 2013
29408 | Wind | 2013-09-25 06:18 | 2013-09-25 | 2013-09-25 06:51 | Calculated | 2144 | 2144 - Fused Link 2144 |  | 110SEG390-2144 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 6 | 24514 | 198 | 0.00808 | 0.00024476 | 65 | 2145 | 2013/2014 | September-2013 | 9 | 2013
29409 | Branch On Line | 2013-09-25 08:32 | 2013-09-25 | 2013-09-25 09:36 | Calculated | 1.27 | 1.27 - Fused Link 1.27 |  | 404SEGF1.27 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 6 | 24514 | 384 | 0.01566 | 0.00024476 | 25 | 1600 | 2013/2014 | September-2013 | 9 | 2013
29410 | Blown HV Fuse - Unknown Fault | 2013-09-25 09:31 | 2013-09-25 | 2013-09-25 13:22 | Calculated | TF2862 | TF2862 - Transformer Fuse: TF2862 |  | 117SEG1322 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 231 | 1 | 24514 | 231 | 0.00942 | 4.0793e-05 | 3 | 693 | 2013/2014 | September-2013 | 9 | 2013
29411 | Wind - Pole Down | 2013-09-25 09:58 | 2013-09-25 | 2013-09-25 11:49 | Calculated | 341 | 341 - Fused Link 341 |  | 109SEG341-587 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 39 | 24514 | 4329 | 0.17659 | 0.0015909 | 345 | 38294 | 2013/2014 | September-2013 | 9 | 2013
29413 | L/V Line Down | 2013-09-25 10:43 | 2013-09-25 | 2013-09-25 12:32 | Calculated | TF1474 | TF1474 - Transformer Fuse: TF1474 |  | 125SEG281-298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 6 | 24514 | 654 | 0.02668 | 0.00024476 | 30 | 3270 | 2013/2014 | September-2013 | 9 | 2013
29414 | Tree vs Tx 491 - Replace Structure | 2013-09-25 11:45 | 2013-09-25 | 2013-09-25 16:14 | Calculated | TF491 | TF491 - Transformer Fuse: TF491 |  | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 269 | 2 | 24514 | 538 | 0.02195 | 8.1586e-05 | 10 | 2690 | 2013/2014 | September-2013 | 9 | 2013
29415 | Blown HV Fuse - Unknown Fault | 2013-09-25 12:30 | 2013-09-25 | 2013-09-25 13:28 | Calculated | TF758 | TF758 - Transformer Fuse: TF758 |  | 120SEG2065 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 1 | 24514 | 58 | 0.00237 | 4.0793e-05 | 25 | 1450 | 2013/2014 | September-2013 | 9 | 2013
29416 | Wind | 2013-09-25 15:03 | 2013-09-25 | 2013-09-25 17:11 | Calculated | TF1289 | TF1289 - Transformer Fuse: TF1289 |  | 109SEG2041-2228 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 1 | 24514 | 128 | 0.00522 | 4.0793e-05 | 15 | 1920 | 2013/2014 | September-2013 | 9 | 2013
29417 | Vibration - Fell Out | 2013-09-25 17:08 | 2013-09-25 | 2013-09-25 17:57 | Calculated | TF1541 | TF1541 - Transformer Fuse: TF1541 |  | 111SEG579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 1 | 24514 | 49 | 0.002 | 4.0793e-05 | 25 | 1225 | 2013/2014 | September-2013 | 9 | 2013
29418 | L/V Line Down | 2013-09-25 22:28 | 2013-09-25 | 2013-09-25 23:30 | Calculated | TF1096 | TF1096 - Transformer Fuse: TF1096 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 3 | 24514 | 186 | 0.00759 | 0.00012238 | 30 | 1860 | 2013/2014 | September-2013 | 9 | 2013
29402 | Wind | 2013-09-25 23:21 | 2013-09-25 | 2013-09-26 00:52 | Calculated | 5494 | 5494 - Recloser with Bypass 5494 |  | 410SEG5494-5493 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 91 | 40 | 24514 | 3640 | 0.14849 | 0.0016317 | 270 | 24569 | 2013/2014 | September-2013 | 9 | 2013
29419 | Replace Pole - SWER B/F | 2013-09-26 09:09 | 2013-09-26 | 2013-09-26 09:12 | Calculated | 1647 | 1647 - Fused Link 1647 |  | 115SEG1647-1646 | Mokauiti 115-05 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOL1 | Pole Leaning | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 3 | 19 | 24514 | 57 | 0.00233 | 0.00077507 | 170 | 509 | 2013/2014 | September-2013 | 9 | 2013
29420 | Resage LV after Tx Replaced | 2013-09-26 09:21 | 2013-09-26 | 2013-09-26 13:01 | Calculated | TF5G7 | TF5G7 - Transformer Fuse: TF5G7 |  | 422SEG6555-5728 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 220 | 2 | 24514 | 440 | 0.01795 | 8.1586e-05 | 10 | 2200 | 2013/2014 | September-2013 | 9 | 2013
29422 | Replace Pole After Storm | 2013-09-26 10:08 | 2013-09-26 | 2013-09-26 13:07 | Calculated | 341 | 341 - Fused Link 341 |  | 109SEG341-587 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 39 | 24514 | 6981 | 0.28478 | 0.0015909 | 345 | 61754 | 2013/2014 | September-2013 | 9 | 2013
29421 | Change DDO | 2013-09-26 10:22 | 2013-09-26 | 2013-09-26 12:23 | Calculated | TF1369 | TF1369 - Transformer Fuse: TF1369 |  | 107SEG575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 3 | 24514 | 363 | 0.01481 | 0.00012238 | 50 | 6049 | 2013/2014 | September-2013 | 9 | 2013
29423 | Line Down | 2013-09-26 11:47 | 2013-09-26 | 2013-09-26 15:05 | Calculated | TF403 | TF403 - Transformer Fuse: TF403 |  | 111SEG360-395 | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 6 | 24514 | 1188 | 0.04846 | 0.00024476 | 25 | 4949 | 2013/2014 | September-2013 | 9 | 2013
29424 | Replace Leaning Pole | 2013-09-27 10:40 | 2013-09-27 | 2013-09-27 13:11 | Calculated | 1647 | 1647 - Fused Link 1647 |  | 115SEG1647-1646 | Mokauiti 115-05 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOL1 | Pole Leaning | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 151 | 27 | 24514 | 3909 | 0.15946 | 0.0011014 | 220 | 32169 | 2013/2014 | September-2013 | 9 | 2013
29425 | Upgrade earth Mat | 2013-09-27 10:55 | 2013-09-27 | 2013-09-27 13:57 | Calculated | TF2260 | TF2260 - Transformer Fuse: TF2260 |  | 107SEG575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 182 | 2 | 24514 | 364 | 0.01485 | 8.1586e-05 | 30 | 5460 | 2013/2014 | September-2013 | 9 | 2013
29426 | Upgrade Tx | 2013-09-27 11:28 | 2013-09-27 | 2013-09-27 14:25 | Calculated | TF915 | TF915 - Transformer Fuse: TF915 |  | 103SEG459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 177 | 2 | 24514 | 354 | 0.01444 | 8.1586e-05 | 10 | 1770 | 2013/2014 | September-2013 | 9 | 2013
29427 | Tree - Line Down / Gen Set Connected | 2013-09-28 03:30 | 2013-09-28 | 2013-09-28 16:12 | Calculated | TF752 | TF752 - Transformer Fuse: TF752 |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 762 | 7 | 24514 | 4843 | 0.19756 | 0.00028555 | 75 | 48585 | 2013/2014 | September-2013 | 9 | 2013
29428 | Wind | 2013-09-28 13:55 | 2013-09-28 | 2013-09-28 15:50 | Calculated | 5485 | 5485 - Fused Link 5485 |  | 408SEG5485-5791 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 20 | 24514 | 2300 | 0.09382 | 0.00081586 | 160 | 18400 | 2013/2014 | September-2013 | 9 | 2013
29429 | Vehicle vs Pole | 2013-09-29 04:33 | 2013-09-29 | 2013-09-29 10:03 | Calculated | TF720 | TF720 - Transformer Fuse: TF720 |  | 120SEG632 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 330 | 3 | 24514 | 990 | 0.04039 | 0.00012238 | 15 | 4950 | 2013/2014 | September-2013 | 9 | 2013
29430 | Replace Doors To Tx Room | 2013-09-29 09:12 | 2013-09-29 | 2013-09-29 13:15 | Calculated | 2153 | 2153 - Fused Link 2153 |  | 115SEG682-1701 | Mokauiti 115-01 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 243 | 1 | 24514 | 243 | 0.00991 | 4.0793e-05 | 300 | 72900 | 2013/2014 | September-2013 | 9 | 2013
29431 | Blown HV Fuse - Unknown Fault | 2013-09-30 08:48 | 2013-09-30 | 2013-09-30 10:46 | Calculated | TF9D6 | TF9D6 - Transformer Fuse: TF9D6 |  | 413SEG5410 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 118 | 1 | 24514 | 118 | 0.00481 | 4.0793e-05 | 5 | 590 | 2013/2014 | September-2013 | 9 | 2013
29432 | Possible Faulty Tx | 2013-09-30 14:05 | 2013-09-30 | 2013-09-30 16:36 | Calculated | TF2220 | TF2220 - Transformer Fuse: TF2220 |  | 128SEG1628 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 151 | 1 | 24514 | 151 | 0.00616 | 4.0793e-05 | 5 | 755 | 2013/2014 | September-2013 | 9 | 2013
29433 | Faulty DDO | 2013-09-30 19:08 | 2013-09-30 | 2013-09-30 21:09 | Calculated | 351 | 351 - Air Break Switch 351 |  | 111SEG351-647 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 200 | 24514 | 11426 | 0.4661 | 0.0081586 | 2430 | 136391 | 2013/2014 | September-2013 | 9 | 2013
29434 | Lightining | 2013-10-01 08:11 | 2013-10-01 | 2013-10-01 10:22 | Calculated | TF2928 | TF2928 - Transformer Fuse: TF2928 |  | 128SEG1611-1612 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 131 | 2 | 24499 | 262 | 0.01069 | 8.1636e-05 | 7.5 | 982 | 2013/2014 | October-2013 | 10 | 2013
29435 | Faulty L/A | 2013-10-01 14:43 | 2013-10-01 | 2013-10-01 17:50 | Calculated | 290 | 290 - Air Break Switch 290 |  | 101SEG552-290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 187 | 98 | 24499 | 7228 | 0.29503 | 0.0040002 | 791 | 57736 | 2013/2014 | October-2013 | 10 | 2013
29436 | Pull Up Low L/V | 2013-10-01 15:14 | 2013-10-01 | 2013-10-01 17:45 | Calculated | TF368 | TF368 - Transformer Fuse: TF368 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 3 | 24499 | 453 | 0.01849 | 0.00012245 | 15 | 2265 | 2013/2014 | October-2013 | 10 | 2013
29437 | Old Age | 2013-10-01 16:14 | 2013-10-01 | 2013-10-01 18:00 | Calculated | TF2540 | TF2540 - Transformer Fuse: TF2540 |  | 125SEG298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 2 | 24499 | 212 | 0.00865 | 8.1636e-05 | 15 | 1590 | 2013/2014 | October-2013 | 10 | 2013
29438 | Unknown E/F | 2013-10-01 18:46 | 2013-10-01 | 2013-10-01 18:57 | Calculated | 2062 | 2062 - Circuit Breaker Maraetai 11 kV 2062 |  | No Segment | 210-01 Maraetai | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 1224 | 24499 | 12814 | 0.52304 | 0.049961 | 12726 | 133459 | 2013/2014 | October-2013 | 10 | 2013
29439 | Birds | 2013-10-01 19:42 | 2013-10-01 | 2013-10-01 21:04 | Calculated | TF2048 | TF2048 - Transformer Fuse: TF2048 |  | 117SEG1729 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 82 | 2 | 24499 | 164 | 0.00669 | 8.1636e-05 | 10 | 820 | 2013/2014 | October-2013 | 10 | 2013
29442 | Vehicle vs Line | 2013-10-02 22:26 | 2013-10-02 | 2013-10-03 00:32 | Calculated | TF2 | TF2 - Transformer Fuse: TF2 |  | 106SEG203-205 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 63 | 24499 | 7938 | 0.32401 | 0.0025715 | 200 | 25199 | 2013/2014 | October-2013 | 10 | 2013
29445 | Line Down | 2013-10-03 08:52 | 2013-10-03 | 2013-10-03 11:52 | Calculated | T2953 | TF2953 - Transformer Fuse: TF2953 |  | 128SEG1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 25 | 24499 | 4500 | 0.18368 | 0.0010204 | 160 | 28799 | 2013/2014 | October-2013 | 10 | 2013
29443 | Refer 2013 / 332 Replace Poles & X/arms | 2013-10-03 09:02 | 2013-10-03 | 2013-10-03 15:26 | Calculated | 239 | 239 - Fused Link 239 |  | 107SEG239-508 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 384 | 35 | 24499 | 13440 | 0.54859 | 0.0014286 | 205 | 78719 | 2013/2014 | October-2013 | 10 | 2013
29444 | Refer 2013 / 333 Replace Hardware @ Tx's 3G3 & 3G6 | 2013-10-03 09:41 | 2013-10-03 | 2013-10-03 15:34 | Calculated | 5435 | 5435 - Fused Link 5435 |  | 421SEG5435 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 353 | 6 | 24499 | 2118 | 0.08645 | 0.00024491 | 45 | 15885 | 2013/2014 | October-2013 | 10 | 2013
29446 | Blown HV Fuse - Unknown Fault | 2013-10-03 16:44 | 2013-10-03 | 2013-10-03 17:27 | Calculated | TF4180 | TF4180 - Transformer Fuse: TF4180 |  | 406SEG6022 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 1 | 24499 | 43 | 0.00176 | 4.0818e-05 | 15 | 645 | 2013/2014 | October-2013 | 10 | 2013
29394 | Blown HV Fuse - Unknown Fault | 2013-10-04 08:00 | 2013-10-04 | 2013-10-04 09:12 | Calculated | TF8J9 | TF8J9 - Transformer Fuse: TF8J9 |  | 404SEG5229 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 2 | 24499 | 144 | 0.00588 | 8.1636e-05 | 30 | 2160 | 2013/2014 | October-2013 | 10 | 2013
29447 | Refer 2013 / 334 Replace Poles & X//arms | 2013-10-04 09:03 | 2013-10-04 | 2013-10-04 15:24 | Calculated | 244 | 244 - Air Break Switch 244 |  | 107SEG244-575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 381 | 41 | 24499 | 15621 | 0.63762 | 0.0016735 | 435 | 165734 | 2013/2014 | October-2013 | 10 | 2013
29448 | Refer 2013 / 335 Change CT Metering | 2013-10-04 09:59 | 2013-10-04 | 2013-10-04 12:40 | Calculated | 1004 | 1004 - Air Break Switch 1004 |  | No Segment | 207-01 Wairere Falls | Rural D | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 156 | 2 | 24499 | 312 | 0.01274 | 8.1636e-05 | 15 | 2340 | 2013/2014 | October-2013 | 10 | 2013
29449 | Private Line Maintenace | 2013-10-04 12:09 | 2013-10-04 | 2013-10-04 12:33 | Calculated | TF2079 | TF2079 - Transformer Fuse: TF2079 |  | 117SEG2179 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 24 | 2 | 24499 | 48 | 0.00196 | 8.1636e-05 | 10 | 240 | 2013/2014 | October-2013 | 10 | 2013
29450 | Wind | 2013-10-04 14:44 | 2013-10-04 | 2013-10-04 17:02 | Calculated | TF1889 | TF1889 - Transformer Fuse: TF1889 |  | 128SEG1358-1602 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 2 | 24499 | 276 | 0.01127 | 8.1636e-05 | 15 | 2070 | 2013/2014 | October-2013 | 10 | 2013
29451 | Pillar Box Fault | 2013-10-05 17:13 | 2013-10-05 | 2013-10-05 20:57 | Calculated | TF8 | TF8 - Transformer Fuse: TF8 |  | 107SEG201 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 224 | 55 | 24499 | 12320 | 0.50288 | 0.002245 | 200 | 44799 | 2013/2014 | October-2013 | 10 | 2013
29452 | Earth Fault | 2013-10-06 08:16 | 2013-10-06 | 2013-10-06 13:43 | Calculated | 570 | 570 - Circuit Breaker 570 |  | 303SEG162-164 | Te Waireka Road 303-01 | Urban A | Te Waireka Rd 33 | Direct from Hangatiki Supply |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24499 |  | 0 | 0 |  |  | 2013/2014 | October-2013 | 10 | 2013
29453 | Blown HV Fuse - Unknown Fault | 2013-10-06 13:22 | 2013-10-06 | 2013-10-06 14:46 | Calculated | TF4163 | TF4163 - Transformer Fuse: TF4163 |  | 426SEG5531 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 1 | 24499 | 84 | 0.00343 | 4.0818e-05 | 30 | 2520 | 2013/2014 | October-2013 | 10 | 2013
29454 | Refer 2013 / 341 Northern Feeder Renewal Project | 2013-10-07 08:58 | 2013-10-07 | 2013-10-07 16:04 | Calculated | 5343 | 5343 - Fused Link 5343 |  | 402SEG5343-5446 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 411 | 108 | 24499 | 27006 | 1.1023 | 0.0044083 | 1075 | 311137 | 2013/2014 | October-2013 | 10 | 2013
29455 | Change Transformer | 2013-10-07 10:12 | 2013-10-07 | 2013-10-07 11:20 | Calculated | TF235 | TF235 - Transformer Fuse: TF235 |  | 111SEG342-544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 68 | 3 | 24499 | 204 | 0.00833 | 0.00012245 | 25 | 1699 | 2013/2014 | October-2013 | 10 | 2013
29456 | Line Down | 2013-10-07 15:46 | 2013-10-07 | 2013-10-07 19:04 | Calculated | 1325 | 1325 - Fused Link 1325 |  | 103SEG1335-1301 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 198 | 4 | 24499 | 792 | 0.03233 | 0.00016327 | 30 | 5940 | 2013/2014 | October-2013 | 10 | 2013
29457 | Jumper Off | 2013-10-07 16:06 | 2013-10-07 | 2013-10-07 16:51 | Calculated | TF10E02 | TF10E02 - Transformer Fuse: TF10E02 |  | 413SEG5453-5647 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 45 | 1 | 24499 | 45 | 0.00184 | 4.0818e-05 | 15 | 675 | 2013/2014 | October-2013 | 10 | 2013
29458 | L/V Maintenance | 2013-10-08 09:00 | 2013-10-08 | 2013-10-08 13:01 | Calculated | TF1467 | TF1467 - Transformer Fuse: TF1467 |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 241 | 5 | 24499 | 1205 | 0.04919 | 0.00020409 | 50 | 12050 | 2013/2014 | October-2013 | 10 | 2013
29459 | Refer 2013 / 338 Northern Feeder Renewal Project | 2013-10-08 09:05 | 2013-10-08 | 2013-10-08 16:08 | Calculated | 5797 | 5797 - Fused Link 5797 |  | 402SEG5797-5777 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 381 | 39 | 24499 | 8367 | 0.34152 | 0.0015919 | 282.5 | 57097 | 2013/2014 | October-2013 | 10 | 2013
29460 | Refer 2013 / 342 Replace Stay & LV X arms | 2013-10-08 09:35 | 2013-10-08 | 2013-10-08 12:50 | Calculated | 1531 | 1531 - Sectionaliser 1531 |  | 113SEG1531-1501 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 195 | 18 | 24499 | 3510 | 0.14327 | 0.00073472 | 130 | 25349 | 2013/2014 | October-2013 | 10 | 2013
29462 | Lightning | 2013-10-08 09:49 | 2013-10-08 | 2013-10-08 14:38 | Calculated | TF7L5 | TF7L5 - Transformer Fuse: TF7L5 |  | 408SEG5791 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 289 | 1 | 24499 | 289 | 0.0118 | 4.0818e-05 | 15 | 4335 | 2013/2014 | October-2013 | 10 | 2013
29463 | Lightning | 2013-10-08 18:57 | 2013-10-08 | 2013-10-08 22:32 | Calculated | 1021 | 1021 - Recloser 1021 |  | 112SEG314-1021 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 214 | 1340 | 24499 | 82049 | 3.3491 | 0.054696 | 9881.0769 | 772117 | 2013/2014 | October-2013 | 10 | 2013
29465 | Lightning | 2013-10-08 19:00 | 2013-10-08 | 2013-10-08 22:10 | Calculated | 209 | 209 - Fused Link 209 |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 190 | 56 | 24499 | 10640 | 0.4343 | 0.0022858 | 565 | 107349 | 2013/2014 | October-2013 | 10 | 2013
29466 | Lightning | 2013-10-08 19:00 | 2013-10-08 | 2013-10-09 10:49 | Calculated | TF493 | TF493 - Transformer Fuse: TF493 |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 949 | 2 | 24499 | 1898 | 0.07747 | 8.1636e-05 | 15 | 14235 | 2013/2014 | October-2013 | 10 | 2013
29467 | Lightning | 2013-10-08 19:00 | 2013-10-08 | 2013-10-08 23:27 | Calculated | TF556 | TF556 - Transformer Fuse: TF556 |  | 112SEG300-646 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 267 | 41 | 24499 | 10947 | 0.44683 | 0.0016735 | 0 | 0 | 2013/2014 | October-2013 | 10 | 2013
29469 | Lightning | 2013-10-08 20:44 | 2013-10-08 | 2013-10-08 23:35 | Calculated | TF3115 | TF3115 - Transformer Fuse: TF3115 |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 2 | 24499 | 342 | 0.01396 | 8.1636e-05 | 15 | 2565 | 2013/2014 | October-2013 | 10 | 2013
29468 | Lightning | 2013-10-08 21:09 | 2013-10-08 | 2013-10-08 23:20 | Calculated | TF1N1 | TF1N1 - Transformer Fuse: TF1N1 |  | 421SEG5933 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 131 | 3 | 24499 | 393 | 0.01604 | 0.00012245 | 15 | 1965 | 2013/2014 | October-2013 | 10 | 2013
29464 | Lightning | 2013-10-08 21:14 | 2013-10-08 | 2013-10-08 22:07 | Calculated | TF1385 | TF1385 - Transformer Fuse: TF1385 |  | 123SEG469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 2 | 24499 | 106 | 0.00433 | 8.1636e-05 | 10 | 530 | 2013/2014 | October-2013 | 10 | 2013
29470 | Wind | 2013-10-09 05:45 | 2013-10-09 | 2013-10-09 10:44 | Calculated | 1510 | 1510 - Fused Link 1510 |  | 113SEG1510-1636 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 299 | 172 | 24499 | 30780 | 1.2564 | 0.0070207 | 1153 | 203137 | 2013/2014 | October-2013 | 10 | 2013
29471 | Wind | 2013-10-09 06:21 | 2013-10-09 | 2013-10-09 07:44 | Calculated | 687 | 687 - Circuit Breaker 687 |  | 117SEG687-1289 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 227 | 24499 | 6356 | 0.25944 | 0.0092657 | 1884.5 | 52766 | 2013/2014 | October-2013 | 10 | 2013
29473 | Lightning | 2013-10-09 07:00 | 2013-10-09 | 2013-10-09 09:44 | Calculated | TF1594 | TF1594 - Transformer Fuse: TF1594 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 2 | 24499 | 328 | 0.01339 | 8.1636e-05 | 10 | 1640 | 2013/2014 | October-2013 | 10 | 2013
29475 | Lightning | 2013-10-09 08:30 | 2013-10-09 | 2013-10-09 11:10 | Calculated | TF2256 | TF2256 - Transformer Fuse: TF2256 |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 2 | 24499 | 320 | 0.01306 | 8.1636e-05 | 15 | 2400 | 2013/2014 | October-2013 | 10 | 2013
29477 | Wind | 2013-10-09 08:57 | 2013-10-09 | 2013-10-09 17:25 | Calculated | 1645 | 1645 - Solid Link 1645 |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 508 | 44 | 24499 | 18909 | 0.77183 | 0.001796 | 305.5 | 129371 | 2013/2014 | October-2013 | 10 | 2013
29472 | Refer 2013 / 339 Northern Feeder Renewal Project | 2013-10-09 09:16 | 2013-10-09 | 2013-10-09 16:16 | Calculated | 5777 | 5777 - Fused Link 5777 |  | 402SEG5797-5777 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 400 | 39 | 24499 | 10740 | 0.43839 | 0.0015919 | 282.5 | 78550 | 2013/2014 | October-2013 | 10 | 2013
29474 | Broken Pole | 2013-10-09 10:11 | 2013-10-09 | 2013-10-09 11:27 | Calculated | 170 | 170 - Electronic Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 21 | 24499 | 1596 | 0.06515 | 0.00085718 | 178 | 13528 | 2013/2014 | October-2013 | 10 | 2013
29476 | Lightning | 2013-10-09 10:31 | 2013-10-09 | 2013-10-09 11:46 | Calculated | TF896 | TF896 - Transformer Fuse: TF896 |  | 123SEG450-469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 3 | 24499 | 225 | 0.00918 | 0.00012245 | 30 | 2250 | 2013/2014 | October-2013 | 10 | 2013
29478 | Refer 2013 / 340 Northern Feeder Renewal Project | 2013-10-10 08:45 | 2013-10-10 | 2013-10-10 16:08 | Calculated | 5446 | 5446 - Sectionaliser with Bypass & Links 5446 |  | 402SEG5343-5446 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 368 | 68 | 24499 | 10742 | 0.43847 | 0.0027756 | 470 | 69665 | 2013/2014 | October-2013 | 10 | 2013
29479 | Refer 2013 / 346 Change Poles And X Arms | 2013-10-10 09:05 | 2013-10-10 | 2013-10-10 14:43 | Calculated | 575 | 575 - Fused Link 575 |  | 107SEG575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 338 | 13 | 24499 | 4394 | 0.17935 | 0.00053063 | 150 | 50699 | 2013/2014 | October-2013 | 10 | 2013
29480 | Refer 2013 / 343 Replace Insulators & Faulty Section Switch 5352 | 2013-10-10 09:34 | 2013-10-10 | 2013-10-10 14:30 | Calculated | 5108 | 5108 - Sectionaliser with Bypass 5108 |  | 402SEG5115-5108 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 250 | 128 | 24499 | 24640 | 1.0058 | 0.0052247 | 962.5 | 184872 | 2013/2014 | October-2013 | 10 | 2013
29481 | Private Line Maintenance | 2013-10-10 09:42 | 2013-10-10 | 2013-10-10 15:08 | Calculated | TF2079 | TF2079 - Transformer Fuse: TF2079 |  | 117SEG2179 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 326 | 2 | 24499 | 652 | 0.02661 | 8.1636e-05 | 10 | 3260 | 2013/2014 | October-2013 | 10 | 2013
29482 | Lightning | 2013-10-10 11:02 | 2013-10-10 | 2013-10-10 11:48 | Calculated | TF1278 | TF1278 - Transformer Fuse: TF1278 |  | 123SEG469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 2 | 24499 | 92 | 0.00376 | 8.1636e-05 | 10 | 460 | 2013/2014 | October-2013 | 10 | 2013
29483 | Burnt Pole | 2013-10-11 04:40 | 2013-10-11 | 2013-10-11 12:10 | Calculated | TF1706 | TF1706 - Transformer Fuse: TF1706 |  | 129SEG725 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 450 | 1 | 24499 | 450 | 0.01837 | 4.0818e-05 | 30 | 13500 | 2013/2014 | October-2013 | 10 | 2013
29486 | Wind | 2013-10-11 07:45 | 2013-10-11 | 2013-10-11 09:25 | Calculated | TF08P02 | TF08P02 - Transformer Fuse: TF08P02 |  | 426SEG5892-5240 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 100 | 3 | 24499 | 300 | 0.01225 | 0.00012245 | 15 | 1500 | 2013/2014 | October-2013 | 10 | 2013
29484 | Lightning | 2013-10-11 08:00 | 2013-10-11 | 2013-10-11 08:30 | Calculated | 5730 | 5730 - Fused Link 5730 |  | 416SEG5730-5676 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 13 | 24499 | 390 | 0.01592 | 0.00053063 | 120 | 3600 | 2013/2014 | October-2013 | 10 | 2013
29485 | Lightning | 2013-10-11 08:40 | 2013-10-11 | 2013-10-11 09:45 | Calculated | 5717 | 5717 - Fused Link 5717 |  | 416SEG5717 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 5 | 24499 | 325 | 0.01327 | 0.00020409 | 45 | 2925 | 2013/2014 | October-2013 | 10 | 2013
29487 | Broken Xarm | 2013-10-11 14:34 | 2013-10-11 | 2013-10-11 16:33 | Calculated | TF1190 | TF1190 - Transformer Fuse: TF1190 |  | 122SEG633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 3 | 24499 | 357 | 0.01457 | 0.00012245 | 15 | 1785 | 2013/2014 | October-2013 | 10 | 2013
29488 | Trees | 2013-10-11 17:12 | 2013-10-11 | 2013-10-11 20:49 | Calculated | 5538 | 5538 - Fused Link 5538 |  | 422SEG5538-5841 | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 217 | 28 | 24499 | 5804 | 0.23691 | 0.0011429 | 213.5 | 44357 | 2013/2014 | October-2013 | 10 | 2013
29490 | Wind | 2013-10-11 23:16 | 2013-10-11 | 2013-10-12 03:05 | Calculated | 360 | 360 - Air Break Switch 360 |  | 111SEG360-395 | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 229 | 227 | 24499 | 27623 | 1.1275 | 0.0092657 | 2305 | 254809 | 2013/2014 | October-2013 | 10 | 2013
29489 | Wind | 2013-10-11 23:23 | 2013-10-11 | 2013-10-11 23:27 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | 609SEG5180-5839 | 509-01 Kuratau | Rural D | No Feeder |  |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 4 | 24499 | 16 | 0.00065 | 0.00016327 | 450 | 1800 | 2013/2014 | October-2013 | 10 | 2013
29491 | Wind | 2013-10-11 23:34 | 2013-10-11 | 2013-10-12 10:48 | Calculated | 290 | 290 - Air Break Switch 290 |  | 101SEG552-290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 674 | 14 | 24499 | 9280 | 0.37879 | 0.00057145 | 105 | 69729 | 2013/2014 | October-2013 | 10 | 2013
29492 | Line Down | 2013-10-12 04:09 | 2013-10-12 | 2013-10-12 21:03 | Calculated | TF13F04 | TF13F04 - Transformer Fuse: TF13F04 |  | 410SEG5668 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1014 | 41 | 24499 | 14875 | 0.60717 | 0.0016735 | 180 | 63885 | 2013/2014 | October-2013 | 10 | 2013
29494 | Wind | 2013-10-12 07:32 | 2013-10-12 | 2013-10-12 13:59 | Calculated | 5293 | 5293 - Air Break Switch 5293 |  | 413SEG5293-5294 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 387 | 121 | 24499 | 10707 | 0.43704 | 0.004939 | 941 | 89955 | 2013/2014 | October-2013 | 10 | 2013
29493 | Lightning | 2013-10-12 08:25 | 2013-10-12 | 2013-10-12 09:23 | Calculated | TF1819 | TF1819 - Transformer Fuse: TF1819 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 58 | 2 | 24499 | 116 | 0.00473 | 8.1636e-05 | 7.5 | 435 | 2013/2014 | October-2013 | 10 | 2013
29495 | Wind | 2013-10-12 21:42 | 2013-10-12 | 2013-10-12 23:37 | Calculated | 411 | 411 - Recloser with Bypass & Links 411 |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 18 | 24499 | 756 | 0.03086 | 0.00073472 | 300 | 12600 | 2013/2014 | October-2013 | 10 | 2013
29496 | Line Down | 2013-10-13 08:59 | 2013-10-13 | 2013-10-13 15:14 | Calculated | 1615 | 1615 - Sectionaliser with Bypass & Links 1615 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 375 | 17 | 24499 | 6375 | 0.26021 | 0.00069391 | 135 | 50625 | 2013/2014 | October-2013 | 10 | 2013
29497 | Wind | 2013-10-14 12:58 | 2013-10-14 | 2013-10-14 14:25 | Calculated | TF355 | TF355 - Transformer Fuse: TF355 |  | 112SEG774 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 1 | 24499 | 87 | 0.00355 | 4.0818e-05 | 15 | 1305 | 2013/2014 | October-2013 | 10 | 2013
29498 | Unknown | 2013-10-14 13:58 | 2013-10-14 | 2013-10-14 19:30 | Calculated | 687 | 687 - Circuit Breaker 687 |  | 117SEG687-1289 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 227 | 24499 | 681 | 0.0278 | 0.0092657 | 1892 | 5676 | 2013/2014 | October-2013 | 10 | 2013
29499 | Stay Wire Touching Line | 2013-10-14 17:50 | 2013-10-14 | 2013-10-14 19:39 | Calculated | 1311 | 1311 - Air Break Switch 1311 |  | 117SEG1311-1299 | Te Mapara 117-02 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DICL | Conductor Low - Incorrect Clearances | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 103 | 24499 | 9167 | 0.37418 | 0.0042043 | 840.5 | 74804 | 2013/2014 | October-2013 | 10 | 2013
29500 | Wind | 2013-10-14 18:15 | 2013-10-14 | 2013-10-15 17:45 | Calculated | 1616 | 1616 - Sectionaliser with Bypass & Links 1616 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1290 | 54 | 24499 | 21476 | 0.87661 | 0.0022042 | 415.5 | 180321 | 2013/2014 | October-2013 | 10 | 2013
29501 | Wind | 2013-10-15 00:25 | 2013-10-15 | 2013-10-16 14:53 | Calculated | TF2006 | TF2006 - Transformer Fuse: TF2006 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2308 | 601 | 24499 | 118163 | 4.8232 | 0.024532 | 3576.5 | 696235 | 2013/2014 | October-2013 | 10 | 2013
29502 | Wind | 2013-10-15 02:44 | 2013-10-15 | 2013-10-15 05:36 | Calculated | TF230 | TF230 - Transformer Fuse: TF230 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 6 | 24499 | 1032 | 0.04212 | 0.00024491 | 30 | 5160 | 2013/2014 | October-2013 | 10 | 2013
29504 | Wind | 2013-10-15 04:13 | 2013-10-15 | 2013-10-15 05:17 | Calculated | 1317 | 1317 - Fused Link 1317 |  | 117SEG1317 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 5 | 24499 | 320 | 0.01306 | 0.00020409 | 75 | 4800 | 2013/2014 | October-2013 | 10 | 2013
29503 | Wind | 2013-10-15 04:23 | 2013-10-15 | 2013-10-15 09:36 | Calculated | TPOngarue CB192 | TPOngarue CB192 - 33kV Minimum Oil Circuit Breaker TP192 |  | No Segment | 514-01 Transpower Ongarue | Rural D | No Feeder |  |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 11 | 4153 | 24499 | 44489 | 1.8159 | 0.16952 | 29494.7554 | 315226 | 2013/2014 | October-2013 | 10 | 2013
29505 | Wind | 2013-10-15 04:50 | 2013-10-15 | 2013-10-15 05:52 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 26 | 24499 | 9516 | 0.38842 | 0.0010613 | 330 | 120780 | 2013/2014 | October-2013 | 10 | 2013
29520 | Wind | 2013-10-15 06:27 | 2013-10-15 | 2013-10-15 14:17 | Calculated | TF2170 | TF2170 - Transformer Fuse: TF2170 |  | 128SEG1601 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 470 | 3 | 24499 | 1410 | 0.05755 | 0.00012245 | 25 | 11749 | 2013/2014 | October-2013 | 10 | 2013
29506 | Wind | 2013-10-15 07:22 | 2013-10-15 | 2013-10-15 10:01 | Calculated | 493 | 493 - Air Break Switch 493 |  | 123SEG493-466 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 175 | 24499 | 17104 | 0.69815 | 0.0071431 | 1825 | 161825 | 2013/2014 | October-2013 | 10 | 2013
29577 | Wind | 2013-10-15 07:23 | 2013-10-15 | 2013-10-15 08:13 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 26 | 24499 | 1300 | 0.05306 | 0.0010613 | 260 | 12999 | 2013/2014 | October-2013 | 10 | 2013
29507 | Wind | 2013-10-15 08:27 | 2013-10-15 | 2013-10-15 10:59 | Calculated | 5623 | 5623 - Electronic Sectionaliser 5623 |  | 409SEG5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 152 | 15 | 24499 | 2280 | 0.09307 | 0.00061227 | 72.5 | 11020 | 2013/2014 | October-2013 | 10 | 2013
29510 | Wind | 2013-10-15 08:37 | 2013-10-15 | 2013-10-15 11:47 | Calculated | 5378 | 5378 - Recloser 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 190 | 60 | 24499 | 11400 | 0.46533 | 0.0024491 | 383 | 72769 | 2013/2014 | October-2013 | 10 | 2013
29511 | Wind | 2013-10-15 08:41 | 2013-10-15 | 2013-10-15 12:14 | Calculated | 5485 | 5485 - Fused Link 5485 |  | 408SEG5485-5791 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 213 | 20 | 24499 | 4260 | 0.17388 | 0.00081636 | 160 | 34080 | 2013/2014 | October-2013 | 10 | 2013
29516 | Refer 2013 / 348 Replace X Arms | 2013-10-15 09:07 | 2013-10-15 | 2013-10-15 13:01 | Calculated | 1313 | 1313 - Fused Link 1313 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 234 | 27 | 24499 | 6318 | 0.25789 | 0.0011021 | 250 | 58499 | 2013/2014 | October-2013 | 10 | 2013
29513 | Wind | 2013-10-15 09:33 | 2013-10-15 | 2013-10-15 12:36 | Calculated | TF9K49 | TF9K49 - Transformer Fuse: TF9K49 |  | 409SEG5383-5922 | Southern 409-02 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 183 | 2 | 24499 | 366 | 0.01494 | 8.1636e-05 | 50 | 9150 | 2013/2014 | October-2013 | 10 | 2013
29509 | Wind | 2013-10-15 11:24 | 2013-10-15 | 2013-10-15 15:46 | Calculated | 5765 | 5765 - Fused Link 5765 |  | 403SEG5765-5653 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 262 | 6 | 24499 | 1572 | 0.06417 | 0.00024491 | 28 | 7336 | 2013/2014 | October-2013 | 10 | 2013
29526 | Wind | 2013-10-15 11:33 | 2013-10-15 | 2013-10-15 15:29 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 236 | 6 | 24499 | 1416 | 0.0578 | 0.00024491 | 95 | 22419 | 2013/2014 | October-2013 | 10 | 2013
29530 | Wind | 2013-10-15 11:33 | 2013-10-15 | 2013-10-16 13:52 | Calculated | 1519 | 1519 - Recloser 1519 |  | 113SEG1519-1541 | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1576 | 22 | 24499 | 20262 | 0.82705 | 0.000898 | 138 | 112688 | 2013/2014 | October-2013 | 10 | 2013
29534 | Wind | 2013-10-15 11:34 | 2013-10-15 | 2013-10-16 13:27 | Calculated | TF977 | TF977 - Transformer Fuse: TF977 |  | 120SEG481-422 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1548 | 5 | 24499 | 7740 | 0.31593 | 0.00020409 | 0 | 0 | 2013/2014 | October-2013 | 10 | 2013
29523 | Wind | 2013-10-15 11:49 | 2013-10-15 | 2013-10-15 13:42 | Calculated | TF693 | TF693 - Transformer Fuse: TF693 |  | 112SEG319 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 2 | 24499 | 226 | 0.00922 | 8.1636e-05 | 15 | 1695 | 2013/2014 | October-2013 | 10 | 2013
29522 | Wind | 2013-10-15 12:02 | 2013-10-15 | 2013-10-15 18:45 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 403 | 33 | 24499 | 9498 | 0.38769 | 0.001347 | 208.5 | 69934 | 2013/2014 | October-2013 | 10 | 2013
29512 | Wind - AUFLS | 2013-10-15 12:04 | 2013-10-15 | 2013-10-15 12:06 | Calculated | TPOngarue CB192 | TPOngarue CB192 - 33kV Minimum Oil Circuit Breaker TP192 |  | No Segment | 514-01 Transpower Ongarue | Rural D | No Feeder |  |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 4153 | 24499 | 5378 | 0.21952 | 0.16952 | 29494.7554 | 37325 | 2013/2014 | October-2013 | 10 | 2013
29525 | Wind | 2013-10-15 12:27 | 2013-10-15 | 2013-10-15 14:34 | Calculated | 179 | 179 - Fused Link 179 |  | 109SEG179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 20 | 24499 | 2540 | 0.10368 | 0.00081636 | 160 | 20319 | 2013/2014 | October-2013 | 10 | 2013
29515 | Wind | 2013-10-15 12:29 | 2013-10-15 | 2013-10-16 16:23 | Calculated | 380 | 380 - Air Break Switch 380 |  | 122SEG398-380 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1674 | 305 | 24499 | 24521 | 1.0009 | 0.012449 | 2853 | 229667 | 2013/2014 | October-2013 | 10 | 2013
29517 | Wind | 2013-10-15 12:32 | 2013-10-15 | 2013-10-15 17:41 | Calculated | 424 | 424 - Fused Link 424 |  | 121SEG424-799 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 282 | 156 | 24499 | 14374 | 0.58672 | 0.0063676 | 1721.5 | 132955 | 2013/2014 | October-2013 | 10 | 2013
29514 | Wind | 2013-10-15 12:33 | 2013-10-15 | 2013-10-22 18:17 | Calculated | 293 | 293 - Air Break Switch 293 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 330 | 59 | 24499 | 14840 | 0.60574 | 0.0024083 | 1008 | 125871 | 2013/2014 | October-2013 | 10 | 2013
29518 | Wind | 2013-10-15 12:45 | 2013-10-15 | 2013-10-15 17:48 | Calculated | 446 | 446 - Recloser 446 |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 303 | 175 | 24499 | 15285 | 0.6239 | 0.0071431 | 1825 | 157725 | 2013/2014 | October-2013 | 10 | 2013
29529 | Wind | 2013-10-15 13:32 | 2013-10-15 | 2013-10-15 16:33 | Calculated | 355 | 355 - Fused Link 355 |  | 112SEG355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 181 | 10 | 24499 | 1810 | 0.07388 | 0.00040818 | 105 | 19005 | 2013/2014 | October-2013 | 10 | 2013
29532 | Wind | 2013-10-15 13:38 | 2013-10-15 | 2013-10-15 18:43 | Calculated | 1639 | 1639 - Fused Link 1639 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 305 | 19 | 24499 | 5795 | 0.23654 | 0.00077554 | 122.5 | 37362 | 2013/2014 | October-2013 | 10 | 2013
29531 | Wind | 2013-10-15 13:51 | 2013-10-15 | 2013-10-16 00:47 | Calculated | 5892 | 5892 - Earth Working Link 5892 |  | 426SEG5892-5240 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 656 | 34 | 24499 | 22304 | 0.9104 | 0.0013878 | 182.5 | 119719 | 2013/2014 | October-2013 | 10 | 2013
29524 | Wind | 2013-10-15 14:52 | 2013-10-15 | 2013-10-17 18:16 | Calculated | TF7D24 | TF7D24 - Transformer Fuse: TF7D24 |  | 413SEG6543-5996 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 420 | 28 | 24499 | 11760 | 0.48002 | 0.0011429 | 500 | 209999 | 2013/2014 | October-2013 | 10 | 2013
29527 | Wind | 2013-10-15 15:35 | 2013-10-15 | 2013-10-15 16:06 | Calculated | 188 | 188 - Fused Link 188 |  | 109SEG188 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 2 | 24499 | 62 | 0.00253 | 8.1636e-05 | 40 | 1240 | 2013/2014 | October-2013 | 10 | 2013
29540 | Wind | 2013-10-15 16:39 | 2013-10-15 | 2013-10-15 22:10 | Calculated | 5768 | 5768 - Recloser with Bypass 5768 |  | 408SEG5384-5116 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 331 | 69 | 24499 | 17599 | 0.71836 | 0.0028164 | 391 | 91430 | 2013/2014 | October-2013 | 10 | 2013
29537 | Wind | 2013-10-15 17:52 | 2013-10-15 | 2013-10-15 18:56 | Calculated | T2702 | T2702 - 3 Phase : 50.00 kVA : POLEMNT |  | 120SEG632 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 5 | 24499 | 320 | 0.01306 | 0.00020409 | 115 | 7360 | 2013/2014 | October-2013 | 10 | 2013
29535 | Wind | 2013-10-15 17:55 | 2013-10-15 | 2013-10-15 18:38 | Calculated | 364 | 364 - Fused Link 364 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 31 | 24499 | 1333 | 0.05441 | 0.0012654 | 260 | 11179 | 2013/2014 | October-2013 | 10 | 2013
29539 | Faulty DDO | 2013-10-15 18:08 | 2013-10-15 | 2013-10-15 21:05 | Calculated | TF539 | TF539 - Transformer Fuse: TF539 |  | 125SEG268-281 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 1 | 24499 | 177 | 0.00722 | 4.0818e-05 | 10 | 1770 | 2013/2014 | October-2013 | 10 | 2013
29508 | Wind | 2013-10-15 18:47 | 2013-10-15 | 2013-10-15 20:15 | Calculated | 5623 | 5623 - Electronic Sectionaliser 5623 |  | 409SEG5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 15 | 24499 | 1320 | 0.05388 | 0.00061227 | 72.5 | 6380 | 2013/2014 | October-2013 | 10 | 2013
29538 | Wind | 2013-10-15 19:00 | 2013-10-15 | 2013-10-15 19:51 | Calculated | 648 | 648 - fused link : 648 |  | 111SEG648 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 9 | 24499 | 459 | 0.01874 | 0.00036736 | 70 | 3569 | 2013/2014 | October-2013 | 10 | 2013
29543 | Wind | 2013-10-15 20:15 | 2013-10-15 | 2013-10-15 23:30 | Calculated | TF1683 | TF1683 - Transformer Fuse: TF1683 |  | 116SEG1354-1334 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 195 | 4 | 24499 | 780 | 0.03184 | 0.00016327 | 30 | 5850 | 2013/2014 | October-2013 | 10 | 2013
29551 | Wind | 2013-10-15 20:52 | 2013-10-15 | 2013-10-16 18:42 | Calculated | 5935 | 5935 - Fused Link 5935 |  | 408SEG5935-5936 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1304 | 69 | 24499 | 4847 | 0.19784 | 0.0028164 | 391 | 35190 | 2013/2014 | October-2013 | 10 | 2013
29542 | Wind | 2013-10-15 21:03 | 2013-10-15 | 2013-10-15 21:21 | Calculated | 1639 | 1639 - Fused Link 1639 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 18 | 19 | 24499 | 342 | 0.01396 | 0.00077554 | 122.5 | 2205 | 2013/2014 | October-2013 | 10 | 2013
29536 | Wind | 2013-10-16 04:54 | 2013-10-16 | 2013-10-16 06:22 | Calculated | 458 | 458 - Fused Link 458 |  | 129SEG458 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 7 | 24499 | 616 | 0.02514 | 0.00028573 | 80 | 7040 | 2013/2014 | October-2013 | 10 | 2013
29533 | Unknown | 2013-10-16 05:49 | 2013-10-16 | 2013-10-16 05:56 | Calculated | 687 | 687 - Circuit Breaker 687 |  | 117SEG687-1289 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 227 | 24499 | 1589 | 0.06486 | 0.0092657 | 1884.5 | 13191 | 2013/2014 | October-2013 | 10 | 2013
29544 | Wind | 2013-10-16 06:20 | 2013-10-16 | 2013-10-16 07:27 | Calculated | TF1133 | TF1133 - Transformer Fuse: TF1133 |  | 120SEG485-413 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 2 | 24499 | 134 | 0.00547 | 8.1636e-05 | 15 | 1005 | 2013/2014 | October-2013 | 10 | 2013
29545 | Wind | 2013-10-16 07:09 | 2013-10-16 | 2013-10-16 08:05 | Calculated | TF2326 | TF2326 - Transformer Fuse: TF2326 |  | 111SEG551 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 2 | 24499 | 112 | 0.00457 | 8.1636e-05 | 15 | 840 | 2013/2014 | October-2013 | 10 | 2013
29547 | Wind | 2013-10-16 09:02 | 2013-10-16 | 2013-10-16 11:09 | Calculated | TF2109 | TF2109 - Transformer Fuse: TF2109 |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 127 | 1 | 24499 | 127 | 0.00518 | 4.0818e-05 | 10 | 1270 | 2013/2014 | October-2013 | 10 | 2013
29546 | Broken Xarm | 2013-10-16 09:39 | 2013-10-16 | 2013-10-16 13:00 | Calculated | TF1821 | TF1821 - Transformer Fuse: TF1821 |  | 103SEG641-1350 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 201 | 3 | 24499 | 603 | 0.02461 | 0.00012245 | 10 | 2009 | 2013/2014 | October-2013 | 10 | 2013
29548 | Wind | 2013-10-16 10:19 | 2013-10-16 | 2013-10-16 12:10 | Calculated | TF7C1 | TF7C1 - Transformer Fuse: TF7C1 |  | 413SEG5420-5305 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 111 | 1 | 24499 | 111 | 0.00453 | 4.0818e-05 | 15 | 1665 | 2013/2014 | October-2013 | 10 | 2013
29549 | Wind | 2013-10-16 12:05 | 2013-10-16 | 2013-10-16 13:45 | Calculated | 471 | 471 - Fused Link 471 |  | 123SEG471 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 10 | 24499 | 1000 | 0.04082 | 0.00040818 | 85 | 8500 | 2013/2014 | October-2013 | 10 | 2013
29550 | L/V Line Down | 2013-10-16 15:25 | 2013-10-16 | 2013-10-16 16:22 | Calculated | TF635 | TF635 - Transformer Fuse: TF635 |  | 104SEG730-547 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 2 | 24499 | 114 | 0.00465 | 8.1636e-05 | 5 | 285 | 2013/2014 | October-2013 | 10 | 2013
29552 | Broken Xarm | 2013-10-17 07:05 | 2013-10-17 | 2013-10-17 18:03 | Calculated | TF4H4 | TF4H4 - Transformer Fuse: TF4H4 |  | 421SEG6640-5462 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 658 | 1 | 24499 | 658 | 0.02686 | 4.0818e-05 | 5 | 3290 | 2013/2014 | October-2013 | 10 | 2013
29553 | Refer 2013 / 349 Replace Poles & X Arms | 2013-10-17 09:35 | 2013-10-17 | 2013-10-17 14:36 | Calculated | 239 | 239 - Fused Link 239 |  | 107SEG239-508 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 301 | 35 | 24499 | 10535 | 0.43002 | 0.0014286 | 205 | 61704 | 2013/2014 | October-2013 | 10 | 2013
29554 | Broken Xarm | 2013-10-17 14:58 | 2013-10-17 | 2013-10-17 16:59 | Calculated | 5126 | 5126 - Air Break Switch 5126 |  | 407SEG5126-5850 | Manunui 407-01 (was Affco) | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 4 | 24499 | 484 | 0.01976 | 0.00016327 | 565 | 68365 | 2013/2014 | October-2013 | 10 | 2013
29556 | Blown HV Fuse - Unknown Fault | 2013-10-17 16:16 | 2013-10-17 | 2013-10-17 17:45 | Calculated | TF10K16 | TF10K16 - Transformer Fuse: TF10K16 |  | 409SEG5904-6206 | Southern 409-04 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 23 | 24499 | 2047 | 0.08355 | 0.00093881 | 100 | 8899 | 2013/2014 | October-2013 | 10 | 2013
29555 | Removed Genset | 2013-10-17 17:10 | 2013-10-17 | 2013-10-17 18:16 | Calculated | TF7D24 | TF7D24 - Transformer Fuse: TF7D24 |  | 413SEG6543-5996 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 28 | 24499 | 1848 | 0.07543 | 0.0011429 | 500 | 32999 | 2013/2014 | October-2013 | 10 | 2013
29558 | Faulty DDO | 2013-10-17 19:40 | 2013-10-17 | 2013-10-17 22:53 | Calculated | 5959 | 5959 - Air Break Switch 5959 |  | 406SEG5959-5899 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 187 | 313 | 24499 | 52511 | 2.1434 | 0.012776 | 1545 | 253224 | 2013/2014 | October-2013 | 10 | 2013
29557 | Line Down | 2013-10-17 20:12 | 2013-10-17 | 2013-10-18 09:55 | Calculated | 453 | 453 - Air Break Switch 453 |  | 103SEG709-453 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 818 | 59 | 24499 | 25127 | 1.0256 | 0.0024083 | 1008 | 255484 | 2013/2014 | October-2013 | 10 | 2013
29559 | Unknown | 2013-10-18 09:58 | 2013-10-18 | 2013-10-18 10:52 | Calculated | 109 | 109 - Recloser with bypass 109 |  | 101SEG110-109 | Caves 101-09 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 98 | 24499 | 5292 | 0.21601 | 0.0040002 | 791 | 42714 | 2013/2014 | October-2013 | 10 | 2013
29560 | Refer 2013 / 1155 | 2013-10-18 10:39 | 2013-10-18 | 2013-10-18 11:22 | Calculated | 562 | 562 - Fused Link 562 |  | 122SEG562 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 43 | 13 | 24499 | 559 | 0.02282 | 0.00053063 | 200 | 8600 | 2013/2014 | October-2013 | 10 | 2013
29561 | Broken Xarm | 2013-10-18 11:36 | 2013-10-18 | 2013-10-18 16:33 | Calculated | 5850 | 5850 - Air Break Switch 5850 |  | 407SEG5850-5838 | Manunui 407-01 (was Affco) | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 297 | 4 | 24499 | 1172 | 0.04784 | 0.00016327 | 565 | 167685 | 2013/2014 | October-2013 | 10 | 2013
29564 | Blown HV Fuse - Unknown Fault | 2013-10-18 11:49 | 2013-10-18 | 2013-10-18 13:49 | Calculated | TF2080 | TF2080 - Transformer Fuse: TF2080 |  | 117SEG2179 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 120 | 2 | 24499 | 240 | 0.0098 | 8.1636e-05 | 15 | 1800 | 2013/2014 | October-2013 | 10 | 2013
29562 | L/V Line Down | 2013-10-18 13:00 | 2013-10-18 | 2013-10-18 14:01 | Calculated | TF727 | TF727 - Transformer Fuse: TF727 |  | 120SEG485-413 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 3 | 24499 | 183 | 0.00747 | 0.00012245 | 25 | 1524 | 2013/2014 | October-2013 | 10 | 2013
29563 | Broken Earth Wire | 2013-10-18 13:18 | 2013-10-18 | 2013-10-18 14:36 | Calculated | TF3R2 | TF3R2 - Transformer Fuse: TF3R2 |  | 124SEG5536 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 2 | 24499 | 156 | 0.00637 | 8.1636e-05 | 15 | 1170 | 2013/2014 | October-2013 | 10 | 2013
29565 | Refer 2013 / 7904 | 2013-10-18 13:47 | 2013-10-18 | 2013-10-18 14:35 | Calculated | TF3284 | TF3284 - Transformer Fuse: T3284 |  | 122SEG807 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 48 | 1 | 24499 | 48 | 0.00196 | 4.0818e-05 | 75 | 3600 | 2013/2014 | October-2013 | 10 | 2013
29567 | Blown due to old age | 2013-10-19 12:07 | 2013-10-19 | 2013-10-19 14:23 | Calculated | TF17K08 | TF17K08 - Transformer Fuse: TF17K08 |  | 411SEG5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 2 | 24499 | 272 | 0.0111 | 8.1636e-05 | 15 | 2040 | 2013/2014 | October-2013 | 10 | 2013
29566 | Excavator v LV Line | 2013-10-19 12:19 | 2013-10-19 | 2013-10-19 13:39 | Calculated | TF809 | TF809 - Transformer Fuse: TF809 |  | 119SEG423-432 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 2 | 24499 | 160 | 0.00653 | 8.1636e-05 | 15 | 1200 | 2013/2014 | October-2013 | 10 | 2013
29568 | Over Current | 2013-10-20 06:54 | 2013-10-20 | 2013-10-20 06:57 | Calculated | TPTokaanu CB1062 | TPTokaanu CB1062 - 33kV Minimum Oil Circuit Breaker TP1062 |  | No Segment | 515-01 Transpower Tokaanu | Rural D | No Feeder |  |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 1956 | 24499 | 5868 | 0.23952 | 0.07984 | 13908.0303 | 41724 | 2013/2014 | October-2013 | 10 | 2013
29569 | Blown HV Fuse - Unknown Fault | 2013-10-20 09:26 | 2013-10-20 | 2013-10-20 10:59 | Calculated | TF2109 | TF2109 - Transformer Fuse: TF2109 |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 93 | 1 | 24499 | 93 | 0.0038 | 4.0818e-05 | 10 | 930 | 2013/2014 | October-2013 | 10 | 2013
29570 | L/V Fault | 2013-10-20 12:24 | 2013-10-20 | 2013-10-20 16:01 | Calculated | TF5F8 | TF5F8 - Transformer Fuse: TF5F8 |  | 422SEG5270-5269 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 217 | 3 | 24499 | 651 | 0.02657 | 0.00012245 | 15 | 3255 | 2013/2014 | October-2013 | 10 | 2013
29571 | Trees | 2013-10-20 20:05 | 2013-10-20 | 2013-10-20 21:15 | Calculated | 1.27 | 1.27 - Fused Link 1.27 |  | 404SEGF1.27 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 6 | 24499 | 420 | 0.01714 | 0.00024491 | 25 | 1750 | 2013/2014 | October-2013 | 10 | 2013
29572 | Refer 2013 / 357 Replace Poles 1090239 + 1090238 | 2013-10-21 09:30 | 2013-10-21 | 2013-10-21 13:58 | Calculated | 170 | 170 - Electronic Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 268 | 21 | 24499 | 5628 | 0.22972 | 0.00085718 | 178 | 47704 | 2013/2014 | October-2013 | 10 | 2013
29573 | L/V fault | 2013-10-21 11:42 | 2013-10-21 | 2013-10-21 15:13 | Calculated | TF355 | TF355 - Transformer Fuse: TF355 |  | 112SEG774 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 211 | 1 | 24499 | 211 | 0.00861 | 4.0818e-05 | 15 | 3165 | 2013/2014 | October-2013 | 10 | 2013
29574 | Lightning | 2013-10-21 12:32 | 2013-10-21 | 2013-10-21 16:30 | Calculated | TF6J3 | TF6J3 - Transformer Fuse: TF6J3 |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24499 |  | 0 | 0 |  |  | 2013/2014 | October-2013 | 10 | 2013
29575 | Lightning | 2013-10-21 12:32 | 2013-10-21 | 2013-10-21 17:10 | Calculated | TF16J01 | TF16J01 - Transformer Fuse: TF16J01 |  | 410SEG5631 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 278 | 2 | 24499 | 556 | 0.02269 | 8.1636e-05 | 3 | 834 | 2013/2014 | October-2013 | 10 | 2013
29576 | Lightning | 2013-10-21 16:14 | 2013-10-21 | 2013-10-21 18:10 | Calculated | TF1617 | TF1617 - Transformer Fuse: TF1617 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 1 | 24499 | 116 | 0.00473 | 4.0818e-05 | 10 | 1160 | 2013/2014 | October-2013 | 10 | 2013
29578 | Unknown | 2013-10-22 07:12 | 2013-10-22 | 2013-10-22 07:39 | Calculated | 5107 | 5107 - Recloser with Bypass & Links 5107 |  | 422SEG05F14-5107 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 27 | 61 | 24499 | 1647 | 0.06723 | 0.0024899 | 439 | 11853 | 2013/2014 | October-2013 | 10 | 2013
29579 | Refer 2013 / 355 Replace Pole Structure 68 Including Links 5294 | 2013-10-22 08:05 | 2013-10-22 | 2013-10-22 15:44 | Calculated | 5308 | 5308 - Fused Link 5308 |  | 413SEG5308-5794 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 459 | 121 | 24499 | 27167 | 1.1089 | 0.004939 | 941 | 200198 | 2013/2014 | October-2013 | 10 | 2013
29582 | Private Line Down / Customer Unavailable | 2013-10-22 08:34 | 2013-10-22 | 2013-10-24 17:17 | Calculated | 5578 | 5578 - Fused Link 5578 |  | 422SEG5278-5307 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFPL | Fault on Private Line - Affecting Network | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 3403 | 18 | 24499 | 14451 | 0.58986 | 0.00073472 | 126 | 74699 | 2013/2014 | October-2013 | 10 | 2013
29580 | Refer 2013 / 358 Replace Poles & X Arms | 2013-10-22 09:33 | 2013-10-22 | 2013-10-22 10:15 | Calculated | 575 | 575 - Fused Link 575 |  | 107SEG575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 13 | 24499 | 546 | 0.02229 | 0.00053063 | 150 | 6299 | 2013/2014 | October-2013 | 10 | 2013
29581 | L/V Fault | 2013-10-22 10:01 | 2013-10-22 | 2013-10-22 10:55 | Calculated | TF9R37 | TF9R37 - Transformer Fuse: TF9R37 |  | 406SEG6021 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 6 | 24499 | 324 | 0.01323 | 0.00024491 | 15 | 810 | 2013/2014 | October-2013 | 10 | 2013
29583 | L/V Fault | 2013-10-22 11:19 | 2013-10-22 | 2013-10-22 12:14 | Calculated | TF693 | TF693 - Transformer Fuse: TF693 |  | 112SEG319 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 2 | 24499 | 110 | 0.00449 | 8.1636e-05 | 15 | 825 | 2013/2014 | October-2013 | 10 | 2013
29584 | Change Taps | 2013-10-22 11:20 | 2013-10-22 | 2013-10-22 12:30 | Calculated | TF9R28 | TF9R28 - Transformer Fuse: TF9R28 |  | 406SEG5896 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 70 | 3 | 24499 | 210 | 0.00857 | 0.00012245 | 200 | 13999 | 2013/2014 | October-2013 | 10 | 2013
29585 | Wind | 2013-10-22 15:30 | 2013-10-22 | 2013-10-22 16:39 | Calculated | TF1530 | TF1530 - Transformer Fuse: TF1530 |  | 101SEG290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 1 | 24499 | 69 | 0.00282 | 4.0818e-05 | 5 | 345 | 2013/2014 | October-2013 | 10 | 2013
29586 | Refer 2013 / 352 Replace Poles | 2013-10-23 08:33 | 2013-10-23 | 2013-10-23 15:58 | Calculated | 5602 | 5602 - Fused Link 5602 |  | 403SEG5602-5317 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 445 | 11 | 24499 | 4895 | 0.1998 | 0.000449 | 95 | 42274 | 2013/2014 | October-2013 | 10 | 2013
29587 | L/V Repairs | 2013-10-23 09:20 | 2013-10-23 | 2013-10-23 11:38 | Calculated | TF1461 | TF1461 - Transformer Fuse: TF1461 |  | 107SEG508-1798 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 138 | 2 | 24499 | 276 | 0.01127 | 8.1636e-05 | 10 | 1380 | 2013/2014 | October-2013 | 10 | 2013
29588 | Blown HV Fuse - Unknown Fault | 2013-10-24 07:27 | 2013-10-24 | 2013-10-24 08:42 | Calculated | TF673 | TF673 - Transformer Fuse: TF673 |  | 107SEG250-254 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 3 | 24499 | 225 | 0.00918 | 0.00012245 | 30 | 2250 | 2013/2014 | October-2013 | 10 | 2013
29589 | Upgrade Tx | 2013-10-24 09:42 | 2013-10-24 | 2013-10-24 11:04 | Calculated | TF786 | TF786 - Transformer Fuse: TF786 |  | 121SEG487-531 | Huirimu 121-04 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 82 | 3 | 24499 | 246 | 0.01004 | 0.00012245 | 15 | 1230 | 2013/2014 | October-2013 | 10 | 2013
29590 | Refer 2013 / 354 Pole Replacement Western Feeder | 2013-10-25 09:03 | 2013-10-25 | 2013-10-25 12:19 | Calculated | 5322 | 5322 - Fused Link 5322 |  | 403SEG5322-5738 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 153 | 18 | 24499 | 1055 | 0.04306 | 0.00073472 | 110 | 6755 | 2013/2014 | October-2013 | 10 | 2013
29592 | L/V Fault | 2013-10-25 13:48 | 2013-10-25 | 2013-10-25 15:25 | Calculated | TF8G8 | TF8G8 - Transformer Fuse: TF8G8 |  | 403SEG5316-5622 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 97 | 2 | 24499 | 194 | 0.00792 | 8.1636e-05 | 15 | 1455 | 2013/2014 | October-2013 | 10 | 2013
29593 | O/C Tractors Working Under Lines | 2013-10-26 16:23 | 2013-10-26 | 2013-10-26 16:59 | Calculated | 570 | 570 - Circuit Breaker 570 |  | 303SEG162-164 | Te Waireka Road 303-01 | Urban A | Te Waireka Rd 33 | Direct from Hangatiki Supply |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 33 | 3024 | 24499 | 93942 | 3.8345 | 0.12343 | 26939 | 837078 | 2013/2014 | October-2013 | 10 | 2013
29594 | Line Down | 2013-10-26 21:43 | 2013-10-26 | 2013-10-27 01:31 | Calculated | 101 | 101 - Circuit Breaker Benneydale 101 |  | No Segment | 206-01 Waitete | Urban A | No Feeder |  |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 351 | 24499 | 1600 | 0.06531 | 0.014327 | 6304.5 | 190697 | 2013/2014 | October-2013 | 10 | 2013
29595 | Blown HV Fuse - Unknown Fault | 2013-10-27 08:49 | 2013-10-27 | 2013-10-27 09:20 | Calculated | TF3140 | TF3140 - Transformer Fuse: TF3140 |  | 103SEG200-225 | Benneydale 103-01 | Urban A | Benneydale | Waitete Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24499 |  | 0 | 0 |  |  | 2013/2014 | October-2013 | 10 | 2013
29596 | Unknown | 2013-10-27 09:37 | 2013-10-27 | 2013-10-27 10:56 | Calculated | 1126 | 1126 - Recloser with Bypass & Links 1126 |  | 114SEG1126-1127 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 79 | 30 | 24499 | 3423 | 0.13972 | 0.0012245 | 215 | 24274 | 2013/2014 | October-2013 | 10 | 2013
29597 | LV Fault | 2013-10-27 20:27 | 2013-10-27 | 2013-10-27 22:27 | Calculated | TF223 | TF223 - Transformer Fuse: TF223 |  | 112SEG316-637 | Otorohanga 112-07 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 5 | 24499 | 600 | 0.02449 | 0.00020409 | 30 | 3600 | 2013/2014 | October-2013 | 10 | 2013
29598 | Trees | 2013-10-28 10:08 | 2013-10-28 | 2013-10-28 11:11 | Calculated | 620 | 620 - Fused Link 620 |  | 109SEG620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 8 | 24499 | 504 | 0.02057 | 0.00032654 | 75 | 4725 | 2013/2014 | October-2013 | 10 | 2013
29599 | Birds | 2013-10-28 11:50 | 2013-10-28 | 2013-10-28 15:38 | Calculated | 07A08 | 07A08 - 1 Phase : 15.00 kVA : POLEMNT |  | 413SEG5560-5734 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 228 | 38 | 24499 | 4077 | 0.16641 | 0.0015511 | 218 | 23919 | 2013/2014 | October-2013 | 10 | 2013
29600 | Refer 2013 / TG 865 | 2013-10-29 09:59 | 2013-10-29 | 2013-10-29 16:02 | Calculated | TF369 | TF369 - Transformer Fuse: TF369 |  | 109SEG119-2107 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 363 | 4 | 24499 | 1452 | 0.05927 | 0.00016327 | 30 | 10890 | 2013/2014 | October-2013 | 10 | 2013
29601 | Refer 2013 / 365 FReplace Pole 1111344 | 2013-10-29 10:05 | 2013-10-29 | 2013-10-29 13:10 | Calculated | 648 | 648 - fused link : 648 |  | 111SEG648 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 185 | 9 | 24499 | 1665 | 0.06796 | 0.00036736 | 70 | 12949 | 2013/2014 | October-2013 | 10 | 2013
29602 | Faulty DDO | 2013-10-29 13:37 | 2013-10-29 | 2013-10-29 15:17 | Calculated | TF2109 | TF2109 - Transformer Fuse: TF2109 |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 100 | 1 | 24499 | 100 | 0.00408 | 4.0818e-05 | 10 | 1000 | 2013/2014 | October-2013 | 10 | 2013
29603 | Blown fuse due to Magpie | 2013-10-29 13:57 | 2013-10-29 | 2013-10-29 15:59 | Calculated | TF10E06 | TF10E06 - Transformer Fuse: TF10E06 |  | 413SEG5647-5646 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 122 | 4 | 24499 | 488 | 0.01992 | 0.00016327 | 15 | 1830 | 2013/2014 | October-2013 | 10 | 2013
29604 | Change Taps | 2013-10-29 18:27 | 2013-10-29 | 2013-10-29 18:55 | Calculated | TF369 | TF369 - Transformer Fuse: TF369 |  | 109SEG119-2107 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLS | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 4 | 24499 | 112 | 0.00457 | 0.00016327 | 30 | 840 | 2013/2014 | October-2013 | 10 | 2013
29606 | Change Taps | 2013-10-30 06:07 | 2013-10-30 | 2013-10-30 08:20 | Calculated | TF295 | TF295 - Transformer Fuse: TF295 |  | 122SEG618-367 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLS | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 5 | 24499 | 665 | 0.02714 | 0.00020409 | 25 | 3325 | 2013/2014 | October-2013 | 10 | 2013
29607 | L/V Faults | 2013-10-30 09:18 | 2013-10-30 | 2013-10-30 14:14 | Calculated | TF1679 | TF1679 - Transformer Fuse: TF1679 |  | 116SEG1341-1354 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 296 | 45 | 24499 | 13320 | 0.5437 | 0.0018368 | 200 | 59199 | 2013/2014 | October-2013 | 10 | 2013
29608 | Blown HV Fuse - Unknown Fault | 2013-10-30 10:01 | 2013-10-30 | 2013-10-30 14:59 | Calculated | TF1823 | TF1823 - Transformer Fuse: TF1823 |  | 103SEG1335-1301 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 298 | 1 | 24499 | 298 | 0.01216 | 4.0818e-05 | 10 | 2980 | 2013/2014 | October-2013 | 10 | 2013
29609 | Jumper Off | 2013-10-30 22:26 | 2013-10-30 | 2013-10-31 01:38 | Calculated | TF2186 | TF2186 - Transformer Fuse: TF2186 |  | 128SEG2095-1635 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 192 | 153 | 24499 | 7926 | 0.32352 | 0.0062452 | 1053.5 | 53051 | 2013/2014 | October-2013 | 10 | 2013
29610 | Refer 2013 / 362A Install 11Kv Pole & Cables For Tawhai Sub Upgrade & 33/11 Transformer Removal Tx 513T1 - Replace Poles 72 & 73 Kuratau/Nat Park 33Kv | 2013-10-31 08:31 | 2013-10-31 | 2013-10-31 16:36 | Calculated | 6631 | 6631 - Load Break Switch 6631 |  | 419SEG6630-6631 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 481 | 151 | 24499 | 47703 | 1.9471 | 0.0061635 | 12280 | 5091749 | 2013/2014 | October-2013 | 10 | 2013
29611 | Northpower - Rebuild Tx Structure | 2013-10-31 09:13 | 2013-10-31 | 2013-10-31 12:39 | Calculated | TF2715 | TF2715 - Transformer Fuse: TF2715 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 206 | 4 | 24499 | 824 | 0.03363 | 0.00016327 | 45 | 9270 | 2013/2014 | October-2013 | 10 | 2013
29612 | Refer 2013 / 366 Replace Poles & X Arms | 2013-10-31 09:34 | 2013-10-31 | 2013-10-31 14:05 | Calculated | 244 | 244 - Air Break Switch 244 |  | 107SEG244-575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 271 | 41 | 24499 | 11111 | 0.45353 | 0.0016735 | 435 | 117884 | 2013/2014 | October-2013 | 10 | 2013
29614 | L/V Fault | 2013-10-31 12:02 | 2013-10-31 | 2013-10-31 12:43 | Calculated | TF8M1 | TF8M1 - Transformer Fuse: TF8M1 |  | 408SEG5379-5654 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 41 | 4 | 24499 | 164 | 0.00669 | 0.00016327 | 15 | 615 | 2013/2014 | October-2013 | 10 | 2013
29619 | Blown HV Fuse - Unknown Fault | 2013-10-31 15:32 | 2013-10-31 | 2013-11-01 14:02 | Calculated | TF1824 | TF1824 - Transformer Fuse: TF1824 |  | 103SEG1335-1301 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1350 | 1 | 24499 | 1350 | 0.0551 | 4.0818e-05 | 10 | 13500 | 2013/2014 | October-2013 | 10 | 2013
29615 | Wind | 2013-11-01 07:26 | 2013-11-01 | 2013-11-01 08:18 | Calculated | 5485 | 5485 - Fused Link 5485 |  | 408SEG5485-5791 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 20 | 24552 | 1040 | 0.04236 | 0.0008146 | 160 | 8320 | 2013/2014 | November-2013 | 11 | 2013
29616 | Refer 2013/11113 Northpower | 2013-11-01 09:18 | 2013-11-01 | 2013-11-01 11:57 | Calculated | TF1668 | TF1668 - Transformer Fuse: TF1668 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 159 | 2 | 24552 | 318 | 0.01295 | 8.146e-05 | 10 | 1590 | 2013/2014 | November-2013 | 11 | 2013
29617 | Refer 2013/367 Replace Poles & X Arms | 2013-11-01 09:31 | 2013-11-01 | 2013-11-01 14:39 | Calculated | 239 | 239 - Fused Link 239 |  | 107SEG239-508 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 308 | 35 | 24552 | 10780 | 0.43907 | 0.0014255 | 205 | 63139 | 2013/2014 | November-2013 | 11 | 2013
29618 | L/V Fault | 2013-11-01 12:51 | 2013-11-01 | 2013-11-01 16:28 | Calculated | TF996 | TF996 - Transformer Fuse: TF996 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 4 | 24552 | 868 | 0.03535 | 0.00016292 | 25 | 5425 | 2013/2014 | November-2013 | 11 | 2013
29620 | Birds | 2013-11-02 07:50 | 2013-11-02 | 2013-11-02 09:47 | Calculated | TF7R3 | TF7R3 - Transformer Fuse: TF7R3 |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 3 | 24552 | 351 | 0.0143 | 0.00012219 | 10 | 1169 | 2013/2014 | November-2013 | 11 | 2013
29621 | Birds | 2013-11-02 09:04 | 2013-11-02 | 2013-11-02 10:23 | Calculated | TF9L6 | TF9L6 - Transformer Fuse: TF9L6 |  | 408SEG5406 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 79 | 5 | 24552 | 395 | 0.01609 | 0.00020365 | 10 | 790 | 2013/2014 | November-2013 | 11 | 2013
29623 | Faulty DDO | 2013-11-02 09:33 | 2013-11-02 | 2013-11-02 13:05 | Calculated | TF6E12 | TF6E12 - Transformer Fuse: TF6E12 |  | 412SEG5256-5445 | Nihoniho 412-01 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 212 | 2 | 24552 | 424 | 0.01727 | 8.146e-05 | 5 | 1060 | 2013/2014 | November-2013 | 11 | 2013
29622 | Birds | 2013-11-02 11:08 | 2013-11-02 | 2013-11-02 12:03 | Calculated | TO5I9 | TO5I9 - Tap-off Fuse TO5I9 |  | 402SEG5798 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 55 | 2 | 24552 | 110 | 0.00448 | 8.146e-05 | 10 | 550 | 2013/2014 | November-2013 | 11 | 2013
29624 | Refer 2013/371 Urgent Replacement of Suspect Tension Sleeves Outside UBP | 2013-11-03 08:08 | 2013-11-03 | 2013-11-03 10:47 | Calculated | 225 | 225 - Air Break Switch 225 |  | 103SEG200-225 | Benneydale 103-01 | Urban A | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 77 | 3 | 24552 | 231 | 0.00941 | 0.00012219 | 850 | 65450 | 2013/2014 | November-2013 | 11 | 2013
29625 | Faulty DDO | 2013-11-03 18:36 | 2013-11-03 | 2013-11-03 19:28 | Calculated | TF1509 | TF1509 - Transformer Fuse: TF1509 |  | 112SEG316-637 | Otorohanga 112-07 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 2 | 24552 | 104 | 0.00424 | 8.146e-05 | 25 | 1300 | 2013/2014 | November-2013 | 11 | 2013
29626 | Blown HV Fuse - Unknown Fault | 2013-11-04 08:14 | 2013-11-04 | 2013-11-04 11:01 | Calculated | TF7J23 | TF7J23 - Transformer Fuse: TF7J23 |  | 402SEG5596-5930 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 167 | 1 | 24552 | 167 | 0.0068 | 4.073e-05 | 15 | 2505 | 2013/2014 | November-2013 | 11 | 2013
29634 | L/V Fault | 2013-11-04 12:07 | 2013-11-04 | 2013-11-04 12:54 | Calculated | TF11H01 | TF11H01 - Transformer Fuse: TF11H01 |  | 403SEG5765-5653 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 47 | 2 | 24552 | 94 | 0.00383 | 8.146e-05 | 10 | 470 | 2013/2014 | November-2013 | 11 | 2013
29637 | Faulty DDO | 2013-11-04 16:37 | 2013-11-04 | 2013-11-05 14:25 | Calculated | TF2210 | TF2210 - Transformer Fuse: TF2210 |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1308 | 2 | 24552 | 2616 | 0.10655 | 8.146e-05 | 15 | 19620 | 2013/2014 | November-2013 | 11 | 2013
29635 | Unknown | 2013-11-05 09:11 | 2013-11-05 | 2013-11-05 10:40 | Calculated | 575 | 575 - Fused Link 575 |  | 107SEG575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 13 | 24552 | 1157 | 0.04712 | 0.00052949 | 150 | 13349 | 2013/2014 | November-2013 | 11 | 2013
29636 | Unknown | 2013-11-05 09:11 | 2013-11-05 | 2013-11-05 10:58 | Calculated | TF53 | TF53 - Transformer Fuse: TF53 |  | 107SEG575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 2 | 24552 | 214 | 0.00872 | 8.146e-05 | 30 | 3210 | 2013/2014 | November-2013 | 11 | 2013
29528 | Refer 2013/364 Replace Poles 1191091, 1191093 - Replace X Arms On Pole 1191087 | 2013-11-05 09:30 | 2013-11-05 | 2013-11-05 14:26 | Calculated | 409 | 409 - Air Break Switch 409 |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 3 | 24552 | 846 | 0.03446 | 0.00012219 | 110 | 31020 | 2013/2014 | November-2013 | 11 | 2013
29638 | Refer 2013/381 Repair DDOs 397 & 705 Live Line & Move poles Due to Flooding | 2013-11-06 09:21 | 2013-11-06 | 2013-11-06 14:19 | Calculated | 5397 | 5397 - Fused Link 5397 |  | 415SEG5397-5670 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 298 | 19 | 24552 | 5165 | 0.21037 | 0.00077387 | 125 | 33344 | 2013/2014 | November-2013 | 11 | 2013
29639 | Change Tx | 2013-11-06 09:40 | 2013-11-06 | 2013-11-06 12:15 | Calculated | TF588 | TF588 - Transformer Fuse: TF588 |  | 110SEG2164 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 155 | 2 | 24552 | 310 | 0.01263 | 8.146e-05 | 15 | 2325 | 2013/2014 | November-2013 | 11 | 2013
29642 | Birds | 2013-11-06 13:54 | 2013-11-06 | 2013-11-06 15:12 | Calculated | TF5I1 | TF5I1 - Transformer Fuse: TF5I1 |  | 402SEG5797-5777 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 78 | 1 | 24552 | 78 | 0.00318 | 4.073e-05 | 7.5 | 585 | 2013/2014 | November-2013 | 11 | 2013
29641 | Lightning | 2013-11-06 14:06 | 2013-11-06 | 2013-11-06 15:27 | Calculated | TF708 | TF708 - Transformer Fuse: TF708 |  | 118SEG588 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 2 | 24552 | 162 | 0.0066 | 8.146e-05 | 25 | 2025 | 2013/2014 | November-2013 | 11 | 2013
29645 | Lightning | 2013-11-06 14:06 | 2013-11-06 | 2013-11-06 14:55 | Calculated | TF797 | TF797 - Transformer Fuse: TF797 |  | 120SEG497-REG31 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 2 | 24552 | 98 | 0.00399 | 8.146e-05 | 25 | 1225 | 2013/2014 | November-2013 | 11 | 2013
29644 | Lightning | 2013-11-06 14:16 | 2013-11-06 | 2013-11-06 15:30 | Calculated | TF796 | TF796 - Transformer Fuse: TF796 |  | 120SEG497-REG31 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 2 | 24552 | 148 | 0.00603 | 8.146e-05 | 25 | 1850 | 2013/2014 | November-2013 | 11 | 2013
29643 | L/V Fault | 2013-11-06 15:06 | 2013-11-06 | 2013-11-06 15:28 | Calculated | TF836 | TF836 - Transformer Fuse: TF836 |  | 121SEG421-424 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 2 | 24552 | 44 | 0.00179 | 8.146e-05 | 25 | 550 | 2013/2014 | November-2013 | 11 | 2013
29649 | Lightning | 2013-11-06 15:14 | 2013-11-06 | 2013-11-06 16:30 | Calculated | TF2691 | TF2691 - Transformer Fuse: TF2691 |  | 124SEG542-786 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 1 | 24552 | 76 | 0.0031 | 4.073e-05 | 50 | 3800 | 2013/2014 | November-2013 | 11 | 2013
29663 | Lightning - Replaced Tx | 2013-11-06 15:24 | 2013-11-06 | 2013-11-07 09:00 | Calculated | TF2415 | TF2415 - Transformer Fuse: TF2415 |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1056 | 3 | 24552 | 3168 | 0.12903 | 0.00012219 | 30 | 31680 | 2013/2014 | November-2013 | 11 | 2013
29656 | Lightning | 2013-11-06 15:31 | 2013-11-06 | 2013-11-06 17:43 | Calculated | TF4153 | TF4153 - Transformer Fuse: TF4153 |  | 124SEG5536 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 1 | 24552 | 132 | 0.00538 | 4.073e-05 | 15 | 1980 | 2013/2014 | November-2013 | 11 | 2013
29646 | Lightning | 2013-11-06 15:38 | 2013-11-06 | 2013-11-06 16:26 | Calculated | TF707 | TF707 - Transformer Fuse: TF707 |  | 118SEG462-664 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 4 | 24552 | 192 | 0.00782 | 0.00016292 | 50 | 2400 | 2013/2014 | November-2013 | 11 | 2013
29647 | Faulty Tx - Lightning | 2013-11-06 15:38 | 2013-11-06 | 2013-11-06 20:15 | Calculated | TF708 | TF708 - Transformer Fuse: TF708 |  | 118SEG588 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 277 | 2 | 24552 | 554 | 0.02256 | 8.146e-05 | 25 | 6925 | 2013/2014 | November-2013 | 11 | 2013
29648 | Lightning | 2013-11-06 15:44 | 2013-11-06 | 2013-11-06 15:53 | Calculated | TF1802 | TF1802 - Transformer Fuse: TF1802 |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24552 |  | 0 | 0 |  |  | 2013/2014 | November-2013 | 11 | 2013
29650 | Lightning | 2013-11-06 15:50 | 2013-11-06 | 2013-11-06 16:51 | Calculated | TF1258 | TF1258 - Transformer Fuse: TF1258 |  | 118SEG491-462 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 3 | 24552 | 183 | 0.00745 | 0.00012219 | 30 | 1830 | 2013/2014 | November-2013 | 11 | 2013
29651 | Lightning | 2013-11-06 16:01 | 2013-11-06 | 2013-11-06 17:04 | Calculated | TF4Q4 | TF4Q4 - Transformer Fuse: TF4Q4 |  | 124SEG5610-5535 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 4 | 24552 | 252 | 0.01026 | 0.00016292 | 15 | 945 | 2013/2014 | November-2013 | 11 | 2013
29658 | Lightning | 2013-11-06 16:02 | 2013-11-06 | 2013-11-06 20:21 | Calculated | TF2Q5 | TF2Q5 - Transformer Fuse: TF2Q5 |  | 124SEG1283 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 259 | 1 | 24552 | 259 | 0.01055 | 4.073e-05 | 3 | 777 | 2013/2014 | November-2013 | 11 | 2013
29652 | Lightning | 2013-11-06 16:09 | 2013-11-06 | 2013-11-06 17:09 | Calculated | TF798 | TF798 - Transformer Fuse: TF798 |  | 118SEG491-462 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 1 | 24552 | 60 | 0.00244 | 4.073e-05 | 30 | 1800 | 2013/2014 | November-2013 | 11 | 2013
29660 | Lightning | 2013-11-06 16:09 | 2013-11-06 | 2013-11-06 20:48 | Calculated | TF797 | TF797 - Transformer Fuse: TF797 |  | 120SEG497-REG31 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 279 | 2 | 24552 | 558 | 0.02273 | 8.146e-05 | 25 | 6975 | 2013/2014 | November-2013 | 11 | 2013
29653 | Lightning | 2013-11-06 16:13 | 2013-11-06 | 2013-11-06 17:27 | Calculated | TF1551 | TF1551 - Transformer Fuse: TF1551 |  | 120SEG497-REG31 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 1 | 24552 | 74 | 0.00301 | 4.073e-05 | 15 | 1110 | 2013/2014 | November-2013 | 11 | 2013
29654 | Lightning Broken DDO | 2013-11-06 16:15 | 2013-11-06 | 2013-11-06 21:05 | Calculated | TF1384 | TF1384 - Transformer Fuse: TF1384 |  | 124SEG478-2145 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 290 | 2 | 24552 | 580 | 0.02362 | 8.146e-05 | 15 | 4350 | 2013/2014 | November-2013 | 11 | 2013
29659 | Lightning | 2013-11-06 18:49 | 2013-11-06 | 2013-11-06 20:51 | Calculated | TF1432 | TF1432 - Transformer Fuse: TF1432 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 2 | 24552 | 244 | 0.00994 | 8.146e-05 | 15 | 1830 | 2013/2014 | November-2013 | 11 | 2013
29657 | Lightning | 2013-11-06 19:08 | 2013-11-06 | 2013-11-06 20:06 | Calculated | TF368 | TF368 - Transformer Fuse: TF368 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 3 | 24552 | 174 | 0.00709 | 0.00012219 | 15 | 870 | 2013/2014 | November-2013 | 11 | 2013
29655 | Replace DDO Tx 1384 | 2013-11-06 19:43 | 2013-11-06 | 2013-11-06 21:05 | Calculated | 478 | 478 - Fused Link 478 |  | 124SEG478-2145 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 12 | 24552 | 984 | 0.04008 | 0.00048876 | 110 | 9020 | 2013/2014 | November-2013 | 11 | 2013
29662 | Lightning | 2013-11-06 19:43 | 2013-11-06 | 2013-11-06 21:41 | Calculated | TF817 | TF817 - Transformer Fuse :TF817 |  | 123SEG1653 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 2 | 24552 | 236 | 0.00961 | 8.146e-05 | 10 | 1180 | 2013/2014 | November-2013 | 11 | 2013
29661 | Lightning | 2013-11-06 20:14 | 2013-11-06 | 2013-11-06 21:28 | Calculated | TF148 | TF148 - Transformer Fuse: TF148 |  | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 4 | 24552 | 296 | 0.01206 | 0.00016292 | 25 | 1850 | 2013/2014 | November-2013 | 11 | 2013
29664 | Lightning | 2013-11-06 20:50 | 2013-11-06 | 2013-11-06 23:27 | Calculated | TF653 | TF653 - Transformer Fuse: TF653 |  | 104SEG730-547 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 1 | 24552 | 157 | 0.00639 | 4.073e-05 | 5 | 785 | 2013/2014 | November-2013 | 11 | 2013
29665 | Lightning | 2013-11-06 22:30 | 2013-11-06 | 2013-11-06 23:12 | Calculated | TF635 | TF635 - Transformer Fuse: TF635 |  | 104SEG730-547 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 2 | 24552 | 84 | 0.00342 | 8.146e-05 | 5 | 210 | 2013/2014 | November-2013 | 11 | 2013
29668 | Lightning | 2013-11-07 08:41 | 2013-11-07 | 2013-11-07 12:04 | Calculated | 2041 | 2041 - Fused Link 2041 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 203 | 4 | 24552 | 611 | 0.02489 | 0.00016292 | 65 | 11140 | 2013/2014 | November-2013 | 11 | 2013
29670 | Lightning | 2013-11-07 09:21 | 2013-11-07 | 2013-11-07 14:04 | Calculated | TF1287 | TF1287 - Transformer Fuse: TF1287 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 283 | 2 | 24552 | 566 | 0.02305 | 8.146e-05 | 15 | 4245 | 2013/2014 | November-2013 | 11 | 2013
29669 | Lightning | 2013-11-07 12:32 | 2013-11-07 | 2013-11-07 13:39 | Calculated | TF968 | TF968 - Transformer Fuse: TF968 |  | 124SEG1764-454 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 1 | 24552 | 67 | 0.00273 | 4.073e-05 | 5 | 335 | 2013/2014 | November-2013 | 11 | 2013
29671 | Lightning | 2013-11-07 16:05 | 2013-11-07 | 2013-11-07 17:17 | Calculated | TF21N8 | TF21N8 - Transformer Fuse: TF21N8 |  | 416SEG5683-5523 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 3 | 24552 | 216 | 0.0088 | 0.00012219 | 15 | 1080 | 2013/2014 | November-2013 | 11 | 2013
29673 | Lightning | 2013-11-07 17:01 | 2013-11-07 | 2013-11-07 18:06 | Calculated | TF21N14 | TF21N14 - Transformer Fuse: TF21N14 |  | 416SEG5683-5523 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 5 | 24552 | 325 | 0.01324 | 0.00020365 | 50 | 3250 | 2013/2014 | November-2013 | 11 | 2013
29672 | Lightning | 2013-11-07 17:50 | 2013-11-07 | 2013-11-07 21:19 | Calculated | TF21N17 | TF21N17 - Transformer Fuse: TF21N17 |  | 416SEG5683-5523 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 209 | 4 | 24552 | 836 | 0.03405 | 0.00016292 | 30 | 6270 | 2013/2014 | November-2013 | 11 | 2013
29674 | Lightning | 2013-11-07 23:26 | 2013-11-07 | 2013-11-08 01:25 | Calculated | TF4020 | TF4020 - Transformer Fuse: TF4020 |  | 416SEG5961-5683 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 1 | 24552 | 119 | 0.00485 | 4.073e-05 | 3 | 357 | 2013/2014 | November-2013 | 11 | 2013
29675 | Possum | 2013-11-08 03:18 | 2013-11-08 | 2013-11-08 04:26 | Calculated | TF7I22 | TF7I22 - Transformer Fuse: TF7I22 |  | 402SEG5351-5548 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 53 | 24552 | 3604 | 0.14679 | 0.0021587 | 200 | 13599 | 2013/2014 | November-2013 | 11 | 2013
29676 | Lightning - Replace Faulty Tx | 2013-11-08 08:11 | 2013-11-08 | 2013-11-08 18:22 | Calculated | 5524 | 5524 - Sectionaliser 5524 |  | 427SEG5524 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 611 | 6 | 24552 | 2694 | 0.10973 | 0.00024438 | 50 | 22045 | 2013/2014 | November-2013 | 11 | 2013
29677 | Refer 2013/ 7956 Access Permit | 2013-11-08 09:22 | 2013-11-08 | 2013-11-08 12:54 | Calculated | 5239 | 5239 - Fused Link 5239 |  | 426SEG5239 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 212 | 6 | 24552 | 1272 | 0.05181 | 0.00024438 | 60 | 12720 | 2013/2014 | November-2013 | 11 | 2013
29678 | Refer 2013/388 Replace Poles & X-Arms | 2013-11-08 09:40 | 2013-11-08 | 2013-11-08 14:23 | Calculated | 5435 | 5435 - Fused Link 5435 |  | 421SEG5435 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 283 | 6 | 24552 | 1698 | 0.06916 | 0.00024438 | 45 | 12735 | 2013/2014 | November-2013 | 11 | 2013
29679 | Refer 2013/374 Replace Red Tagged Tx 249 | 2013-11-08 09:43 | 2013-11-08 | 2013-11-08 16:09 | Calculated | 522 | 522 - Air Break Switch 522 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 386 | 52 | 24552 | 16322 | 0.66479 | 0.002118 | 560 | 176034 | 2013/2014 | November-2013 | 11 | 2013
29681 | L/V Line Down | 2013-11-08 12:23 | 2013-11-08 | 2013-11-08 14:08 | Calculated | TF1286 | TF1286 - Transformer Fuse: TF1286 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 2 | 24552 | 210 | 0.00855 | 8.146e-05 | 25 | 2625 | 2013/2014 | November-2013 | 11 | 2013
29682 | Lightning | 2013-11-08 16:03 | 2013-11-08 | 2013-11-08 16:45 | Calculated | TF21O5 | TF21O5 - Transformer Fuse: TF21O5 |  | 416SEG5523-5554 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 2 | 24552 | 84 | 0.00342 | 8.146e-05 | 3 | 126 | 2013/2014 | November-2013 | 11 | 2013
29683 | Lightning | 2013-11-09 08:22 | 2013-11-09 | 2013-11-09 10:45 | Calculated | TF21O5 | TF21O5 - Transformer Fuse: TF21O5 |  | 416SEG5523-5554 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 2 | 24552 | 286 | 0.01165 | 8.146e-05 | 3 | 429 | 2013/2014 | November-2013 | 11 | 2013
29684 | Vehicle vs Line | 2013-11-09 22:35 | 2013-11-09 | 2013-11-10 06:02 | Calculated | 1110 | 1110 - Air Break Switch 1110 |  | 114SEG1109-1110 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 447 | 196 | 24552 | 50939 | 2.0747 | 0.0079831 | 1355.5 | 322614 | 2013/2014 | November-2013 | 11 | 2013
29685 | Birds | 2013-11-10 09:23 | 2013-11-10 | 2013-11-10 18:52 | Calculated | 5641 | 5641 - Recloser with Bypass & Links 5641 |  | 413SEG6781-5666 | Ohura 413-01 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 218 | 359 | 24552 | 28263 | 1.1511 | 0.014622 | 2640 | 218057 | 2013/2014 | November-2013 | 11 | 2013
29688 | Blown HV Fuse - Unknown Fault | 2013-11-10 10:10 | 2013-11-10 | 2013-11-10 11:45 | Calculated | TF14L03 | TF14L03 - Transformer Fuse: TF14L03 |  | 411SEG5774 | National Park 411-02 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 1 | 24552 | 95 | 0.00387 | 4.073e-05 | 15 | 1425 | 2013/2014 | November-2013 | 11 | 2013
29691 | Blown HV Fuse - Unknown Fault | 2013-11-11 08:27 | 2013-11-11 | 2013-11-11 09:35 | Calculated | TF318 | TF318 - Transformer Fuse: TF318 |  | 110SEG711 | McDonalds 110-04 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 5 | 24552 | 340 | 0.01385 | 0.00020365 | 25 | 1700 | 2013/2014 | November-2013 | 11 | 2013
29689 | Refer 2013/378 Replace Poles & X Arms Crossing State Highway And Railway Electrification | 2013-11-11 08:35 | 2013-11-11 | 2013-11-11 15:45 | Calculated | 669 | 669 - Recloser with Bypass & Links 669 |  | 103SEG REG14-669 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 401 | 14 | 24552 | 5614 | 0.22866 | 0.00057022 | 160 | 64159 | 2013/2014 | November-2013 | 11 | 2013
29690 | Refer 2013/376 Move pole 17/1/38/18 - 1 Metre | 2013-11-11 09:11 | 2013-11-11 | 2013-11-11 10:34 | Calculated | 5443 | 5443 - Fused Link 5443 |  | 403SEG5766-5460 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 83 | 4 | 24552 | 332 | 0.01352 | 0.00016292 | 40 | 3320 | 2013/2014 | November-2013 | 11 | 2013
29692 | Refer 2013/375 Replace Pole Damaged By Tree During Faults | 2013-11-11 09:41 | 2013-11-11 | 2013-11-11 14:32 | Calculated | 5765 | 5765 - Fused Link 5765 |  | 403SEG5765-5653 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 291 | 6 | 24552 | 1746 | 0.07111 | 0.00024438 | 28 | 8148 | 2013/2014 | November-2013 | 11 | 2013
29695 | Birds | 2013-11-12 05:23 | 2013-11-12 | 2013-11-12 06:43 | Calculated | 189 | 189 - Fused Link 189 |  | 110SEG189 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 5 | 24552 | 400 | 0.01629 | 0.00020365 | 80 | 6400 | 2013/2014 | November-2013 | 11 | 2013
29696 | Trees | 2013-11-12 09:01 | 2013-11-12 | 2013-11-12 15:20 | Calculated | TF44 | TF44 - Transformer Fuse: TF44 |  | 104SEG730-547 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 379 | 2 | 24552 | 758 | 0.03087 | 8.146e-05 | 15 | 5685 | 2013/2014 | November-2013 | 11 | 2013
29699 | Refer 2013/379 Replace Poles & X Arms | 2013-11-13 08:22 | 2013-11-13 | 2013-11-13 15:50 | Calculated | 669 | 669 - Recloser with Bypass & Links 669 |  | 103SEG REG14-669 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 402 | 10 | 24552 | 4020 | 0.16373 | 0.0004073 | 115 | 46229 | 2013/2014 | November-2013 | 11 | 2013
29700 | Broken X Arrm | 2013-11-13 08:46 | 2013-11-13 | 2013-11-13 15:09 | Calculated | TF1894 | TF1894 - Transformer Fuse: TF1894 |  | 114SEG1100 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 383 | 4 | 24552 | 1532 | 0.0624 | 0.00016292 | 30 | 11490 | 2013/2014 | November-2013 | 11 | 2013
29702 | Refer 2013/380 Replace Poles & X Arms Between ABS 219 & 181 Including ABS 181 | 2013-11-13 08:55 | 2013-11-13 | 2013-11-13 15:53 | Calculated | 219 | 219 - Air Break Switch 219 |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 380 | 49 | 24552 | 18620 | 0.75839 | 0.0019958 | 280 | 106400 | 2013/2014 | November-2013 | 11 | 2013
29701 | Refer 2013/382 Replace Sectionalizers 5396 & 5170 | 2013-11-13 10:01 | 2013-11-13 | 2013-11-13 13:49 | Calculated | 5438 | 5438 - Fused Link 5438 |  | 410SEG5438-5597 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 228 | 71 | 24552 | 16188 | 0.65934 | 0.0028918 | 438 | 99863 | 2013/2014 | November-2013 | 11 | 2013
29703 | Unknown | 2013-11-13 23:41 | 2013-11-13 | 2013-11-14 00:02 | Calculated | 788 | 788 - Circuit Breaker 788 |  | 302SEG147-788 | Taharoa B 302-02 | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 18 | 319 | 24552 | 5742 | 0.23387 | 0.012993 | 2466 | 44387 | 2013/2014 | November-2013 | 11 | 2013
29704 | Refer 2013/385 Replacing X Arms | 2013-11-14 09:31 | 2013-11-14 | 2013-11-14 13:41 | Calculated | 575 | 575 - Fused Link 575 |  | 107SEG575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 250 | 13 | 24552 | 3250 | 0.13237 | 0.00052949 | 150 | 37499 | 2013/2014 | November-2013 | 11 | 2013
29705 | Refer 2013/383 Replace Pole Structure Tx 9L6 | 2013-11-14 09:52 | 2013-11-14 | 2013-11-14 15:24 | Calculated | 5406 | 5406 - Solid Link 5406 |  | 408SEG5406 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 332 | 10 | 24552 | 3320 | 0.13522 | 0.0004073 | 31 | 10292 | 2013/2014 | November-2013 | 11 | 2013
29706 | Refer 2013/399 Replace X Arms | 2013-11-14 13:20 | 2013-11-14 | 2013-11-14 17:05 | Calculated | 5334 | 5334 - Fused Link 5334 |  | 410SEG5334-5745 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 225 | 9 | 24552 | 2025 | 0.08248 | 0.00036657 | 65 | 14625 | 2013/2014 | November-2013 | 11 | 2013
29708 | Refer 2013/384 Replace Poles & X Arms | 2013-11-15 09:03 | 2013-11-15 | 2013-11-15 14:43 | Calculated | 239 | 239 - Fused Link 239 |  | 107SEG239-508 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 340 | 35 | 24552 | 11900 | 0.48469 | 0.0014255 | 205 | 69699 | 2013/2014 | November-2013 | 11 | 2013
29709 | Faulty HV Jumper | 2013-11-15 09:57 | 2013-11-15 | 2013-11-15 14:01 | Calculated | 1611 | 1611 - Fused Link 1611 |  | 128SEG1610-1611 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 244 | 50 | 24552 | 12200 | 0.4969 | 0.0020365 | 387.5 | 94550 | 2013/2014 | November-2013 | 11 | 2013
29710 | Blown HV Fuse - Unknown Fault | 2013-11-15 21:54 | 2013-11-15 | 2013-11-15 23:27 | Calculated | TF11S10 | TF11S10 - Transformer Fuse: TF11S10 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 2 | 24552 | 186 | 0.00758 | 8.146e-05 | 15 | 1395 | 2013/2014 | November-2013 | 11 | 2013
29711 | Branch through line | 2013-11-16 12:06 | 2013-11-16 | 2013-11-16 13:57 | Calculated | 5986 | 5986 - Fused Link 5986 |  | 402SEG5986 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 29 | 24552 | 3219 | 0.13111 | 0.0011812 | 250 | 27749 | 2013/2014 | November-2013 | 11 | 2013
29712 | Refer 2013/MM1 | 2013-11-18 09:04 | 2013-11-18 | 2013-11-18 09:42 | Calculated | TO9H3 | TO9H3 - Tap-off Fuse 9H3 |  | 403SEG5316-5622 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 38 | 2 | 24552 | 76 | 0.0031 | 8.146e-05 | 15 | 570 | 2013/2014 | November-2013 | 11 | 2013
29714 | Refer 2013/MM2 | 2013-11-18 10:01 | 2013-11-18 | 2013-11-18 10:25 | Calculated | TF9H9 | TF9H9 - Transformer Fuse: TF9H9 |  | 403SEG5602-5317 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 24 | 1 | 24552 | 24 | 0.00098 | 4.073e-05 | 25 | 600 | 2013/2014 | November-2013 | 11 | 2013
29715 | Refer 2013/MM3 | 2013-11-18 11:02 | 2013-11-18 | 2013-11-18 11:31 | Calculated | TO9H10 | TO9H10 - Tap-off Fuse 9H10 |  | 403SEG5602-5317 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 29 | 3 | 24552 | 87 | 0.00354 | 0.00012219 | 15 | 435 | 2013/2014 | November-2013 | 11 | 2013
29716 | Refer 2013/MM4 | 2013-11-18 12:02 | 2013-11-18 | 2013-11-18 12:45 | Calculated | TO10H3 | TO10H3 - Tap-off Fuse 10H3 |  | 403SEG5368-5230 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 43 | 2 | 24552 | 86 | 0.0035 | 8.146e-05 | 10 | 430 | 2013/2014 | November-2013 | 11 | 2013
29717 | Refer 2013/MM5 | 2013-11-18 13:14 | 2013-11-18 | 2013-11-18 13:37 | Calculated | TO09G10 | TO09G10 - Tap-off Fuse: TO9G10 |  | 403SEG5932-5649 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 23 | 2 | 24552 | 46 | 0.00187 | 8.146e-05 | 15 | 345 | 2013/2014 | November-2013 | 11 | 2013
29718 | Refer 2013/MM6 | 2013-11-18 14:35 | 2013-11-18 | 2013-11-18 14:54 | Calculated | TO9G8 | TO9G8 - Tap-off Fuse 9G8 |  | 403SEG5368-5230 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 19 | 2 | 24552 | 38 | 0.00155 | 8.146e-05 | 10 | 190 | 2013/2014 | November-2013 | 11 | 2013
29720 | Refer 2013/MT001 | 2013-11-19 08:50 | 2013-11-19 | 2013-11-19 13:45 | Calculated | TO6H18 | TO6H18 - Tap-off Fuse TO6H18 |  | 402SEG5776 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 209 | 15 | 24552 | 656 | 0.02672 | 0.00061095 | 107.5 | 4982 | 2013/2014 | November-2013 | 11 | 2013
29719 | Refer 2013/405 Replace ABS 636 Structure | 2013-11-19 09:05 | 2013-11-19 | 2013-11-19 15:41 | Calculated | 238 | 238 - Solid Links 238 |  | 103SEG636-238 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 387 | 3 | 24552 | 1161 | 0.04729 | 0.00012219 | 15 | 5805 | 2013/2014 | November-2013 | 11 | 2013
29721 | Lightning | 2013-11-19 14:05 | 2013-11-19 | 2013-11-19 15:38 | Calculated | TF2583 | TF2583 - Transformer Fuse: TF2583 |  | 111SEG2063 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 1 | 24552 | 93 | 0.00379 | 4.073e-05 | 10 | 930 | 2013/2014 | November-2013 | 11 | 2013
29726 | Lightning | 2013-11-19 15:07 | 2013-11-19 | 2013-11-19 17:12 | Calculated | TF1685 | TF1685 - Transformer Fuse: TF1685 |  | 116SEG1354-1334 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 3 | 24552 | 375 | 0.01527 | 0.00012219 | 15 | 1875 | 2013/2014 | November-2013 | 11 | 2013
29742 | Lightning | 2013-11-19 15:14 | 2013-11-19 | 2013-11-19 17:30 | Calculated | TF2235 | TF2235 - Transformer Fuse: TF2235 |  | 110SEG554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 6 | 24552 | 816 | 0.03324 | 0.00024438 | 30 | 4080 | 2013/2014 | November-2013 | 11 | 2013
29743 | Lightning | 2013-11-19 15:14 | 2013-11-19 | 2013-11-19 18:00 | Calculated | 554 | 554 - Fused Link 554 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 15 | 24552 | 2490 | 0.10142 | 0.00061095 | 110 | 18260 | 2013/2014 | November-2013 | 11 | 2013
29727 | Lightning | 2013-11-19 15:16 | 2013-11-19 | 2013-11-19 18:15 | Calculated | TF632 | TF632 - Transformer Fuse: TF632 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 2 | 24552 | 358 | 0.01458 | 8.146e-05 | 25 | 4475 | 2013/2014 | November-2013 | 11 | 2013
29745 | Lightning | 2013-11-19 15:17 | 2013-11-19 | 2013-11-19 18:30 | Calculated | TF470 | TF470 - Transformer Fuse: TF470 |  | 111SEG648 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 4 | 24552 | 772 | 0.03144 | 0.00016292 | 25 | 4825 | 2013/2014 | November-2013 | 11 | 2013
29723 | Lightning | 2013-11-19 15:30 | 2013-11-19 | 2013-11-19 16:36 | Calculated | TF2447 | TF2447 - Transformer Fuse: TF2447 |  | 116SEG1354-1334 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 3 | 24552 | 198 | 0.00806 | 0.00012219 | 15 | 990 | 2013/2014 | November-2013 | 11 | 2013
29725 | Lightning | 2013-11-19 15:30 | 2013-11-19 | 2013-11-19 16:42 | Calculated | TF2694 | TF2694 - Transformer Fuse: TF2694 |  | 116SEG1354-1334 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 1 | 24552 | 72 | 0.00293 | 4.073e-05 | 50 | 3600 | 2013/2014 | November-2013 | 11 | 2013
29732 | Lightning | 2013-11-19 15:43 | 2013-11-19 | 2013-11-19 18:31 | Calculated | TF1992 | TF1992 - Transformer Fuse: TF1992 |  | 113SEG1505 | Mahoenui 113-01 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 1 | 24552 | 168 | 0.00684 | 4.073e-05 | 15 | 2520 | 2013/2014 | November-2013 | 11 | 2013
29735 | Lightning | 2013-11-19 15:43 | 2013-11-19 | 2013-11-19 18:46 | Calculated | TF1571 | TF1571 - Transformer Fuse: TF1571 |  | 113SEG1505 | Mahoenui 113-01 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 183 | 1 | 24552 | 183 | 0.00745 | 4.073e-05 | 10 | 1830 | 2013/2014 | November-2013 | 11 | 2013
29740 | Lightning, Replaced Tx | 2013-11-19 15:46 | 2013-11-19 | 2013-11-19 23:01 | Calculated | TF1647 | TF1647 - Transformer Fuse: TF1647 |  | 113SEG1529 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 435 | 1 | 24552 | 435 | 0.01772 | 4.073e-05 | 15 | 6525 | 2013/2014 | November-2013 | 11 | 2013
29741 | Lightning | 2013-11-19 15:46 | 2013-11-19 | 2013-11-19 20:02 | Calculated | TF1083 | TF1083 - Transformer Fuse: TF1083 |  | 113SEG1529 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 256 | 1 | 24552 | 256 | 0.01043 | 4.073e-05 | 3 | 768 | 2013/2014 | November-2013 | 11 | 2013
29722 | Lightning | 2013-11-19 15:48 | 2013-11-19 | 2013-11-19 16:51 | Calculated | TF274 | TF274 - Transformer Fuse: TF274 |  | 111SEG648 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 9 | 24552 | 567 | 0.02309 | 0.00036657 | 70 | 4409 | 2013/2014 | November-2013 | 11 | 2013
29733 | Lightning | 2013-11-19 15:54 | 2013-11-19 | 2013-11-19 18:18 | Calculated | 1528 | 1528 - Fused Link 1528 |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 12 | 24552 | 1728 | 0.07038 | 0.00048876 | 58 | 8351 | 2013/2014 | November-2013 | 11 | 2013
29724 | Lightning | 2013-11-19 15:56 | 2013-11-19 | 2013-11-19 16:55 | Calculated | TF782 | TF782 - Transformer Fuse: TF782 |  | 129SEG442-2238 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 5 | 24552 | 295 | 0.01202 | 0.00020365 | 15 | 885 | 2013/2014 | November-2013 | 11 | 2013
29693 | Lightning | 2013-11-19 16:03 | 2013-11-19 | 2013-11-19 18:03 | Calculated | 1121 | 1121 - Fused Link 1121 |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 5 | 24552 | 600 | 0.02444 | 0.00020365 | 25 | 3000 | 2013/2014 | November-2013 | 11 | 2013
29728 | Lightning | 2013-11-19 16:03 | 2013-11-19 | 2013-11-19 17:30 | Calculated | TF1988 | TF1988 - Transformer Fuse: TF1988 |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 1 | 24552 | 87 | 0.00354 | 4.073e-05 | 10 | 870 | 2013/2014 | November-2013 | 11 | 2013
29729 | Lightning | 2013-11-19 16:08 | 2013-11-19 | 2013-11-19 17:25 | Calculated | TF181 | TF181 - Transformer Fuse: TF181 |  | 110SEG554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 1 | 24552 | 77 | 0.00314 | 4.073e-05 | 15 | 1155 | 2013/2014 | November-2013 | 11 | 2013
29730 | Lightning | 2013-11-19 16:26 | 2013-11-19 | 2013-11-19 18:25 | Calculated | TF1477 | TF1477 - Transformer Fuse: TF1477 |  | 124SEG433 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 2 | 24552 | 238 | 0.00969 | 8.146e-05 | 10 | 1190 | 2013/2014 | November-2013 | 11 | 2013
29734 | Lightning | 2013-11-19 16:51 | 2013-11-19 | 2013-11-19 18:31 | Calculated | TF2943 | TF2943 - Transformer Fuse: TF2943 |  | 122SEG372 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 1 | 24552 | 100 | 0.00407 | 4.073e-05 | 10 | 1000 | 2013/2014 | November-2013 | 11 | 2013
29736 | Lightning | 2013-11-19 17:47 | 2013-11-19 | 2013-11-19 18:43 | Calculated | 1531 | 1531 - Sectionaliser 1531 |  | 113SEG1531-1501 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 56 | 18 | 24552 | 1008 | 0.04106 | 0.00073314 | 130 | 7279 | 2013/2014 | November-2013 | 11 | 2013
29738 | Lightning, Replaced Tx | 2013-11-19 17:51 | 2013-11-19 | 2013-11-19 23:51 | Calculated | TF1423 | TF1423 - Transformer Fuse: TF1423 |  | 122SEG372 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 360 | 1 | 24552 | 360 | 0.01466 | 4.073e-05 | 3 | 1080 | 2013/2014 | November-2013 | 11 | 2013
29739 | Lightning | 2013-11-19 17:53 | 2013-11-19 | 2013-11-19 19:37 | Calculated | TF1N1 | TF1N1 - Transformer Fuse: TF1N1 |  | 421SEG5933 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 104 | 3 | 24552 | 312 | 0.01271 | 0.00012219 | 15 | 1560 | 2013/2014 | November-2013 | 11 | 2013
29746 | Lightning | 2013-11-19 19:08 | 2013-11-19 | 2013-11-19 21:45 | Calculated | TF17I01 | TF17I01 - Transformer Fuse: TF17I01 |  | 410SEG5510-5511 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 157 | 1 | 24552 | 157 | 0.00639 | 4.073e-05 | 3 | 471 | 2013/2014 | November-2013 | 11 | 2013
29737 | Lightning, Replace Tx | 2013-11-19 19:34 | 2013-11-19 | 2013-11-20 00:48 | Calculated | TF1654 | TF1654 - Transformer Fuse: TF1654 |  | 113SEG1531-1501 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 314 | 3 | 24552 | 942 | 0.03837 | 0.00012219 | 10 | 3139 | 2013/2014 | November-2013 | 11 | 2013
29747 | Refer 2013/392 Replace Poles & X Arms Between ABS 211 & ABS 501 | 2013-11-20 08:33 | 2013-11-20 | 2013-11-20 15:48 | Calculated | 211 | 211 - Air Break Switch 211 |  | 108SEG211-212 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 385 | 154 | 24552 | 59290 | 2.4149 | 0.0062724 | 750 | 288749 | 2013/2014 | November-2013 | 11 | 2013
29749 | Lightning | 2013-11-20 08:48 | 2013-11-20 | 2013-11-20 09:56 | Calculated | TF1571 | TF1571 - Transformer Fuse: TF1571 |  | 113SEG1505 | Mahoenui 113-01 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 1 | 24552 | 68 | 0.00277 | 4.073e-05 | 10 | 680 | 2013/2014 | November-2013 | 11 | 2013
29748 | Refer 2013/394 Move Line @ Tx 1378/ Shift Away From Trees | 2013-11-20 09:35 | 2013-11-20 | 2013-11-20 15:02 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 26 | 24552 | 8502 | 0.34629 | 0.001059 | 330 | 107910 | 2013/2014 | November-2013 | 11 | 2013
29750 | Lightning | 2013-11-20 10:07 | 2013-11-20 | 2013-11-20 11:13 | Calculated | TF2991 | TF2991 - Transformer Fuse: TF2991 |  | 103SEG641-1350 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 66 | 1 | 24552 | 66 | 0.00269 | 4.073e-05 | 10 | 660 | 2013/2014 | November-2013 | 11 | 2013
29751 | Lightning | 2013-11-20 10:48 | 2013-11-20 | 2013-11-20 12:26 | Calculated | TF1429 | TF1429 - Transformer Fuse: TF1429 |  | 110SEG554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 1 | 24552 | 98 | 0.00399 | 4.073e-05 | 10 | 980 | 2013/2014 | November-2013 | 11 | 2013
29753 | L/V Line Down | 2013-11-20 17:40 | 2013-11-20 | 2013-11-20 18:33 | Calculated | TF21N14 | TF21N14 - Transformer Fuse: TF21N14 |  | 416SEG5683-5523 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 5 | 24552 | 265 | 0.01079 | 0.00020365 | 50 | 2650 | 2013/2014 | November-2013 | 11 | 2013
29755 | Lightning | 2013-11-20 18:21 | 2013-11-20 | 2013-11-20 20:49 | Calculated | TF4Q4 | TF4Q4 - Transformer Fuse: TF4Q4 |  | 124SEG5610-5535 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 4 | 24552 | 592 | 0.02411 | 0.00016292 | 15 | 2220 | 2013/2014 | November-2013 | 11 | 2013
29754 | Lightning | 2013-11-20 18:33 | 2013-11-20 | 2013-11-20 20:35 | Calculated | TF4Q9 | TF4Q9 - Transformer Fuse: TF4Q9 |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 1 | 24552 | 122 | 0.00497 | 4.073e-05 | 15 | 1830 | 2013/2014 | November-2013 | 11 | 2013
29756 | Lightning | 2013-11-20 19:21 | 2013-11-20 | 2013-11-20 20:21 | Calculated | TF4J2 | TF4J2 - Transformer Fuse: TF4J2 |  | 421SEG5656-5669 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 60 | 3 | 24552 | 180 | 0.00733 | 0.00012219 | 15 | 900 | 2013/2014 | November-2013 | 11 | 2013
29757 | Lightning | 2013-11-20 19:35 | 2013-11-20 | 2013-11-20 21:29 | Calculated | TF6E12 | TF6E12 - Transformer Fuse: TF6E12 |  | 412SEG5256-5445 | Nihoniho 412-01 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 2 | 24552 | 228 | 0.00929 | 8.146e-05 | 5 | 570 | 2013/2014 | November-2013 | 11 | 2013
29761 | Lightning | 2013-11-21 08:03 | 2013-11-21 | 2013-11-21 11:55 | Calculated | TF4Q12 | TF4Q12 - Transformer Fuse: TF4Q12 |  | 426SEG5333-5532 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 232 | 1 | 24552 | 232 | 0.00945 | 4.073e-05 | 7.5 | 1740 | 2013/2014 | November-2013 | 11 | 2013
29758 | Refer 2013/400 Resag 11KV Lines | 2013-11-21 08:53 | 2013-11-21 | 2013-11-21 14:52 | Calculated | 669 | 669 - Recloser with Bypass & Links 669 |  | 103SEG REG14-669 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 200 | 10 | 24552 | 2000 | 0.08146 | 0.0004073 | 4734.5 | 22999 | 2013/2014 | November-2013 | 11 | 2013
29759 | Refer 2013/398 Replace Pole & X Arms - Line Renewal Project | 2013-11-21 09:10 | 2013-11-21 | 2013-11-21 16:14 | Calculated | 5434 | 5434 - Fused Link 5434 |  | 421SEG5434-5851 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 424 | 16 | 24552 | 6784 | 0.27631 | 0.00065168 | 115 | 48760 | 2013/2014 | November-2013 | 11 | 2013
29760 | Refer 2013/387 Upgrade LV Panel In Tx 10S42, Clean & Tidy Tx 10S41 | 2013-11-21 09:21 | 2013-11-21 | 2013-11-21 16:20 | Calculated | 6198 | 6198 - Fused Link 6198 |  | 423SEG6197-6198 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 419 | 142 | 24552 | 59498 | 2.4234 | 0.0057836 | 450 | 188549 | 2013/2014 | November-2013 | 11 | 2013
29762 | Lightning | 2013-11-21 11:10 | 2013-11-21 | 2013-11-21 13:38 | Calculated | TF14N02 | TF14N02 - Transformer Fuse: TF14N02 |  | 609SEG5158-5159 | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 148 | 2 | 24552 | 296 | 0.01206 | 8.146e-05 | 15 | 2220 | 2013/2014 | November-2013 | 11 | 2013
29763 | Unknown | 2013-11-21 12:35 | 2013-11-21 | 2013-11-21 14:28 | Calculated | TF1953 | TF1953 - Transformer Fuse: TF1953 |  | 114SEG2160 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 1 | 24552 | 113 | 0.0046 | 4.073e-05 | 10 | 1130 | 2013/2014 | November-2013 | 11 | 2013
29764 | Refer 2013/397 Replace Poles & X Arms - Line Renewal Project | 2013-11-22 09:06 | 2013-11-22 | 2013-11-22 14:43 | Calculated | 5739 | 5739 - Sectionaliser with Bypass & Links 5739 |  | 421SEG5436-5434 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 337 | 2 | 24552 | 674 | 0.02745 | 8.146e-05 | 3 | 1011 | 2013/2014 | November-2013 | 11 | 2013
29765 | Refer 2013/396 Move Tx 727 To Pole 92, Replace Pole 121257, Replace ABS Pole 416, Remove Disused LV Lines | 2013-11-22 09:32 | 2013-11-22 | 2013-11-22 15:32 | Calculated | 485 | 485 - Air Break Switch 485 |  | 120SEG485-413 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 360 | 78 | 24552 | 28053 | 1.1426 | 0.0031769 | 1055 | 379404 | 2013/2014 | November-2013 | 11 | 2013
29766 | Unknown | 2013-11-22 10:07 | 2013-11-22 | 2013-11-22 11:04 | Calculated | 455 | 455 - Fused Link 455 |  | 129SEG455-402 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 60 | 24552 | 3420 | 0.1393 | 0.0024438 | 860 | 49019 | 2013/2014 | November-2013 | 11 | 2013
29767 | L/V Maintenance | 2013-11-22 11:00 | 2013-11-22 | 2013-11-22 13:40 | Calculated | TF302 | TF302 - Transformer Fuse: TF302 |  | 122SEG371-633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 160 | 4 | 24552 | 640 | 0.02607 | 0.00016292 | 15 | 2400 | 2013/2014 | November-2013 | 11 | 2013
29768 | Lightning | 2013-11-22 12:44 | 2013-11-22 | 2013-11-22 14:48 | Calculated | TF4009 | TF4009 - Transformer Fuse: TF4009 |  | 410SEG5611-5400 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 124 | 2 | 24552 | 248 | 0.0101 | 8.146e-05 | 5 | 620 | 2013/2014 | November-2013 | 11 | 2013
29770 | Lightning | 2013-11-22 18:28 | 2013-11-22 | 2013-11-22 21:15 | Calculated | TF1075 | TF1075 - Transformer Fuse: TF1075 |  | 121SEG748-418 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 167 | 2 | 24552 | 334 | 0.0136 | 8.146e-05 | 15 | 2505 | 2013/2014 | November-2013 | 11 | 2013
29769 | Lightning | 2013-11-22 18:48 | 2013-11-22 | 2013-11-22 20:00 | Calculated | TF2609 | TF2609 - Transformer Fuse: TF2609 |  | 115SEG1713 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 2 | 24552 | 144 | 0.00587 | 8.146e-05 | 15 | 1080 | 2013/2014 | November-2013 | 11 | 2013
29771 | LV Line Down | 2013-11-22 20:31 | 2013-11-22 | 2013-11-23 01:45 | Calculated | TF254 | TF254 - Transformer Fuse: TF254 |  | 109SEG396-397 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 314 | 9 | 24552 | 1681 | 0.06847 | 0.00036657 | 75 | 12100 | 2013/2014 | November-2013 | 11 | 2013
29772 | Lightning | 2013-11-23 05:58 | 2013-11-23 | 2013-11-23 07:55 | Calculated | TF8F2 | TF8F2 - Transformer Fuse: TF8F2 |  | 413SEG5123 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 117 | 3 | 24552 | 351 | 0.0143 | 0.00012219 | 15 | 1755 | 2013/2014 | November-2013 | 11 | 2013
29773 | Lightning | 2013-11-23 06:33 | 2013-11-23 | 2013-11-23 08:29 | Calculated | TF832 | TF832 - Transformer Fuse: TF832 |  | 121SEG748-418 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 5 | 24552 | 580 | 0.02362 | 0.00020365 | 25 | 2900 | 2013/2014 | November-2013 | 11 | 2013
29774 | Unknown | 2013-11-23 10:10 | 2013-11-23 | 2013-11-23 12:22 | Calculated | 5986 | 5986 - Fused Link 5986 |  | 402SEG5986 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 29 | 24552 | 3828 | 0.15591 | 0.0011812 | 250 | 32999 | 2013/2014 | November-2013 | 11 | 2013
29775 | Refer 2013/391 Replace Poles & X Arms, ABS 212 - Taupiri St | 2013-11-24 09:14 | 2013-11-24 | 2013-11-24 16:35 | Calculated | 211 | 211 - Air Break Switch 211 |  | 108SEG211-212 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 57 | 98 | 24552 | 4328 | 0.17628 | 0.0039915 | 925 | 40399 | 2013/2014 | November-2013 | 11 | 2013
29776 | Lightning | 2013-11-24 17:33 | 2013-11-24 | 2013-11-24 19:53 | Calculated | TF1329 | TF1329 - Transformer Fuse: TF1329 |  | 121SEG425-748 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 2 | 24552 | 280 | 0.0114 | 8.146e-05 | 10 | 1400 | 2013/2014 | November-2013 | 11 | 2013
29777 | Faulty DDO | 2013-11-24 20:51 | 2013-11-24 | 2013-11-24 22:30 | Calculated | TF663 | TF663 - Transformer Fuse: TF663 |  | 107SEG218-640 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 67 | 24552 | 6633 | 0.27016 | 0.0027289 | 200 | 19799 | 2013/2014 | November-2013 | 11 | 2013
29778 | Blown HV Fuse - Unknown Fault | 2013-11-25 12:16 | 2013-11-25 | 2013-11-25 14:23 | Calculated | TF14M05 | TF14M05 - Transformer Fuse: TF14M05 |  | 609SEG5158-5159 | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 127 | 1 | 24552 | 127 | 0.00517 | 4.073e-05 | 15 | 1905 | 2013/2014 | November-2013 | 11 | 2013
29780 | Inframax Truck Vs LV | 2013-11-25 12:37 | 2013-11-25 | 2013-11-25 14:22 | Calculated | TF2550 | TF2550 - Transformer Fuse: TF2550 |  | 109SEG337-2229 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 5 | 24552 | 525 | 0.02138 | 0.00020365 | 30 | 3150 | 2013/2014 | November-2013 | 11 | 2013
29779 | Lightning | 2013-11-25 15:12 | 2013-11-25 | 2013-11-25 16:07 | Calculated | TF817 | TF817 - Transformer Fuse :TF817 |  | 123SEG1653 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 2 | 24552 | 110 | 0.00448 | 8.146e-05 | 10 | 550 | 2013/2014 | November-2013 | 11 | 2013
29731 | Birds | 2013-11-26 07:16 | 2013-11-26 | 2013-11-26 07:55 | Calculated | TF9L7 | TF9L7 - Transformer Fuse: TF9L7 |  | 408SEG5406 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 39 | 3 | 24552 | 117 | 0.00477 | 0.00012219 | 3 | 117 | 2013/2014 | November-2013 | 11 | 2013
29782 | Refer 2013/409 Tapuwahine SWER Change Poles & X Arms | 2013-11-26 09:16 | 2013-11-26 | 2013-11-26 16:14 | Calculated | 5465 | 5465 - Recloser 5465 |  | No Segment | No Asset Group | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 418 | 42 | 24552 | 17553 | 0.71493 | 0.0017107 | 295.5 | 123489 | 2013/2014 | November-2013 | 11 | 2013
29633 | Birds | 2013-11-26 09:40 | 2013-11-26 | 2013-11-26 14:14 | Calculated | TF11S02 | TF11S02 - Transformer Fuse: TF11S02 |  | 424SEG6657 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 274 | 1 | 24552 | 274 | 0.01116 | 4.073e-05 | 10 | 2740 | 2013/2014 | November-2013 | 11 | 2013
29783 | Refer 2013/1161a | 2013-11-26 10:37 | 2013-11-26 | 2013-11-26 12:47 | Calculated | TF2822 | TF2822 - Transformer Fuse: TF2822 |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 130 | 1 | 24552 | 130 | 0.00529 | 4.073e-05 | 15 | 1950 | 2013/2014 | November-2013 | 11 | 2013
29784 | Birds found 27/11 | 2013-11-26 13:30 | 2013-11-26 | 2013-11-26 15:18 | Calculated | 5287 | 5287 - Recloser with Bypass & Links 5287 |  | 413SEG5288-5287 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 108 | 30 | 24552 | 3240 | 0.13196 | 0.0012219 | 203 | 21924 | 2013/2014 | November-2013 | 11 | 2013
29785 | Blown fuse due to overloading | 2013-11-26 14:52 | 2013-11-26 | 2013-11-26 16:12 | Calculated | 5986 | 5986 - Fused Link 5986 |  | 402SEG5986 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 29 | 24552 | 2320 | 0.09449 | 0.0011812 | 250 | 19999 | 2013/2014 | November-2013 | 11 | 2013
29786 | Birds found 27/11 | 2013-11-26 18:37 | 2013-11-26 | 2013-11-27 11:59 | Calculated | 5287 | 5287 - Recloser with Bypass & Links 5287 |  | 413SEG5288-5287 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 907 | 30 | 24552 | 9528 | 0.38807 | 0.0012219 | 203 | 58160 | 2013/2014 | November-2013 | 11 | 2013
29788 | Lightning | 2013-11-26 19:35 | 2013-11-26 | 2013-11-26 22:35 | Calculated | TF7E3 | TF7E3 - Transformer Fuse: TF7E3 |  | 413SEG6781-5666 | Ohura 413-01 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 3 | 24552 | 540 | 0.02199 | 0.00012219 | 10 | 1799 | 2013/2014 | November-2013 | 11 | 2013
29787 | Lightning | 2013-11-26 19:56 | 2013-11-26 | 2013-11-26 21:03 | Calculated | TF12P03 | TF12P03 - Transformer Fuse: TF12P03 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 67 | 4 | 24552 | 268 | 0.01092 | 0.00016292 | 15 | 1005 | 2013/2014 | November-2013 | 11 | 2013
29790 | Lightning | 2013-11-26 20:39 | 2013-11-26 | 2013-11-26 22:04 | Calculated | TF809 | TF809 - Transformer Fuse: TF809 |  | 119SEG423-432 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 2 | 24552 | 170 | 0.00692 | 8.146e-05 | 15 | 1275 | 2013/2014 | November-2013 | 11 | 2013
29789 | Lightning | 2013-11-26 20:55 | 2013-11-26 | 2013-11-26 21:25 | Calculated | TF727 | TF727 - Transformer Fuse: TF727 |  | 120SEG485-413 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 3 | 24552 | 90 | 0.00367 | 0.00012219 | 25 | 749 | 2013/2014 | November-2013 | 11 | 2013
29791 | Lightning | 2013-11-26 21:24 | 2013-11-26 | 2013-11-27 00:10 | Calculated | 1528 | 1528 - Fused Link 1528 |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 12 | 24552 | 1992 | 0.08113 | 0.00048876 | 58 | 9627 | 2013/2014 | November-2013 | 11 | 2013
29792 | Fuse Again Polylogger Fitted | 2013-11-27 05:09 | 2013-11-27 | 2013-11-27 06:19 | Calculated | 5986 | 5986 - Fused Link 5986 |  | 402SEG5986 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 29 | 24552 | 2030 | 0.08268 | 0.0011812 | 250 | 17499 | 2013/2014 | November-2013 | 11 | 2013
29796 | Birds | 2013-11-27 07:08 | 2013-11-27 | 2013-11-27 10:44 | Calculated | TF7A2 | TF7A2 - Transformer Fuse: TF7A2 |  | 413SEG5734 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 216 | 6 | 24552 | 1296 | 0.05279 | 0.00024438 | 15 | 3240 | 2013/2014 | November-2013 | 11 | 2013
29795 | Birds | 2013-11-27 08:03 | 2013-11-27 | 2013-11-27 09:50 | Calculated | TF653 | TF653 - Transformer Fuse: TF653 |  | 104SEG730-547 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 1 | 24552 | 107 | 0.00436 | 4.073e-05 | 5 | 535 | 2013/2014 | November-2013 | 11 | 2013
29793 | Birds | 2013-11-27 08:10 | 2013-11-27 | 2013-11-27 08:50 | Calculated | TF758 | TF758 - Transformer Fuse: TF758 |  | 120SEG2065 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 1 | 24552 | 40 | 0.00163 | 4.073e-05 | 25 | 1000 | 2013/2014 | November-2013 | 11 | 2013
29794 | Refer 2013/410 Tapuwahine SWER Change Poles & X Arms | 2013-11-27 09:12 | 2013-11-27 | 2013-11-27 15:57 | Calculated | 5465 | 5465 - Recloser 5465 |  | No Segment | No Asset Group | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 405 | 41 | 24552 | 16605 | 0.67632 | 0.0016699 | 285.5 | 115627 | 2013/2014 | November-2013 | 11 | 2013
29797 | Change Taps | 2013-11-27 12:51 | 2013-11-27 | 2013-11-27 15:26 | Calculated | TF1427 | TF1427 - Transformer Fuse: TF1427 |  | 111SEG2066-347 | Maihiihi 111-02 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLS | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 27 | 24552 | 4185 | 0.17045 | 0.0010997 | 100 | 15499 | 2013/2014 | November-2013 | 11 | 2013
29798 | Lightning | 2013-11-27 14:25 | 2013-11-27 | 2013-11-27 16:07 | Calculated | TF810 | TF810 - Transformer Fuse: TF810 |  | 119SEG427-456 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 1 | 24552 | 102 | 0.00415 | 4.073e-05 | 15 | 1530 | 2013/2014 | November-2013 | 11 | 2013
29799 | Refer 2013/411 U/G Cable Alterations/Install Xaria Unit | 2013-11-27 17:08 | 2013-11-27 | 2013-11-29 13:40 | Calculated | 5831 | 5831 - Air Break Switch 5831 |  | 401SEG5967-5831 | Hakiaha 401-02 | Rural B | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 44 | 47 | 24552 | 2068 | 0.08423 | 0.0019143 | 600 | 26399 | 2013/2014 | November-2013 | 11 | 2013
29800 | Jumper Off | 2013-11-27 18:43 | 2013-11-27 | 2013-11-27 22:56 | Calculated | 5237 | 5237 - Sectionaliser 5237 |  | 426SEG5237-5892 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 253 | 40 | 24552 | 10120 | 0.41219 | 0.0016292 | 212.5 | 53762 | 2013/2014 | November-2013 | 11 | 2013
29802 | Lightning/DDO Faulty | 2013-11-27 20:31 | 2013-11-27 | 2013-11-28 03:29 | Calculated | TF940 | TF940 - Transformer Fuse: TF940 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 174 | 17 | 24552 | 1070 | 0.04358 | 0.00069241 | 243 | 14788 | 2013/2014 | November-2013 | 11 | 2013
29801 | Lightning | 2013-11-27 20:43 | 2013-11-27 | 2013-11-27 22:06 | Calculated | TF1988 | TF1988 - Transformer Fuse: TF1988 |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 1 | 24552 | 83 | 0.00338 | 4.073e-05 | 10 | 830 | 2013/2014 | November-2013 | 11 | 2013
29810 | Lightning | 2013-11-27 22:30 | 2013-11-27 | 2013-11-28 13:05 | Calculated | TF240 | TF240 - Transformer Fuse: TF240 |  | 129SEG477 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 875 | 1 | 24552 | 875 | 0.03564 | 4.073e-05 | 30 | 26250 | 2013/2014 | November-2013 | 11 | 2013
29804 | Lightning | 2013-11-28 07:12 | 2013-11-28 | 2013-11-28 08:22 | Calculated | TF21M2 | TF21M2 - Transformer Fuse: TF21M2 |  | 416SEG6118-5961 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 3 | 24552 | 210 | 0.00855 | 0.00012219 | 10 | 699 | 2013/2014 | November-2013 | 11 | 2013
29805 | Lightning | 2013-11-28 07:12 | 2013-11-28 | 2013-11-28 08:43 | Calculated | TF21M7 | TF21M7 - Transformer Fuse: TF21M7 |  | 416SEG5677-5681 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 1 | 24552 | 91 | 0.00371 | 4.073e-05 | 15 | 1365 | 2013/2014 | November-2013 | 11 | 2013
29806 | Refer 2013/415 Drop SWER Line For Treescape @ Link 5171 | 2013-11-28 08:52 | 2013-11-28 | 2013-11-28 15:40 | Calculated | 5777 | 5777 - Fused Link 5777 |  | 402SEG5797-5777 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 389 | 17 | 24552 | 2008 | 0.08179 | 0.00069241 | 132.5 | 18815 | 2013/2014 | November-2013 | 11 | 2013
29807 | Refer 2013/AL1255 LV U/G Cable Install | 2013-11-28 10:15 | 2013-11-28 | 2013-11-28 15:46 | Calculated | TF9E1 | TF9E1 - Transformer Fuse: TF9E1 |  | 413SEG5569-5437 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Underground | 11kV SWER | 9000 |  | 331 | 4 | 24552 | 1324 | 0.05393 | 0.00016292 | 30 | 9930 | 2013/2014 | November-2013 | 11 | 2013
29808 | Broken Staywire Tx 2880 | 2013-11-28 11:48 | 2013-11-28 | 2013-11-28 17:13 | Calculated | 1620 | 1620 - Recloser 1620 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:OIWAWD | Broken Stay Wire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 251 | 237 | 24552 | 48566 | 1.9781 | 0.009653 | 1631 | 335024 | 2013/2014 | November-2013 | 11 | 2013
29814 | Lightning | 2013-11-28 13:12 | 2013-11-28 | 2013-11-28 16:34 | Calculated | 5622 | 5622 - Fused Link 5622 |  | 403SEG5622-5368 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 202 | 25 | 24552 | 5050 | 0.20569 | 0.0010182 | 165 | 33329 | 2013/2014 | November-2013 | 11 | 2013
29809 | Earth Fault | 2013-11-28 15:00 | 2013-11-28 | 2013-11-28 15:04 | Calculated | 594 | 594 - Recloser 594 |  | No Segment | 205-01 Gadsby Road | Urban A | No Feeder |  |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 5 | 24552 | 5 | 0.0002 | 0.00020365 | 800 | 799 | 2013/2014 | November-2013 | 11 | 2013
29812 | Lightning | 2013-11-28 19:05 | 2013-11-28 | 2013-11-28 21:05 | Calculated | TF17H04 | TF17H04 - Transformer Fuse: TF17H04 |  | 410SEG5510-5511 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 120 | 6 | 24552 | 720 | 0.02933 | 0.00024438 | 10 | 1199 | 2013/2014 | November-2013 | 11 | 2013
29811 | Refer 2013/413 U/G Cabble Alterations/Install Xaria Unit - Connect Xaria Unit | 2013-11-28 20:13 | 2013-11-28 | 2013-11-29 00:20 | Calculated | 6723 | 6723 - Circuit Breaker 6723 |  | No Segment | No Asset Group | Remote Rural F | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 247 | 47 | 24552 | 5795 | 0.23603 | 0.0019143 | 600 | 96899 | 2013/2014 | November-2013 | 11 | 2013
29813 | FS 5986 Fuse Blown Again | 2013-11-28 22:01 | 2013-11-28 | 2013-11-29 00:35 | Calculated | 5986 | 5986 - Fused Link 5986 |  | 402SEG5986 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 29 | 24552 | 4466 | 0.1819 | 0.0011812 | 250 | 38499 | 2013/2014 | November-2013 | 11 | 2013
29815 | Trees | 2013-11-29 05:18 | 2013-11-29 | 2013-11-29 07:15 | Calculated | 1335 | 1335 - Sectionaliser 1335 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 117 | 17 | 24552 | 1989 | 0.08101 | 0.00069241 | 148 | 17316 | 2013/2014 | November-2013 | 11 | 2013
29816 | Birds | 2013-11-29 06:52 | 2013-11-29 | 2013-11-29 07:28 | Calculated | TF8K15 | TF8K15 - Transformer Fuse: TF8K15 |  | No Segment | Manunui 407-01 (was Affco) | Rural B | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 3 | 24552 | 108 | 0.0044 | 0.00012219 | 10 | 359 | 2013/2014 | November-2013 | 11 | 2013
29817 | Refer 2013/417 Replace Poles & X Arms | 2013-11-29 07:53 | 2013-11-29 | 2013-11-29 16:00 | Calculated | 337 | 337 - Air Break Switch 337 |  | 109SEG337-2229 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 347 | 63 | 24552 | 19446 | 0.79203 | 0.002566 | 605 | 192684 | 2013/2014 | November-2013 | 11 | 2013
29819 | Vehicle vs Line | 2013-11-29 09:43 | 2013-11-29 | 2013-11-29 15:22 | Calculated | 1310 | 1310 - Air Break Switch 1310 |  | 116SEG1310-1781 | Piopio 116-03 | Rural D | Piopio | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 207 | 14 | 24552 | 2898 | 0.11804 | 0.00057022 | 95 | 19665 | 2013/2014 | November-2013 | 11 | 2013
29818 | Refer 2013/A229 Replace L/V Fuses | 2013-11-29 10:02 | 2013-11-29 | 2013-11-29 11:13 | Calculated | TF9K19 | TF9K19 - Transformer Fuse: TF9K19 |  | 409SEG6159 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 10 | 24552 | 710 | 0.02892 | 0.0004073 | 50 | 3550 | 2013/2014 | November-2013 | 11 | 2013
29820 | HV Cable Fault | 2013-11-30 08:02 | 2013-11-30 | 2013-12-07 14:36 | Calculated | TF11S25 | TF11S25 - Transformer Fuse: TF11S25 |  | 424SEG5200-6650 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 558 | 38 | 24552 | 21204 | 0.86364 | 0.0015477 | 100 | 55799 | 2013/2014 | November-2013 | 11 | 2013
29822 | Birds | 2013-11-30 09:47 | 2013-11-30 | 2013-11-30 14:40 | Calculated | TF17I01 | TF17I01 - Transformer Fuse: TF17I01 |  | 410SEG5510-5511 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 293 | 1 | 24552 | 293 | 0.01193 | 4.073e-05 | 3 | 879 | 2013/2014 | November-2013 | 11 | 2013
29821 | Wind | 2013-11-30 12:57 | 2013-11-30 | 2013-12-02 15:55 | Calculated | 714 | 714 - Recloser with Bypass 714 |  | 103SEG598-714 | Benneydale 103-07 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 431 | 59 | 24552 | 13923 | 0.56708 | 0.0024031 | 1028 | 124414 | 2013/2014 | November-2013 | 11 | 2013
29824 | L/V Fault | 2013-11-30 13:00 | 2013-11-30 | 2013-11-30 16:13 | Calculated | TF547 | TF547 - Transformer Fuse: TF547 |  | 125SEG281-298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 19 | 24552 | 3667 | 0.14936 | 0.00077387 | 300 | 57899 | 2013/2014 | November-2013 | 11 | 2013
29823 | Unknown | 2013-11-30 15:08 | 2013-11-30 | 2013-11-30 15:11 | Calculated | 683 | 683 - Circuit Breaker 683 |  | No Segment | 207-01 Wairere Falls | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 459 | 24552 | 1377 | 0.05609 | 0.018695 | 3121 | 9362 | 2013/2014 | November-2013 | 11 | 2013
29827 | Wind | 2013-11-30 15:45 | 2013-11-30 | 2013-11-30 18:37 | Calculated | 1297 | 1297 - Fused Link 1297 |  | 117SEG1297-1296 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 72 | 24552 | 12384 | 0.5044 | 0.0029326 | 548 | 94256 | 2013/2014 | November-2013 | 11 | 2013
29828 | Wind | 2013-11-30 15:53 | 2013-11-30 | 2013-11-30 18:49 | Calculated | TF81 | TF81 - Transformer Fuse: TF81 |  | 101SEG1272-257 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 11 | 24552 | 1936 | 0.07885 | 0.00044803 | 75 | 13199 | 2013/2014 | November-2013 | 11 | 2013
29825 | Replace HV Fuses @ Tx1835 | 2013-11-30 16:16 | 2013-11-30 | 2013-11-30 17:27 | Calculated | 137 | 137 - Air Break Switch 137 |  | 125SEG281-298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 2 | 24552 | 142 | 0.00578 | 8.146e-05 | 15 | 1065 | 2013/2014 | November-2013 | 11 | 2013
29826 | Trees | 2013-11-30 17:11 | 2013-11-30 | 2013-11-30 19:47 | Calculated | 5623 | 5623 - Electronic Sectionaliser 5623 |  | 409SEG5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 156 | 15 | 24552 | 2340 | 0.09531 | 0.00061095 | 72.5 | 11310 | 2013/2014 | November-2013 | 11 | 2013
29829 | Wind | 2013-11-30 17:34 | 2013-11-30 | 2013-11-30 19:34 | Calculated | TF4J7 | TF4J7 - Transformer Fuse: TF4J7 |  | 421SEG5657-5473 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 120 | 2 | 24552 | 240 | 0.00978 | 8.146e-05 | 15 | 1800 | 2013/2014 | November-2013 | 11 | 2013
29830 | Birds | 2013-12-01 08:04 | 2013-12-01 | 2013-12-01 09:45 | Calculated | TF4E1 | TF4E1 - Transformer Fuse: TF4E1 |  | 422SEG5556-5753 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 101 | 2 | 24558 | 202 | 0.00823 | 8.144e-05 | 15 | 1515 | 2013/2014 | December-2013 | 12 | 2013
29831 | Possum | 2013-12-02 06:06 | 2013-12-02 | 2013-12-02 07:10 | Calculated | TF14I01 | TF14I01 - Transformer Fuse: TF14I01 |  | 410SEG5334-5745 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 64 | 2 | 24558 | 128 | 0.00521 | 8.144e-05 | 15 | 960 | 2013/2014 | December-2013 | 12 | 2013
29832 | Blown HV Fuse - Unknown Fault | 2013-12-02 12:59 | 2013-12-02 | 2013-12-02 14:05 | Calculated | TF11R03 | TF11R03 - Transformer Fuse: TF11R03 |  | 424SEG6657 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 1 | 24558 | 66 | 0.00269 | 4.072e-05 | 15 | 990 | 2013/2014 | December-2013 | 12 | 2013
29833 | Unknown | 2013-12-02 15:16 | 2013-12-02 | 2013-12-02 15:54 | Calculated | 5287 | 5287 - Recloser with Bypass & Links 5287 |  | 413SEG5288-5287 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 38 | 30 | 24558 | 1140 | 0.04642 | 0.0012216 | 203 | 7714 | 2013/2014 | December-2013 | 12 | 2013
29836 | Blown HV Fuse - Unknown Fault | 2013-12-03 07:44 | 2013-12-03 | 2013-12-03 09:56 | Calculated | TF249 | TF249 - Transformer Fuse: TF249 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 2 | 24558 | 264 | 0.01075 | 8.144e-05 | 30 | 3960 | 2013/2014 | December-2013 | 12 | 2013
29837 | Refer 2013/420 Replace Poles & X Arms | 2013-12-03 09:03 | 2013-12-03 | 2013-12-03 14:40 | Calculated | 508 | 508 - Air Break Switch 508 |  | 107SEG508-1798 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 337 | 16 | 24558 | 5392 | 0.21956 | 0.00065152 | 80 | 26959 | 2013/2014 | December-2013 | 12 | 2013
29838 | Refer 2013/419 Re-instate Jumpers, Move Link 5628, Install New Link @ Pole 71/21 | 2013-12-03 10:09 | 2013-12-03 | 2013-12-03 16:39 | Calculated | 5227 | 5227 - Fused Link 5227 |  | 412SEG5227-5269 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 390 | 22 | 24558 | 8510 | 0.34653 | 0.00089584 | 166 | 64160 | 2013/2014 | December-2013 | 12 | 2013
29839 | Old Age | 2013-12-03 11:48 | 2013-12-03 | 2013-12-03 15:04 | Calculated | TF9L14 | TF9L14 - Transformer Fuse: TF9L14 |  | 408SEG5241 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 196 | 3 | 24558 | 588 | 0.02394 | 0.00012216 | 15 | 2940 | 2013/2014 | December-2013 | 12 | 2013
29840 | Scrub Fire/ No Comms To Manunui | 2013-12-03 16:05 | 2013-12-03 | 2013-12-03 16:46 | Calculated | 5132 | 5132 - Circuit Breaker Manunui SF6 5132 |  | 409SEG5132-5900 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Third Party (includeds unauthorised contractors) | Fire | 3PAR:EFIR:EFIB | Fire (Not Electrical) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 611 | 24558 | 25051 | 1.0201 | 0.02488 | 4352.5 | 178452 | 2013/2014 | December-2013 | 12 | 2013
29841 | Fuse too Small | 2013-12-04 06:23 | 2013-12-04 | 2013-12-04 08:08 | Calculated | TF3319 | TF3319 - Transformer Fuse 3319 |  | 124SEG475-440 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 1 | 24558 | 105 | 0.00428 | 4.072e-05 | 100 | 10500 | 2013/2014 | December-2013 | 12 | 2013
29843 | Extend Earthing | 2013-12-04 10:43 | 2013-12-04 | 2013-12-04 12:03 | Calculated | TF1601 | TF1601 - Transformer Fuse: TF1601 |  | 128SEG1615-1624 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 80 | 3 | 24558 | 240 | 0.00977 | 0.00012216 | 15 | 1200 | 2013/2014 | December-2013 | 12 | 2013
29844 | Refer 2013/JG 1091 - LV Work | 2013-12-04 11:10 | 2013-12-04 | 2013-12-04 12:34 | Calculated | TO194 | TO194 - TAP OFF FUSES: T194 |  | 109SEG341-587 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 2 | 24558 | 168 | 0.00684 | 8.144e-05 | 0 | 0 | 2013/2014 | December-2013 | 12 | 2013
29845 | Jumper Off | 2013-12-04 14:28 | 2013-12-04 | 2013-12-04 16:51 | Calculated | TF543 | TF543 - Transformer Fuse: TF543 |  | 113SEG1505 | Mahoenui 113-01 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 4 | 24558 | 299 | 0.01218 | 0.00016288 | 55 | 4225 | 2013/2014 | December-2013 | 12 | 2013
29846 | Birds | 2013-12-05 08:41 | 2013-12-05 | 2013-12-05 09:49 | Calculated | TF1394 | TF1394 - Transformer Fuse: TF1394 |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 1 | 24558 | 68 | 0.00277 | 4.072e-05 | 15 | 1020 | 2013/2014 | December-2013 | 12 | 2013
29847 | Possum | 2013-12-05 08:59 | 2013-12-05 | 2013-12-05 10:10 | Calculated | TF798 | TF798 - Transformer Fuse: TF798 |  | 118SEG491-462 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 1 | 24558 | 71 | 0.00289 | 4.072e-05 | 30 | 2130 | 2013/2014 | December-2013 | 12 | 2013
29707 | Refer 2013/421 Replace Poles & X Arms | 2013-12-05 09:04 | 2013-12-05 | 2013-12-05 15:08 | Calculated | 246 | 246 - Fused Link 246 |  | 106SEG246-252 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 364 | 26 | 24558 | 9464 | 0.38537 | 0.0010587 | 152.5 | 55509 | 2013/2014 | December-2013 | 12 | 2013
29744 | Refer 2013/PTPS | 2013-12-05 09:20 | 2013-12-05 | 2013-12-05 15:05 | Calculated | TF44 | TF44 - Transformer Fuse: TF44 |  | 104SEG730-547 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 345 | 2 | 24558 | 690 | 0.0281 | 8.144e-05 | 15 | 5175 | 2013/2014 | December-2013 | 12 | 2013
29851 | Line Down | 2013-12-05 13:15 | 2013-12-05 | 2013-12-05 19:20 | Calculated | 1616 | 1616 - Sectionaliser with Bypass & Links 1616 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 365 | 16 | 24558 | 5840 | 0.2378 | 0.00065152 | 135 | 49275 | 2013/2014 | December-2013 | 12 | 2013
29848 | Birds | 2013-12-05 13:25 | 2013-12-05 | 2013-12-05 16:00 | Calculated | TF7J23 | TF7J23 - Transformer Fuse: TF7J23 |  | 402SEG5596-5930 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 155 | 1 | 24558 | 155 | 0.00631 | 4.072e-05 | 15 | 2325 | 2013/2014 | December-2013 | 12 | 2013
29850 | Trees | 2013-12-05 16:25 | 2013-12-05 | 2013-12-05 18:30 | Calculated | 5623 | 5623 - Electronic Sectionaliser 5623 |  | 409SEG5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 15 | 24558 | 1875 | 0.07635 | 0.0006108 | 72.5 | 9062 | 2013/2014 | December-2013 | 12 | 2013
29849 | Unknown | 2013-12-05 16:36 | 2013-12-05 | 2013-12-05 16:39 | Calculated | 5152 | 5152 - Circuit Breaker 5152 |  | 514SEG5152 | No Asset Group | Remote Rural F | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24558 |  | 0 | 0 |  |  | 2013/2014 | December-2013 | 12 | 2013
29852 | Trees | 2013-12-05 20:30 | 2013-12-05 | 2013-12-06 14:12 | Calculated | 669 | 669 - Recloser with Bypass & Links 669 |  | 103SEG REG14-669 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1020 | 340 | 24558 | 40252 | 1.6391 | 0.013845 | 4619.5 | 434227 | 2013/2014 | December-2013 | 12 | 2013
29853 | Trees | 2013-12-06 05:41 | 2013-12-06 | 2013-12-06 08:09 | Calculated | 5623 | 5623 - Electronic Sectionaliser 5623 |  | 409SEG5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 15 | 24558 | 2220 | 0.0904 | 0.0006108 | 72.5 | 10730 | 2013/2014 | December-2013 | 12 | 2013
29854 | Refer 2013/61213B | 2013-12-06 09:15 | 2013-12-06 | 2013-12-06 13:17 | Calculated | TF644 | TF644 - Transformer Fuse: TF644 |  | 108SEG501-211 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 242 | 39 | 24558 | 9438 | 0.38431 | 0.0015881 | 200 | 48399 | 2013/2014 | December-2013 | 12 | 2013
29855 | Burnt Pole | 2013-12-06 21:36 | 2013-12-06 | 2013-12-07 05:04 | Calculated | 2092 | 2092 - Circuit Breaker Maraetai 11 kV 2092 |  | No Segment | 210-01 Maraetai | Rural D | No Feeder |  |  | Asset Related | Pole | FAIL:FPOL2:FPOF | Pole Top Fire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 214 | 167 | 24558 | 10876 | 0.44287 | 0.0068002 | 4401 | 323678 | 2013/2014 | December-2013 | 12 | 2013
29856 | Faulty DDO | 2013-12-07 07:09 | 2013-12-07 | 2013-12-07 08:09 | Calculated | TF2652 | TF2652 - Transformer Fuse: TF2652 |  | 110SEG189 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 3 | 24558 | 180 | 0.00733 | 0.00012216 | 15 | 900 | 2013/2014 | December-2013 | 12 | 2013
29857 | Wind | 2013-12-07 12:48 | 2013-12-07 | 2013-12-07 12:58 | Calculated | 5990 | 5990 - Recloser 5990 |  | 419SEG5990-5991 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 40 | 24558 | 400 | 0.01629 | 0.0016288 | 8350 | 83500 | 2013/2014 | December-2013 | 12 | 2013
29858 | Birds | 2013-12-07 13:50 | 2013-12-07 | 2013-12-07 15:41 | Calculated | TF8Q4 | TF8Q4 - Transformer Fuse: TF8Q4 |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 1 | 24558 | 111 | 0.00452 | 4.072e-05 | 5 | 555 | 2013/2014 | December-2013 | 12 | 2013
29859 | Rat | 2013-12-07 19:09 | 2013-12-07 | 2013-12-07 20:08 | Calculated | TF12S4 | TF12S4 - Transformer Fuse: TF12S4 |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AVER | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 1 | 24558 | 59 | 0.0024 | 4.072e-05 | 7.5 | 442 | 2013/2014 | December-2013 | 12 | 2013
29860 | Blown HV Fuse - Unknown Fault | 2013-12-08 17:55 | 2013-12-08 | 2013-12-08 19:25 | Calculated | TF2092 | TF2092 - Transformer Fuse: TF2092 |  | 103SEG1325 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 90 | 3 | 24558 | 270 | 0.01099 | 0.00012216 | 15 | 1350 | 2013/2014 | December-2013 | 12 | 2013
29862 | Refer 2013/AL335 - Replace Tx | 2013-12-09 09:10 | 2013-12-09 | 2013-12-09 11:14 | Calculated | TF9K18 | TF9K18 - Transformer Fuse: TF9K18 |  | 409SEG5778 | Southern 409-03 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 124 | 5 | 24558 | 620 | 0.02525 | 0.0002036 | 15 | 1860 | 2013/2014 | December-2013 | 12 | 2013
29863 | Refer 2013/AL0004D Straighten & Fix Tx Arms | 2013-12-09 09:17 | 2013-12-09 | 2013-12-09 11:52 | Calculated | 5739 | 5739 - Sectionaliser with Bypass & Links 5739 |  | 421SEG5436-5434 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 155 | 2 | 24558 | 310 | 0.01262 | 8.144e-05 | 3 | 465 | 2013/2014 | December-2013 | 12 | 2013
29835 | Jumper Off @ Tx 5H01 | 2013-12-09 12:33 | 2013-12-09 | 2013-12-09 17:29 | Calculated | 5824 | 5824 - Circuit Breaker 5824 |  | 422SEG5824-5825 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 296 | 148 | 24558 | 4469 | 0.18198 | 0.0060265 | 955.5 | 30193 | 2013/2014 | December-2013 | 12 | 2013
29864 | Old Age | 2013-12-10 06:18 | 2013-12-10 | 2013-12-10 07:58 | Calculated | TF2472 | TF2472 - Transformer Fuse: TF2472 |  | 120SEG745 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 1 | 24558 | 100 | 0.00407 | 4.072e-05 | 10 | 1000 | 2013/2014 | December-2013 | 12 | 2013
29865 | Refer 2013/425 Replace Sectionalizers @1612, 1615, 1616 Plus Pole. Replace Poles. Helicopter & Taumarunui Crews to Assist | 2013-12-10 09:03 | 2013-12-10 | 2013-12-10 16:01 | Calculated | 1611 | 1611 - Fused Link 1611 |  | 128SEG1610-1611 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 418 | 50 | 24558 | 19236 | 0.78329 | 0.002036 | 387.5 | 155735 | 2013/2014 | December-2013 | 12 | 2013
29866 | Refer 2013/PTPS 1162A 11kV Extension | 2013-12-11 10:12 | 2013-12-11 | 2013-12-11 15:25 | Calculated | TF282 | TF282 - Transformer Fuse: TF282 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 313 | 4 | 24558 | 1252 | 0.05098 | 0.00016288 | 30 | 9390 | 2013/2014 | December-2013 | 12 | 2013
29867 | Old Age | 2013-12-11 10:35 | 2013-12-11 | 2013-12-11 13:27 | Calculated | TF1607 | TF1607 - Transformer Fuse: TF1607 |  | 113SEG1533-1534 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 172 | 2 | 24558 | 344 | 0.01401 | 8.144e-05 | 7.5 | 1290 | 2013/2014 | December-2013 | 12 | 2013
29868 | Vehicle vs Line | 2013-12-12 05:43 | 2013-12-12 | 2013-12-12 10:57 | Calculated | 474 | 474 - Recloser 474 |  | 123SEG441-474 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 314 | 125 | 24558 | 14860 | 0.6051 | 0.00509 | 1783 | 271788 | 2013/2014 | December-2013 | 12 | 2013
29869 | Refer 2013/423 Replacing Poles & X Arms | 2013-12-12 09:12 | 2013-12-12 | 2013-12-12 14:55 | Calculated | 252 | 252 - Fused Link 252 |  | 106SEG252-803 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 343 | 10 | 24558 | 3430 | 0.13967 | 0.0004072 | 50 | 17150 | 2013/2014 | December-2013 | 12 | 2013
29871 | Old Age | 2013-12-12 09:53 | 2013-12-12 | 2013-12-12 11:23 | Calculated | TF10E07 | TF10E07 - Transformer Fuse: TF10E07 |  | 413SEG5308-5794 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 90 | 2 | 24558 | 180 | 0.00733 | 8.144e-05 | 15 | 1350 | 2013/2014 | December-2013 | 12 | 2013
29870 | Refer 2013/PTPS 1162A | 2013-12-12 10:00 | 2013-12-12 | 2013-12-12 13:03 | Calculated | TF282 | TF282 - Transformer Fuse: TF282 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 183 | 4 | 24558 | 732 | 0.02981 | 0.00016288 | 30 | 5490 | 2013/2014 | December-2013 | 12 | 2013
29872 | Helicopter vs Line | 2013-12-12 13:31 | 2013-12-12 | 2013-12-12 16:53 | Calculated | TF230 | TF230 - Transformer Fuse: TF230 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 202 | 6 | 24558 | 1212 | 0.04935 | 0.00024432 | 30 | 6060 | 2013/2014 | December-2013 | 12 | 2013
29875 | Refer 2013/447 Replace Poles & X Arms | 2013-12-13 09:03 | 2013-12-13 | 2013-12-13 16:00 | Calculated | 239 | 239 - Fused Link 239 |  | 107SEG239-508 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 417 | 35 | 24558 | 14595 | 0.59431 | 0.0014252 | 210 | 87569 | 2013/2014 | December-2013 | 12 | 2013
29877 | Refer 2013/440 Install Generator Insertion Point @ Tx 16N22 | 2013-12-13 10:33 | 2013-12-13 | 2013-12-13 12:50 | Calculated | 6338 | 6338 - Load Break Switch 6338 |  | 419SEG6338-6339 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 137 | 39 | 24558 | 5324 | 0.21679 | 0.0015881 | 1640 | 223904 | 2013/2014 | December-2013 | 12 | 2013
29873 | Magpie | 2013-12-14 07:28 | 2013-12-14 | 2013-12-14 10:01 | Calculated | 5107 | 5107 - Recloser with Bypass & Links 5107 |  | 422SEG05F14-5107 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 153 | 61 | 24558 | 8070 | 0.32861 | 0.0024839 | 439 | 57851 | 2013/2014 | December-2013 | 12 | 2013
29878 | Blown HV Fuse - Unknown Fault | 2013-12-15 01:15 | 2013-12-15 | 2013-12-15 04:14 | Calculated | TF13L4 | TF13L4 - Transformer Fuse: TF13L4 |  | 410SEG5139-5829 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 4 | 24558 | 716 | 0.02916 | 0.00016288 | 30 | 5370 | 2013/2014 | December-2013 | 12 | 2013
29879 | O/C IDMT | 2013-12-15 05:21 | 2013-12-15 | 2013-12-15 05:24 | Calculated | 123 | 123 - Circuit Breaker 123 |  | No Segment | 203-01 Te Waireka Road | Urban A | No Feeder |  |  | Asset Related | Other | FAIL:FOLD:FOLS | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 1150 | 24558 | 3450 | 0.14048 | 0.046828 | 7483 | 22448 | 2013/2014 | December-2013 | 12 | 2013
29880 | Unknown | 2013-12-16 06:34 | 2013-12-16 | 2013-12-16 11:10 | Calculated | 1724 | 1724 - Sectionaliser with Bypass & LInks 1724 |  | 115SEG1723-1724 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 276 | 14 | 24558 | 2787 | 0.11349 | 0.00057008 | 128 | 27486 | 2013/2014 | December-2013 | 12 | 2013
29883 | Unknown/Helicopter Patrol | 2013-12-18 00:31 | 2013-12-18 | 2013-12-18 08:14 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24558 |  | 0 | 0 |  |  | 2013/2014 | December-2013 | 12 | 2013
29884 | Refer 2013/442 Replace Poles & X Arms | 2013-12-18 09:06 | 2013-12-18 | 2013-12-18 15:36 | Calculated | 246 | 246 - Fused Link 246 |  | 106SEG246-252 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 390 | 26 | 24558 | 10140 | 0.4129 | 0.0010587 | 152.5 | 59474 | 2013/2014 | December-2013 | 12 | 2013
29885 | Broken X Arm Tree On Line | 2013-12-18 09:30 | 2013-12-18 | 2013-12-18 14:15 | Calculated | 1117 | 1117 - Air Break Swtich 1117 |  | 114SEG1107-1116 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 285 | 36 | 24558 | 4485 | 0.18263 | 0.0014659 | 280 | 36075 | 2013/2014 | December-2013 | 12 | 2013
29886 | Refer 2013/449 Re-Install Tx513T1 & Regonfigure U/G Cable Into Xiria @ Tawhia Sub | 2013-12-18 16:29 | 2013-12-18 | 2013-12-18 16:33 | Calculated | 5271 | 5271 - Load Break Switch 5271 |  | 419SEG5271-6697 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 4 | 130 | 24558 | 454 | 0.01849 | 0.0052936 | 11965 | 38944 | 2013/2014 | December-2013 | 12 | 2013
29882 | Jumper Off | 2013-12-19 09:00 | 2013-12-19 | 2013-12-19 12:38 | Calculated | TF90 | TF90 - Transformer Fuse: TF90 |  | 102SEG340-191 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 197 | 9 | 24558 | 1101 | 0.04483 | 0.00036648 | 75 | 9174 | 2013/2014 | December-2013 | 12 | 2013
29887 | Birds | 2013-12-19 10:45 | 2013-12-19 | 2013-12-19 12:54 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 129 | 34 | 24558 | 2934 | 0.11947 | 0.0013845 | 208.5 | 15940 | 2013/2014 | December-2013 | 12 | 2013
29888 | Cable Fault/Northpower Job | 2013-12-19 22:58 | 2013-12-19 | 2013-12-23 19:33 | Calculated | 5880 | 5880 - Circuit Breaker Hakiaha 5880 |  | No Segment | 508-01 Borough | Rural B | No Feeder |  |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 93 | 294 | 24558 | 16897 | 0.68804 | 0.011972 | 3780 | 232159 | 2013/2014 | December-2013 | 12 | 2013
29889 | Faulty Insulator | 2013-12-20 06:41 | 2013-12-20 | 2013-12-20 09:06 | Calculated | 263 | 263 - Fused Link 263 |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 3 | 24558 | 435 | 0.01771 | 0.00012216 | 15 | 2175 | 2013/2014 | December-2013 | 12 | 2013
29890 | L/V Maintenance Replace LV X Arms | 2013-12-20 09:04 | 2013-12-20 | 2013-12-20 13:49 | Calculated | TF1500 | TF1500 - Transformer Fuse: TF1500 |  | 108SEG501-211 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 285 | 11 | 24558 | 3135 | 0.12766 | 0.00044792 | 50 | 14249 | 2013/2014 | December-2013 | 12 | 2013
29891 | Refer 2013/448 Replace Leaky Tx 08J09 & Fit New HV Fuses On Structure | 2013-12-20 10:04 | 2013-12-20 | 2013-12-20 13:04 | Calculated | 5229 | 5229 - Fused Link 5229 |  | 404SEG5229 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 180 | 2 | 24558 | 360 | 0.01466 | 8.144e-05 | 30 | 5400 | 2013/2014 | December-2013 | 12 | 2013
29892 | Blown HV Fuse - Unknown Fault | 2013-12-21 10:09 | 2013-12-21 | 2013-12-21 12:09 | Calculated | TF849 | TF849 - Transformer Fuse: TF849 |  | 121SEG724-REG32 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 2 | 24558 | 240 | 0.00977 | 8.144e-05 | 10 | 1200 | 2013/2014 | December-2013 | 12 | 2013
29893 | Jumper Off | 2013-12-21 21:44 | 2013-12-21 | 2013-12-22 00:11 | Calculated | TF20L41 | TF20L41 - Transformer Fuse: TF20L41 |  | 414SEG6644-5643 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 61 | 24558 | 8967 | 0.36514 | 0.0024839 | 200 | 29399 | 2013/2014 | December-2013 | 12 | 2013
29896 | Blown HV Tap off Fuse - Unknown Fault | 2013-12-22 16:49 | 2013-12-22 | 2013-12-23 10:53 | Calculated | TO07D10 | TO07D10 - TAP OFF FUSE : TO07D10 |  | 413SEG5287-5572 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1084 | 1 | 24558 | 1084 | 0.04414 | 4.072e-05 | 5 | 5420 | 2013/2014 | December-2013 | 12 | 2013
29894 | Pukeko | 2013-12-23 06:18 | 2013-12-23 | 2013-12-23 08:00 | Calculated | TF526 | TF526 - Transformer Fuse: TF526 |  | 112SEG331-355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 1 | 24558 | 102 | 0.00415 | 4.072e-05 | 25 | 2550 | 2013/2014 | December-2013 | 12 | 2013
29895 | Unknown | 2013-12-23 06:28 | 2013-12-23 | 2013-12-23 09:11 | Calculated | 1352 | 1352 - Fused Link 1352 |  | 110SEG1352 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 5 | 24558 | 815 | 0.03319 | 0.0002036 | 55 | 8965 | 2013/2014 | December-2013 | 12 | 2013
29898 | Refer 2013/455 Replace 11kV Pole About to Slip into River | 2013-12-23 10:08 | 2013-12-23 | 2013-12-23 12:51 | Calculated | 1605 | 1605 - Fused Link 1605 |  | 128SEG1605-1607 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 163 | 59 | 24558 | 9617 | 0.3916 | 0.0024025 | 455.5 | 74246 | 2013/2014 | December-2013 | 12 | 2013
29899 | Tree Through Line | 2013-12-23 16:51 | 2013-12-23 | 2013-12-23 20:06 | Calculated | 5164 | 5164 - Recloser with Bypass 5164 |  | 402SEG5164-5923 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 195 | 186 | 24558 | 36270 | 1.4769 | 0.0075739 | 1397.5 | 272512 | 2013/2014 | December-2013 | 12 | 2013
29900 | P/L Line Down | 2013-12-23 18:50 | 2013-12-23 | 2013-12-24 09:18 | Calculated | TF236 | TF236 - Transformer Fuse: TF236 |  | 111SEG342-544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 868 | 7 | 24558 | 6076 | 0.24741 | 0.00028504 | 30 | 26039 | 2013/2014 | December-2013 | 12 | 2013
29901 | Jumper Off | 2013-12-24 10:48 | 2013-12-24 | 2013-12-24 12:41 | Calculated | TF2009 | TF2009 - Transformer Fuse: TF2009 |  | 115SEG1701-1710 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 2 | 24558 | 226 | 0.0092 | 8.144e-05 | 15 | 1695 | 2013/2014 | December-2013 | 12 | 2013
29902 | Faulty DDO @ Tx 242 | 2013-12-25 07:18 | 2013-12-25 | 2013-12-25 11:49 | Calculated | TF242 | TF242 - Transformer Fuse: TF242 |  | 111SEG339-346 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 49 | 24558 | 2318 | 0.09439 | 0.0019953 | 530 | 24939 | 2013/2014 | December-2013 | 12 | 2013
29903 | Unknown | 2013-12-26 03:18 | 2013-12-26 | 2013-12-26 05:11 | Calculated | 6018 | 6018 - Solid Link 6018 |  | 406SEG6018-5009 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 13 | 24558 | 1469 | 0.05982 | 0.00052936 | 400 | 45200 | 2013/2014 | December-2013 | 12 | 2013
29904 | Lightning | 2013-12-26 16:43 | 2013-12-26 | 2013-12-26 17:52 | Calculated | 1528 | 1528 - Fused Link 1528 |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 12 | 24558 | 828 | 0.03372 | 0.00048864 | 58 | 4001 | 2013/2014 | December-2013 | 12 | 2013
29906 | Bus Fault @ RMU 5974 | 2013-12-27 01:32 | 2013-12-27 | 2013-12-27 14:30 | Calculated | 5990 | 5990 - Recloser 5990 |  | 419SEG5990-5991 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 760 | 50 | 24558 | 12959 | 0.52769 | 0.002036 | 8950 | 1736450 | 2013/2014 | December-2013 | 12 | 2013
29907 | Faulty Tx | 2013-12-27 13:10 | 2013-12-27 | 2013-12-27 18:39 | Calculated | TF428 | TF428 - Transformer Fuse: TF428 |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 329 | 2 | 24558 | 658 | 0.02679 | 8.144e-05 | 25 | 8225 | 2013/2014 | December-2013 | 12 | 2013
29908 | Lightning | 2013-12-29 13:06 | 2013-12-29 | 2013-12-29 13:08 | Calculated | 2092 | 2092 - Circuit Breaker Maraetai 11 kV 2092 |  | No Segment | 210-01 Maraetai | Rural D | No Feeder |  |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 167 | 24558 | 334 | 0.0136 | 0.0068002 | 4401 | 8801 | 2013/2014 | December-2013 | 12 | 2013
29909 | Lightning | 2013-12-29 17:46 | 2013-12-29 | 2013-12-29 19:46 | Calculated | TF4E1 | TF4E1 - Transformer Fuse: TF4E1 |  | 422SEG5556-5753 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 120 | 2 | 24558 | 240 | 0.00977 | 8.144e-05 | 15 | 1800 | 2013/2014 | December-2013 | 12 | 2013
29910 | Lightning | 2013-12-29 18:14 | 2013-12-29 | 2013-12-29 18:30 | Calculated | TPN/Park 232 | TPN/Park 232 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 516-01 Transpower National Park | Rural D | No Feeder |  |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 244 | 24558 | 2440 | 0.09936 | 0.0099357 | 13141 | 131409 | 2013/2014 | December-2013 | 12 | 2013
29911 | Lightning | 2013-12-29 18:33 | 2013-12-29 | 2013-12-29 20:19 | Calculated | TF4180 | TF4180 - Transformer Fuse: TF4180 |  | 406SEG6022 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 1 | 24558 | 106 | 0.00432 | 4.072e-05 | 15 | 1590 | 2013/2014 | December-2013 | 12 | 2013
29912 | Line Down @ Poles 96 - 97 and Faulty Insulator - Shot At | 2013-12-29 22:58 | 2013-12-29 | 2013-12-30 12:44 | Calculated | TPN/Park 232 | TPN/Park 232 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 516-01 Transpower National Park | Rural D | No Feeder |  |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUV | Wilful Damage or Interference | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 755 | 248 | 24558 | 39383 | 1.6037 | 0.010099 | 13591 | 505015 | 2013/2014 | December-2013 | 12 | 2013
29914 | Blown HV Fuse - Unknown Fault | 2013-12-30 08:59 | 2013-12-30 | 2013-12-30 10:48 | Calculated | TF154 | TF154 - Transformer Fuse: TF154 |  | 116SEG1334-269 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Switch-gear | CANT3:CANT2:CANT1 | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 3 | 24558 | 327 | 0.01332 | 0.00012216 | 25 | 2724 | 2013/2014 | December-2013 | 12 | 2013
29915 | Tree Through Line | 2013-12-30 16:43 | 2013-12-30 | 2013-12-31 12:00 | Calculated | 411 | 411 - Recloser with Bypass & Links 411 |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 964 | 167 | 24558 | 42018 | 1.711 | 0.0068002 | 4401 | 537215 | 2013/2014 | December-2013 | 12 | 2013
29913 | Unknown | 2013-12-31 10:34 | 2013-12-31 | 2013-12-31 10:41 | Calculated | 1620 | 1620 - Recloser 1620 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 237 | 24558 | 1659 | 0.06755 | 0.0096506 | 1631 | 11416 | 2013/2014 | December-2013 | 12 | 2013
29916 | Blown HV Fuses | 2014-01-01 17:13 | 2014-01-01 | 2014-01-01 20:43 | Calculated | 5241 | 5241 - Fused Link 5241 |  | 408SEG5241 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 210 | 7 | 24558 | 1470 | 0.05986 | 0.00028504 | 45 | 9450 | 2013/2014 | January-2014 | 1 | 2014
29917 | Line Down - Found big tree through line | 2014-01-01 19:53 | 2014-01-01 | 2014-01-02 01:22 | Calculated | 1725 | 1725 - Fused Link 1725 |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 329 | 5 | 24558 | 1910 | 0.07778 | 0.0002036 | 60 | 22920 | 2013/2014 | January-2014 | 1 | 2014
29918 | Birds - Found dead bird | 2014-01-02 07:40 | 2014-01-02 | 2014-01-02 09:15 | Calculated | TF8V2 | TF8V2 - Transformer Fuse: TF8V2 |  | 417SEG5905 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 9 | 24558 | 855 | 0.03482 | 0.00036648 | 30 | 2849 | 2013/2014 | January-2014 | 1 | 2014
29919 | Blown HV Fuses | 2014-01-02 09:19 | 2014-01-02 | 2014-01-02 11:29 | Calculated | TF07R10 | TF07R10 - Transformer Fuse: TF7R10 |  | 426SEG5110-5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 2 | 24558 | 260 | 0.01059 | 8.144e-05 | 7.5 | 975 | 2013/2014 | January-2014 | 1 | 2014
29925 | LV Line Down | 2014-01-03 13:01 | 2014-01-03 | 2014-01-03 17:31 | Calculated | TF9K50 | TF9K50 - Transformer Fuse: TF9K50 |  | 409SEG5920-5383 | Southern 409-02 | Rural D | Southern | Manunui Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFPL | Fault on Private Line - Affecting Network | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 270 | 20 | 24558 | 5400 | 0.21989 | 0.0008144 | 100 | 27000 | 2013/2014 | January-2014 | 1 | 2014
29920 | Jumper Off | 2014-01-03 13:45 | 2014-01-03 | 2014-01-03 18:19 | Calculated | 5932 | 5932 - Earth Working Link 5932 |  | 403SEG5932-5649 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 274 | 8 | 24558 | 2192 | 0.08926 | 0.00032576 | 55 | 15070 | 2013/2014 | January-2014 | 1 | 2014
29921 | Blown HV Fuses | 2014-01-03 13:56 | 2014-01-03 | 2014-01-03 15:40 | Calculated | 5170 | 5170 - Electronic Sectionaliser 5170 |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 104 | 21 | 24558 | 2184 | 0.08893 | 0.00085512 | 188 | 19551 | 2013/2014 | January-2014 | 1 | 2014
29924 | Pole fuse hanging out - Old Age | 2014-01-03 14:03 | 2014-01-03 | 2014-01-03 16:41 | Calculated | TF10K08 | TF10K08 - Transformer Fuse: TF10K08 |  | 409SEG5411-5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 2 | 24558 | 316 | 0.01287 | 8.144e-05 | 15 | 2370 | 2013/2014 | January-2014 | 1 | 2014
29923 | Tree on line - Branch on line at T09R02 | 2014-01-03 14:12 | 2014-01-03 | 2014-01-03 17:30 | Calculated | 6025 | 6025 - Recloser 6025 |  | 406SEG6645-T4282 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 20 | 24558 | 3278 | 0.13348 | 0.0008144 | 135 | 23940 | 2013/2014 | January-2014 | 1 | 2014
29922 | Line Down - Trees on line burning | 2014-01-03 15:03 | 2014-01-03 | 2014-01-03 16:34 | Calculated | 468 | 468 - Fused Link 468 |  | 123SEG468 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 27 | 24558 | 2457 | 0.10005 | 0.0010994 | 275 | 25025 | 2013/2014 | January-2014 | 1 | 2014
29926 | Replace DDO's at Transformer | 2014-01-04 10:08 | 2014-01-04 | 2014-01-04 13:00 | Calculated | 5311 | 5311 - Air Break Switch 5311 |  | 409SEG5311-5452 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 95 | 24558 | 7970 | 0.32454 | 0.0038684 | 450 | 38249 | 2013/2014 | January-2014 | 1 | 2014
29927 | Birds - Found dead pigeon on cross arm and jumper | 2014-01-06 06:49 | 2014-01-06 | 2014-01-06 11:25 | Calculated | 5792 | 5792 - Electronic Sectionaliser 5792 |  | 421SEG5792-5356 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 276 | 46 | 24558 | 4743 | 0.19313 | 0.0018731 | 333 | 31007 | 2013/2014 | January-2014 | 1 | 2014
29928 | Unknown - Earth Fault | 2014-01-06 23:56 | 2014-01-06 | 2014-01-07 00:23 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 323 | 24558 | 1292 | 0.05261 | 0.013153 | 2506 | 10023 | 2013/2014 | January-2014 | 1 | 2014
29930 | Jumper Off | 2014-01-07 09:22 | 2014-01-07 | 2014-01-07 10:19 | Calculated | 6740 | 6740 - Fused Link 6740 |  | 409SEG6740 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 5 | 24558 | 285 | 0.01161 | 0.0002036 | 68 | 3876 | 2013/2014 | January-2014 | 1 | 2014
29931 | Faulty L/A | 2014-01-07 09:24 | 2014-01-07 | 2014-01-07 15:12 | Calculated | TO09H05 | TO09H05 - Tap-off Fuse 09H05 |  | 403SEG5602-5317 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 348 | 3 | 24558 | 1044 | 0.04251 | 0.00012216 | 15 | 5220 | 2013/2014 | January-2014 | 1 | 2014
29932 | Refer 2014/1 Install New Pole & 11kV Cable For Transpower | 2014-01-07 09:34 | 2014-01-07 | 2014-01-07 10:36 | Calculated | 482 | 482 - Air Break Switch 482 |  | 120SEG482-480 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 62 | 11 | 24558 | 682 | 0.02777 | 0.00044792 | 200 | 12399 | 2013/2014 | January-2014 | 1 | 2014
29933 | Refer 2014/5 Replace Poles & X Arms | 2014-01-07 10:24 | 2014-01-07 | 2014-01-07 15:39 | Calculated | 337 | 337 - Air Break Switch 337 |  | 109SEG337-2229 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 29 | 24558 | 7560 | 0.30784 | 0.0011809 | 335 | 78064 | 2013/2014 | January-2014 | 1 | 2014
29934 | Blown HV Fuses | 2014-01-08 06:46 | 2014-01-08 | 2014-01-08 07:39 | Calculated | TF1350 | TF1350 - Transformer Fuse: TF1350 |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 2 | 24558 | 106 | 0.00432 | 8.144e-05 | 30 | 1590 | 2013/2014 | January-2014 | 1 | 2014
29936 | Refer 2014/6 Repot Pole 4121095 & Fit New L/A's to Tx 6E3 | 2014-01-08 10:01 | 2014-01-08 | 2014-01-08 12:37 | Calculated | 5261 | 5261 - Air Break Switch 5261 |  | 412SEG5261 | Nihoniho 412-01 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 156 | 3 | 24558 | 468 | 0.01906 | 0.00012216 | 20 | 3120 | 2013/2014 | January-2014 | 1 | 2014
29935 | Wind/Wire Off Insulator | 2014-01-08 13:47 | 2014-01-08 | 2014-01-08 17:15 | Calculated | 5385 | 5385 - Recloser with Bypass 5385 |  | 408SEG5388-5385 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 208 | 178 | 24558 | 21504 | 0.87564 | 0.0072481 | 1345 | 162389 | 2013/2014 | January-2014 | 1 | 2014
29938 | Refer 2014/7 Replace Poles & X Arms | 2014-01-09 08:08 | 2014-01-09 | 2014-01-09 14:36 | Calculated | 337 | 337 - Air Break Switch 337 |  | 109SEG337-2229 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 312 | 16 | 24558 | 4992 | 0.20327 | 0.00065152 | 195 | 60839 | 2013/2014 | January-2014 | 1 | 2014
29929 | Unknown | 2014-01-09 09:02 | 2014-01-09 | 2014-01-09 09:10 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 6 | 1196 | 24558 | 4792 | 0.19513 | 0.048701 | 9458.5 | 38733 | 2013/2014 | January-2014 | 1 | 2014
29937 | Refer 2014/2 Change Poles & X Arms | 2014-01-09 09:05 | 2014-01-09 | 2014-01-09 14:57 | Calculated | 246 | 246 - Fused Link 246 |  | 106SEG246-252 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 352 | 26 | 24558 | 9152 | 0.37267 | 0.0010587 | 152.5 | 53679 | 2013/2014 | January-2014 | 1 | 2014
29939 | Unknown | 2014-01-09 11:24 | 2014-01-09 | 2014-01-09 13:40 | Calculated | 5407 | 5407 - Sectionaliser with Bypass 5407 |  | 410SEG5407-5433 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 136 | 40 | 24558 | 5440 | 0.22152 | 0.0016288 | 254.5 | 34611 | 2013/2014 | January-2014 | 1 | 2014
29940 | Lightning | 2014-01-09 17:15 | 2014-01-09 | 2014-01-09 17:18 | Calculated | 796 | 796 - Circuit Breaker 796 |  | 301SEG1418-796 | Taharoa A 301-02 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 442 | 24558 | 1326 | 0.05399 | 0.017998 | 5794 | 17381 | 2013/2014 | January-2014 | 1 | 2014
29941 | Lightning - Replaced blown fuse after lightning strike | 2014-01-09 18:23 | 2014-01-09 | 2014-01-09 19:55 | Calculated | TF1876 | TF1876 - Transformer Fuse: TF1876 |  | 128SEG1261 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 2 | 24558 | 184 | 0.00749 | 8.144e-05 | 10 | 920 | 2013/2014 | January-2014 | 1 | 2014
29942 | Lightning - Pole fuse blown in lightning strike | 2014-01-09 20:30 | 2014-01-09 | 2014-01-09 22:02 | Calculated | TF6S2 | TF6S2 - Transformer Fuse: TF6S2 |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 1 | 24558 | 92 | 0.00375 | 4.072e-05 | 10 | 920 | 2013/2014 | January-2014 | 1 | 2014
29943 | Faulty Isolating Tx | 2014-01-10 07:38 | 2014-01-10 | 2014-01-10 16:25 | Calculated | 5820 | 5820 - Circuit Breaker 5820 |  | 421SEG5820-5821 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 262 | 24558 | 25251 | 1.0282 | 0.010669 | 1927 | 185910 | 2013/2014 | January-2014 | 1 | 2014
29947 | Faulty Insulator | 2014-01-10 08:12 | 2014-01-10 | 2014-01-10 15:52 | Calculated | 5851 | 5851 - Electronic Sectionaliser 5851 |  | 421SEG5851-5435 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 460 | 15 | 24558 | 6900 | 0.28097 | 0.0006108 | 105 | 48300 | 2013/2014 | January-2014 | 1 | 2014
29944 | Refer 202014/3 Change X Arms, Poles & Tx | 2014-01-10 09:02 | 2014-01-10 | 2014-01-10 15:07 | Calculated | 239 | 239 - Fused Link 239 |  | 107SEG239-508 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 365 | 35 | 24558 | 12775 | 0.5202 | 0.0014252 | 210 | 76649 | 2013/2014 | January-2014 | 1 | 2014
29945 | Faulty Insulator | 2014-01-10 09:45 | 2014-01-10 | 2014-01-10 12:02 | Calculated | 5159 | 5159 - Air Break Switch 5159 |  | 609SEG5158-5159 | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 109 | 7 | 24558 | 763 | 0.03107 | 0.00028504 | 55 | 5995 | 2013/2014 | January-2014 | 1 | 2014
29946 | Lightning | 2014-01-10 12:27 | 2014-01-10 | 2014-01-10 14:04 | Calculated | 696 | 696 - Fused Link 696 |  | 123SEG696 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 2 | 24558 | 194 | 0.0079 | 8.144e-05 | 40 | 3880 | 2013/2014 | January-2014 | 1 | 2014
29948 | Lightning - HV fuse blown by lightning strike | 2014-01-10 12:55 | 2014-01-10 | 2014-01-10 14:04 | Calculated | TF2493 | TF2493 - Transformer Fuse: TF2493 |  | 113SEG1336-1337 | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 1 | 24558 | 69 | 0.00281 | 4.072e-05 | 5 | 345 | 2013/2014 | January-2014 | 1 | 2014
29949 | Lightning - HV fuse blown by lightning strike | 2014-01-10 16:07 | 2014-01-10 | 2014-01-10 17:24 | Calculated | TF2320 | TF2320 - Transformer Fuse: TF2320 |  | 103SEG453-459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 1 | 24558 | 77 | 0.00314 | 4.072e-05 | 5 | 385 | 2013/2014 | January-2014 | 1 | 2014
29950 | Lightning - HV fuse blown by lightning strike | 2014-01-10 17:57 | 2014-01-10 | 2014-01-10 19:30 | Calculated | TF6E12 | TF6E12 - Transformer Fuse: TF6E12 |  | 412SEG5256-5445 | Nihoniho 412-01 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 2 | 24558 | 186 | 0.00757 | 8.144e-05 | 5 | 465 | 2013/2014 | January-2014 | 1 | 2014
29951 | Lightning - Faulty Tx | 2014-01-10 22:29 | 2014-01-10 | 2014-01-11 10:40 | Calculated | TF2574 | TF2574 - Transformer Fuse: TF2574 |  | 104SEG217-730 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 731 | 1 | 24558 | 731 | 0.02977 | 4.072e-05 | 25 | 18275 | 2013/2014 | January-2014 | 1 | 2014
29952 | Birds - Bird on transformer pole | 2014-01-11 08:07 | 2014-01-11 | 2014-01-11 09:55 | Calculated | 5266 | 5266 - Recloser 5266 |  | 413SEG5260-5266 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 108 | 21 | 24558 | 2268 | 0.09235 | 0.00085512 | 125 | 13500 | 2013/2014 | January-2014 | 1 | 2014
29953 | Blown HV Fuses | 2014-01-11 09:13 | 2014-01-11 | 2014-01-11 10:10 | Calculated | 6560 | 6560 - Recloser with Bypass & Links 6560 |  | 424SEG6560-5917 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 25 | 24558 | 1425 | 0.05803 | 0.001018 | 150 | 8550 | 2013/2014 | January-2014 | 1 | 2014
29954 | Bird on line | 2014-01-12 06:44 | 2014-01-12 | 2014-01-12 09:41 | Calculated | 5536 | 5536 - Sectionaliser 5536 |  | 124SEG5536 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 11 | 24558 | 1947 | 0.07928 | 0.00044792 | 77.5 | 13717 | 2013/2014 | January-2014 | 1 | 2014
29955 | Blown HV Fuses | 2014-01-12 07:30 | 2014-01-12 | 2014-01-12 09:20 | Calculated | TF6E18 | TF6E18 - Transformer Fuse: TF6E18 |  | 412SEG5265-5628 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 110 | 1 | 24558 | 110 | 0.00448 | 4.072e-05 | 15 | 1650 | 2013/2014 | January-2014 | 1 | 2014
29956 | Lightning | 2014-01-12 16:29 | 2014-01-12 | 2014-01-12 17:56 | Calculated | TF7Q4 | TF7Q4 - Transformer Fuse: TF7Q4 |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 1 | 24558 | 87 | 0.00354 | 4.072e-05 | 10 | 870 | 2013/2014 | January-2014 | 1 | 2014
29958 | Lightning | 2014-01-12 16:29 | 2014-01-12 | 2014-01-12 21:34 | Calculated | TF7Q10 | TF7Q10 - Transformer Fuse: TF7Q10 |  | 426SEG5526-5359 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 305 | 3 | 24558 | 915 | 0.03726 | 0.00012216 | 15 | 4575 | 2013/2014 | January-2014 | 1 | 2014
29957 | Blown HV Fuses | 2014-01-12 18:41 | 2014-01-12 | 2014-01-12 21:00 | Calculated | TF9C4 | TF9C4 - Transformer Fuse: TF9C4 |  | 413SEG5456-5461 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 139 | 1 | 24558 | 139 | 0.00566 | 4.072e-05 | 15 | 2085 | 2013/2014 | January-2014 | 1 | 2014
29961 | Unknown | 2014-01-13 09:11 | 2014-01-13 | 2014-01-13 10:21 | Calculated | 5422 | 5422 - Recloser with Bypass & Links 5422 |  | 413SEG5636-5422 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 38 | 24558 | 2660 | 0.10832 | 0.0015474 | 218 | 15260 | 2013/2014 | January-2014 | 1 | 2014
29960 | Remove Bird Nests/DDO | 2014-01-13 10:17 | 2014-01-13 | 2014-01-13 12:09 | Calculated | TF9C4 | TF9C4 - Transformer Fuse: TF9C4 |  | 413SEG5456-5461 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 112 | 1 | 24558 | 112 | 0.00456 | 4.072e-05 | 15 | 1680 | 2013/2014 | January-2014 | 1 | 2014
29963 | L/V Line Down | 2014-01-13 10:31 | 2014-01-13 | 2014-01-13 15:05 | Calculated | TF2018 | TF2018 - Transformer Fuse: TF2018 |  | 115SEG1711 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 274 | 6 | 24558 | 1644 | 0.06694 | 0.00024432 | 30 | 8220 | 2013/2014 | January-2014 | 1 | 2014
29962 | Bulls die by rubbing against stay wire | 2014-01-13 12:52 | 2014-01-13 | 2014-01-13 14:43 | Calculated | 5123 | 5123 - Fused Link 5123 |  | 413SEG5123 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AFAR | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 111 | 5 | 24558 | 555 | 0.0226 | 0.0002036 | 40 | 4440 | 2013/2014 | January-2014 | 1 | 2014
29964 | Pole fuse out - Old Age | 2014-01-13 20:29 | 2014-01-13 | 2014-01-13 22:19 | Calculated | TF8I40 | TF8I40 - Transformer Fuse: TF8I40 |  | 403SEG5243-5855 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 1 | 24558 | 110 | 0.00448 | 4.072e-05 | 10 | 1100 | 2013/2014 | January-2014 | 1 | 2014
29965 | Refer 2014/8 Move Cable From Faulty RMU 5974 to Spare RMU 5973 | 2014-01-14 08:56 | 2014-01-14 | 2014-01-14 16:36 | Calculated | 5970 | 5970 - RTE Switch 5970 |  | 419SEG5970-6340 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 392 | 22 | 24558 | 5806 | 0.23642 | 0.00089584 | 2150 | 362699 | 2013/2014 | January-2014 | 1 | 2014
29966 | Rerfer 2014/NP 12114 Replace LV X Arms | 2014-01-14 09:09 | 2014-01-14 | 2014-01-14 12:18 | Calculated | TF1500 | TF1500 - Transformer Fuse: TF1500 |  | 108SEG501-211 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 189 | 11 | 24558 | 2079 | 0.08466 | 0.00044792 | 50 | 9449 | 2013/2014 | January-2014 | 1 | 2014
29967 | Refer 2014/9 Change Poles & X Arms | 2014-01-14 09:10 | 2014-01-14 | 2014-01-14 14:06 | Calculated | TF1049 | TF1049 - Transformer Fuse: TF1049 |  | 109SEG2190 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 296 | 2 | 24558 | 592 | 0.02411 | 8.144e-05 | 30 | 8880 | 2013/2014 | January-2014 | 1 | 2014
29968 | Refer 2014/14114 Replace LV X Arms | 2014-01-14 13:09 | 2014-01-14 | 2014-01-14 15:15 | Calculated | TF378 | TF378 - Transformer Fuse: TF378 |  | 108SEG181-219 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 126 | 16 | 24558 | 2016 | 0.08209 | 0.00065152 | 100 | 12600 | 2013/2014 | January-2014 | 1 | 2014
29969 | Low 11kV Lines | 2014-01-15 06:08 | 2014-01-15 | 2014-01-15 09:19 | Calculated | 522 | 522 - Air Break Switch 522 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DICL | Conductor Low - Incorrect Clearances | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 52 | 24558 | 9932 | 0.40443 | 0.0021174 | 565 | 107914 | 2013/2014 | January-2014 | 1 | 2014
29972 | Birds | 2014-01-15 08:45 | 2014-01-15 | 2014-01-15 10:57 | Calculated | TF9L2 | TF9L2 - Transformer Fuse: TF9L2 |  | 408SEG5916-5241 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 132 | 3 | 24558 | 396 | 0.01613 | 0.00012216 | 15 | 1980 | 2013/2014 | January-2014 | 1 | 2014
29971 | Refer 2014/ DM414 Change X Arms on Tx | 2014-01-15 10:08 | 2014-01-15 | 2014-01-15 16:21 | Calculated | TF1469 | TF1469 - Transformer Fuse: TF1469 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 373 | 3 | 24558 | 1119 | 0.04557 | 0.00012216 | 50 | 18649 | 2013/2014 | January-2014 | 1 | 2014
29973 | Blown HV Fuses | 2014-01-15 10:46 | 2014-01-15 | 2014-01-15 11:52 | Calculated | TF1399 | TF1399 - Transformer Fuse: TF1399 |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 3 | 24558 | 198 | 0.00806 | 0.00012216 | 25 | 1649 | 2013/2014 | January-2014 | 1 | 2014
29974 | Refer 2014/18 Change Poles & X Arms | 2014-01-16 09:04 | 2014-01-16 | 2014-01-16 15:03 | Calculated | 246 | 246 - Fused Link 246 |  | 106SEG246-252 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 359 | 26 | 24558 | 9334 | 0.38008 | 0.0010587 | 152.5 | 54747 | 2013/2014 | January-2014 | 1 | 2014
29977 | Refer 2014/11 Resag Lines @ Poles 1071251 & 1072144 | 2014-01-17 09:54 | 2014-01-17 | 2014-01-17 11:44 | Calculated | 244 | 244 - Air Break Switch 244 |  | 107SEG244-575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 110 | 41 | 24558 | 4510 | 0.18365 | 0.0016695 | 435 | 47849 | 2013/2014 | January-2014 | 1 | 2014
29975 | Trees | 2014-01-17 16:20 | 2014-01-17 | 2014-01-17 18:35 | Calculated | 1325 | 1325 - Fused Link 1325 |  | 103SEG1335-1301 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 135 | 4 | 24558 | 540 | 0.02199 | 0.00016288 | 30 | 4050 | 2013/2014 | January-2014 | 1 | 2014
29976 | Trees | 2014-01-17 19:48 | 2014-01-17 | 2014-01-18 00:22 | Calculated | TF123 | TF123 - Transformer Fuse: TF123 |  | 107SEG113-262 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 274 | 2 | 24558 | 548 | 0.02231 | 8.144e-05 | 10 | 2740 | 2013/2014 | January-2014 | 1 | 2014
29978 | Blown HV Fuses | 2014-01-17 20:22 | 2014-01-17 | 2014-01-17 21:49 | Calculated | TF213 | TF213 - Transformer Fuse: TF213 |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 7 | 24558 | 609 | 0.0248 | 0.00028504 | 30 | 2609 | 2013/2014 | January-2014 | 1 | 2014
29979 | Wind | 2014-01-19 04:22 | 2014-01-19 | 2014-01-19 05:05 | Calculated | 1755 | 1755 - Fused Link 1755 |  | 109SEG1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 5 | 24558 | 215 | 0.00875 | 0.0002036 | 105 | 4515 | 2013/2014 | January-2014 | 1 | 2014
29982 | Pole fuse out on pole - Old Age | 2014-01-19 11:19 | 2014-01-19 | 2014-01-19 12:18 | Calculated | TF20L37 | TF20L37 - Transformer Fuse: TF20L37 |  | 415SEG5695-5692 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 2 | 24558 | 118 | 0.0048 | 8.144e-05 | 15 | 885 | 2013/2014 | January-2014 | 1 | 2014
29980 | Vehicle vs Line | 2014-01-19 12:08 | 2014-01-19 | 2014-01-19 13:31 | Calculated | 730 | 730 - Recloser with Bypass & Links 730 |  | 104SEG217-730 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 46 | 24558 | 3818 | 0.15547 | 0.0018731 | 415 | 34445 | 2013/2014 | January-2014 | 1 | 2014
29981 | Birds | 2014-01-19 13:00 | 2014-01-19 | 2014-01-19 13:59 | Calculated | TF11S13 | TF11S13 - Transformer Fuse: TF11S13 |  | 427SEG5524 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 2 | 24558 | 118 | 0.0048 | 8.144e-05 | 15 | 885 | 2013/2014 | January-2014 | 1 | 2014
29984 | Refer 2014/24 Remove L/Z's Replace Cluster Bracket @ Pole 1051023 | 2014-01-20 09:04 | 2014-01-20 | 2014-01-20 10:46 | Calculated | TF567 | TF567 - Transformer Fuse: TF567 |  | 108SEG287 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 45 | 24558 | 4590 | 0.1869 | 0.0018324 | 300 | 30599 | 2013/2014 | January-2014 | 1 | 2014
29985 | Refer 2014/15 Cut Away Line To Tx 1015, Remove Tx 1015, Change L/A's @ Tx 1013 | 2014-01-20 09:09 | 2014-01-20 | 2014-01-20 12:19 | Calculated | 290 | 290 - Air Break Switch 290 |  | 101SEG552-290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 190 | 8 | 24558 | 1520 | 0.06189 | 0.00032576 | 65 | 12350 | 2013/2014 | January-2014 | 1 | 2014
29986 | Refer 2014/20 Change Poles & X Arms | 2014-01-21 08:26 | 2014-01-21 | 2014-01-21 15:18 | Calculated | 5100 | 5100 - Air Break Switch 5100 |  | 604SEG5120-5100 | Ongarue / Taumarunui 604-01 | Urban A | Ongarue / Taumarunui 33 | Direct from Ongarue Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 210 | 10 | 24558 | 2100 | 0.08551 | 0.0004072 | 60 | 12600 | 2013/2014 | January-2014 | 1 | 2014
29983 | Blown HV Fuses | 2014-01-21 09:39 | 2014-01-21 | 2014-01-21 11:16 | Calculated | TF1936 | TF1936 - Transformer Fuse: TF1936 |  | 114SEG1106-1105 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 5 | 24558 | 485 | 0.01975 | 0.0002036 | 25 | 2425 | 2013/2014 | January-2014 | 1 | 2014
29988 | Refer 2014/19 Install New Pole and Connect 11kV Cable Transpower Job | 2014-01-22 09:39 | 2014-01-22 | 2014-01-22 14:57 | Calculated | 482 | 482 - Air Break Switch 482 |  | 120SEG482-480 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 318 | 11 | 24558 | 3498 | 0.14244 | 0.00044792 | 200 | 63599 | 2013/2014 | January-2014 | 1 | 2014
29989 | Isolating Tx Faulty | 2014-01-23 07:22 | 2014-01-23 | 2014-01-29 15:21 | Calculated | 5764 | 5764 - Fused Link 5764 |  | 408SEGT08J07-5386 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 423 | 87 | 24558 | 22963 | 0.93505 | 0.0035426 | 521 | 142445 | 2013/2014 | January-2014 | 1 | 2014
29991 | Bird nest at transformer pole - HV Fuse blown | 2014-01-23 09:52 | 2014-01-23 | 2014-01-23 12:00 | Calculated | TF6Q5 | TF6Q5 - Transformer Fuse: TF6Q5 |  | 426SEG5588-5583 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 2 | 24558 | 256 | 0.01042 | 8.144e-05 | 15 | 1920 | 2013/2014 | January-2014 | 1 | 2014
29990 | Refer 2014/22 Install New Radio Hut - Isolate Cable From Tx 05L09 | 2014-01-23 10:12 | 2014-01-23 | 2014-01-23 12:50 | Calculated | 5848 | 5848 - Sectionaliser 5848 |  | 421SEG5848 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 158 | 1 | 24558 | 158 | 0.00643 | 4.072e-05 | 3 | 474 | 2013/2014 | January-2014 | 1 | 2014
29992 | Blown HV Fuses | 2014-01-23 22:20 | 2014-01-23 | 2014-01-23 23:10 | Calculated | TF2141 | TF2141 - Transformer Fuse: TF2141 |  | 101SEG248 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 2 | 24558 | 100 | 0.00407 | 8.144e-05 | 15 | 750 | 2013/2014 | January-2014 | 1 | 2014
29995 | Refer 2014/28 Change pole and crossarm | 2014-01-24 08:49 | 2014-01-24 | 2014-01-24 15:21 | Calculated | 5100 | 5100 - Air Break Switch 5100 |  | 604SEG5120-5100 | Ongarue / Taumarunui 604-01 | Urban A | Ongarue / Taumarunui 33 | Direct from Ongarue Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24558 |  | 0 | 0 |  |  | 2013/2014 | January-2014 | 1 | 2014
29996 | Refer 2014/37 33kV Line renewal -safety precaution | 2014-01-24 09:37 | 2014-01-24 | 2014-01-24 14:18 | Calculated | 5781 | 5781 - Fused Link 5781 |  | 402SEG5781 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 281 | 8 | 24558 | 2248 | 0.09154 | 0.00032576 | 75 | 21075 | 2013/2014 | January-2014 | 1 | 2014
29997 | Refer DM411 Upgrade Earth Bank | 2014-01-24 09:57 | 2014-01-24 | 2014-01-24 13:38 | Calculated | TF2067 | TF2067 - Transformer Fuse: TF2067 |  | 115SEG1646-1718 | Mokauiti 115-05 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 221 | 1 | 24558 | 221 | 0.009 | 4.072e-05 | 15 | 3315 | 2013/2014 | January-2014 | 1 | 2014
29998 | Refer DM431 Upgrade Transformer | 2014-01-24 10:06 | 2014-01-24 | 2014-01-24 14:24 | Calculated | TF796 | TF796 - Transformer Fuse: TF796 |  | 120SEG497-REG31 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 2 | 24558 | 516 | 0.02101 | 8.144e-05 | 25 | 6450 | 2013/2014 | January-2014 | 1 | 2014
30002 | Blown HV Fuse - Cause unknown | 2014-01-24 10:43 | 2014-01-24 | 2014-01-24 17:25 | Calculated | TF9L2 | TF9L2 - Transformer Fuse: TF9L2 |  | 408SEG5916-5241 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 402 | 3 | 24558 | 1206 | 0.04911 | 0.00012216 | 15 | 6030 | 2013/2014 | January-2014 | 1 | 2014
29999 | Blown L/V fuse and Fuse holder | 2014-01-24 11:23 | 2014-01-24 | 2014-01-24 12:33 | Calculated | TF2J9 | TF2J9 - Transformer Fuse: TF2J9 |  | 421SEG5468 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 70 | 5 | 24558 | 350 | 0.01425 | 0.0002036 | 50 | 3500 | 2013/2014 | January-2014 | 1 | 2014
30000 | Broken DDO | 2014-01-24 13:38 | 2014-01-24 | 2014-01-24 14:35 | Calculated | TF2067 | TF2067 - Transformer Fuse: TF2067 |  | 115SEG1646-1718 | Mokauiti 115-05 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 57 | 8 | 24558 | 337 | 0.01372 | 0.00032576 | 85 | 3654 | 2013/2014 | January-2014 | 1 | 2014
30001 | Repair LV Fuse on Ground Sub Board | 2014-01-24 16:59 | 2014-01-24 | 2014-01-24 17:37 | Calculated | 5670 | 5670 - Fused Link 5670 |  | 415SEG5670 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 11 | 24558 | 418 | 0.01702 | 0.00044792 | 60 | 2279 | 2013/2014 | January-2014 | 1 | 2014
29994 | Blown links due to duck hitting the line | 2014-01-25 19:23 | 2014-01-25 | 2014-01-25 20:19 | Calculated | 458 | 458 - Fused Link 458 |  | 129SEG458 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Birds & Animals | Birds | BANI:BIRD:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 7 | 24558 | 392 | 0.01596 | 0.00028504 | 80 | 4480 | 2013/2014 | January-2014 | 1 | 2014
30004 | Tree Through Line - Line Down | 2014-01-26 16:12 | 2014-01-26 | 2014-01-26 18:53 | Calculated | 5851 | 5851 - Electronic Sectionaliser 5851 |  | 421SEG5851-5435 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 160 | 15 | 24558 | 2410 | 0.09814 | 0.0006108 | 105 | 16876 | 2013/2014 | January-2014 | 1 | 2014
30005 | Lightning | 2014-01-26 16:25 | 2014-01-26 | 2014-01-26 18:36 | Calculated | 1342 | 1342 - Air Break Switch 1342 |  | 116SEG1342-1312 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 82 | 24558 | 10742 | 0.43741 | 0.003339 | 710 | 93009 | 2013/2014 | January-2014 | 1 | 2014
30003 | Replace LV service box | 2014-01-26 16:34 | 2014-01-26 | 2014-01-26 17:20 | Calculated | TF8I31 | TF8I31 - Transformer Fuse: TF8I31 |  | 403SEG5111-5997 | Western 403-01 | Urban A | Western | Borough Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 38 | 24558 | 1748 | 0.07118 | 0.0015474 | 200 | 9199 | 2013/2014 | January-2014 | 1 | 2014
30007 | 2 BLOWN HV FUSES FROM LIGHTNING AT 13K04 | 2014-01-26 18:28 | 2014-01-26 | 2014-01-26 20:24 | Calculated | TF13K11 | TF13K11 - Transformer Fuse: TF13K11 |  | 410SEG5703-5805 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 116 | 2 | 24558 | 232 | 0.00945 | 8.144e-05 | 15 | 1740 | 2013/2014 | January-2014 | 1 | 2014
30009 | Lightning | 2014-01-26 18:28 | 2014-01-26 | 2014-01-26 20:55 | Calculated | TF4E1 | TF4E1 - Transformer Fuse: TF4E1 |  | 422SEG5556-5753 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 147 | 2 | 24558 | 294 | 0.01197 | 8.144e-05 | 15 | 2205 | 2013/2014 | January-2014 | 1 | 2014
30010 | 2 BLOWN HV FUSES AT TX FROM LIGHTNING | 2014-01-26 18:36 | 2014-01-26 | 2014-01-26 23:29 | Calculated | TF1988 | TF1988 - Transformer Fuse: TF1988 |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 293 | 1 | 24558 | 293 | 0.01193 | 4.072e-05 | 10 | 2930 | 2013/2014 | January-2014 | 1 | 2014
30008 | BLOWN HV FUSE AT TAP OFF FROM LIGHTNING | 2014-01-26 19:04 | 2014-01-26 | 2014-01-26 20:42 | Calculated | TF9H9 | TF9H9 - Transformer Fuse: TF9H9 |  | 403SEG5602-5317 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 98 | 1 | 24558 | 98 | 0.00399 | 4.072e-05 | 25 | 2450 | 2013/2014 | January-2014 | 1 | 2014
30006 | Lightning | 2014-01-26 19:13 | 2014-01-26 | 2014-01-26 19:15 | Calculated | 5684 | 5684 - Recloser 5684 |  | 416SEG5721-5684 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 65 | 24558 | 130 | 0.00529 | 0.0026468 | 632.5 | 1264 | 2013/2014 | January-2014 | 1 | 2014
29993 | Blown Fuse due to Lightning | 2014-01-27 12:44 | 2014-01-27 | 2014-01-27 13:28 | Calculated | TF9I21 | TF9I21 - Transformer Fuse: TF9I21 |  | 403SEG5601-5981 | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 2 | 24558 | 88 | 0.00358 | 8.144e-05 | 3 | 132 | 2013/2014 | January-2014 | 1 | 2014
30011 | WIND - BLOWN HV LINKS | 2014-01-28 07:39 | 2014-01-28 | 2014-01-28 09:00 | Calculated | 5509 | 5509 - Fused Link 5509 |  | 413SEG5509 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 6 | 24558 | 486 | 0.01979 | 0.00024432 | 45 | 3645 | 2013/2014 | January-2014 | 1 | 2014
30012 | Blown HV Fuse - Unknown | 2014-01-28 09:01 | 2014-01-28 | 2014-01-28 10:45 | Calculated | TF07Q15 | TF07Q15 - Transformer Fuse: TF07Q15 |  | 426SEG5359-5237 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 104 | 1 | 24558 | 104 | 0.00423 | 4.072e-05 | 15 | 1560 | 2013/2014 | January-2014 | 1 | 2014
30016 | Refer 2014/31 Taumaruni/Kuratau 33kV 608/03 Line Renewal - Pole Changes | 2014-01-28 09:08 | 2014-01-28 | 2014-01-28 19:53 | Calculated | 5190 | 5190 - Recloser 33kV 5190 |  | 607SEG5833-5190 | Tokaanu / Kuratau 607-01 | Urban A | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24558 |  | 0 | 0 |  |  | 2013/2014 | January-2014 | 1 | 2014
30017 | Refer 2014/32 Part of 33kV isolaton for refer 2014/31- pole changes | 2014-01-28 09:19 | 2014-01-28 | 2014-01-28 19:52 | Calculated | 6126 | 6126 - RTE Switch 6126 |  | 402SEG6126 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24558 |  | 0 | 0 |  |  | 2013/2014 | January-2014 | 1 | 2014
30013 | Install LV fusing for new service mains | 2014-01-28 18:15 | 2014-01-28 | 2014-01-28 18:45 | Calculated | TF2777 | TF2777 - Transformer Fuse: TF2777 |  | 111SEG138-663 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 30 | 2 | 24558 | 60 | 0.00244 | 8.144e-05 | 100 | 3000 | 2013/2014 | January-2014 | 1 | 2014
30014 | Earth Switch Tripped - Can't find cause | 2014-01-28 18:55 | 2014-01-28 | 2014-01-28 21:52 | Calculated | 5277 | 5277 - Electronic Sectionaliser 5277 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 177 | 16 | 24558 | 2382 | 0.09699 | 0.00065152 | 135 | 19395 | 2013/2014 | January-2014 | 1 | 2014
30015 | BLOWN HV FUSE NO OBVIOUS REASON | 2014-01-28 20:14 | 2014-01-28 | 2014-01-28 21:23 | Calculated | TF340 | TF340 - Transformer Fuse: TF340 |  | 122SEG371-633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 4 | 24558 | 276 | 0.01124 | 0.00016288 | 10 | 690 | 2013/2014 | January-2014 | 1 | 2014
30018 | Unknown-SCADA | 2014-01-29 02:37 | 2014-01-29 | 2014-01-29 02:41 | Calculated | 5385 | 5385 - Recloser with Bypass 5385 |  | 408SEG5388-5385 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 178 | 24558 | 712 | 0.02899 | 0.0072481 | 1345 | 5379 | 2013/2014 | January-2014 | 1 | 2014
30019 | Refer 2014 / NP PP33 | 2014-01-29 09:39 | 2014-01-29 | 2014-01-29 13:31 | Calculated | TF1846 | TF1846 - Transformer Fuse: TF1846 |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 232 | 4 | 24558 | 928 | 0.03779 | 0.00016288 | 30 | 6960 | 2013/2014 | January-2014 | 1 | 2014
30020 | Blown LV Fuse | 2014-01-29 11:25 | 2014-01-29 | 2014-01-29 11:33 | Calculated | TF4179 | TF4179 - Transformer Fuse: TF4179 |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWG1 | Switch-gear Failure Low Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 3 | 24558 | 24 | 0.00098 | 0.00012216 | 30 | 240 | 2013/2014 | January-2014 | 1 | 2014
30021 | Faulty L/A | 2014-01-29 14:43 | 2014-01-29 | 2014-01-29 17:07 | Calculated | 5102 | 5102 - Solid Link 5102 |  | 408SEG5550-5102 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 6 | 24558 | 864 | 0.03518 | 0.00024432 | 35 | 5040 | 2013/2014 | January-2014 | 1 | 2014
30022 | Refer 2014 / 10 Upgrade Earthing & Replace Link Arm For Link 5386 | 2014-01-29 15:17 | 2014-01-29 | 2014-01-29 15:21 | Calculated | 5386 | 5386 - Fused Link 5386 |  | 408SEG5386-5935 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 4 | 69 | 24558 | 276 | 0.01124 | 0.0028097 | 391 | 1563 | 2013/2014 | January-2014 | 1 | 2014
30023 | Blown HV Fuses | 2014-01-29 19:59 | 2014-01-29 | 2014-01-29 22:29 | Calculated | TF15J03 | TF15J03 - TRANSFORMER FUSE : 15J03 |  | 410SEG5793-5746 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 150 | 1 | 24558 | 150 | 0.00611 | 4.072e-05 | 15 | 2250 | 2013/2014 | January-2014 | 1 | 2014
30024 | Refer 2014 / 38 Change Poles & X Arms, Raurimu - Kaitieke | 2014-01-30 07:57 | 2014-01-30 | 2014-01-30 16:35 | Calculated | 5793 | 5793 - Fused Link 5793 |  | 410SEG5793-5746 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 510 | 66 | 24558 | 4332 | 0.1764 | 0.0026875 | 428.5 | 42685 | 2013/2014 | January-2014 | 1 | 2014
30025 | Lightning | 2014-01-30 11:14 | 2014-01-30 | 2014-01-30 12:33 | Calculated | TF3291 | TF3291 - Transformer Fuse TF3291 |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 1 | 24558 | 79 | 0.00322 | 4.072e-05 | 15 | 1185 | 2013/2014 | January-2014 | 1 | 2014
30026 | Wind | 2014-01-30 14:50 | 2014-01-30 | 2014-01-30 16:55 | Calculated | TF2299 | TF2299 - Transformer Fuse: TF2299 |  | 122SEG371-633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 1 | 24558 | 125 | 0.00509 | 4.072e-05 | 10 | 1250 | 2013/2014 | January-2014 | 1 | 2014
30027 | Unknown | 2014-01-30 23:09 | 2014-01-30 | 2014-01-30 23:46 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 6 | 1363 | 24558 | 8178 | 0.33301 | 0.055501 | 11962.5 | 71774 | 2013/2014 | January-2014 | 1 | 2014
30028 | Birds | 2014-01-31 06:22 | 2014-01-31 | 2014-01-31 06:45 | Calculated | TF19K03 | TF19K03 - Transformer Fuse: TF19K03 |  | 415SEG5705 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 1 | 24558 | 23 | 0.00094 | 4.072e-05 | 10 | 230 | 2013/2014 | January-2014 | 1 | 2014
30029 | Refer 2014 / 39 Change Poles & X Arms Raurimu - Kaiteike | 2014-01-31 08:10 | 2014-01-31 | 2014-01-31 16:14 | Calculated | 5806 | 5806 - Recloser with Bypass 5806 |  | 410SEG5806-5793 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 417 | 61 | 24558 | 2445 | 0.09956 | 0.0024839 | 383.5 | 22313 | 2013/2014 | January-2014 | 1 | 2014
30030 | Old Age - HT Links | 2014-01-31 12:05 | 2014-01-31 | 2014-01-31 15:29 | Calculated | 5933 | 5933 - Earth Working Link 5933 |  | 421SEG5933 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 204 | 9 | 24558 | 1836 | 0.07476 | 0.00036648 | 60 | 12240 | 2013/2014 | January-2014 | 1 | 2014
30032 | Faulty Tx | 2014-01-31 16:41 | 2014-01-31 | 2014-02-01 13:54 | Calculated | TF1478 | TF1478 - Transformer Fuse: TF1478 |  | 121SEG748-418 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1273 | 1 | 24558 | 1273 | 0.05184 | 4.072e-05 | 10 | 12730 | 2013/2014 | January-2014 | 1 | 2014
30031 | Earth Fault | 2014-01-31 23:58 | 2014-01-31 | 2014-02-01 00:02 | Calculated | 594 | 594 - Recloser 594 |  | No Segment | 205-01 Gadsby Road | Urban A | No Feeder |  |  | Asset Related | Other | FAIL:FOLD:FOLS | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 2047 | 24558 | 8188 | 0.33341 | 0.083354 | 14641.5 | 58565 | 2013/2014 | January-2014 | 1 | 2014
30033 | Broken SWER Earth | 2014-02-01 14:24 | 2014-02-01 | 2014-02-01 16:43 | Calculated | TF1656 | TF1656 - Transformer Fuse: TF1656 |  | 113SEG1531-1501 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 139 | 1 | 24556 | 139 | 0.00566 | 4.0723e-05 | 15 | 2085 | 2013/2014 | February-2014 | 2 | 2014
30034 | Blown HV Fuse | 2014-02-01 22:20 | 2014-02-01 | 2014-02-01 23:30 | Calculated | TF8J30 | TF8J30 - Transformer Fuse: TF8J30 |  | 403SEG5811-5315 | Western 403-03 | Rural B | Western | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 70 | 1 | 24556 | 70 | 0.00285 | 4.0723e-05 | 10 | 700 | 2013/2014 | February-2014 | 2 | 2014
30036 | Recloser | 2014-02-02 18:19 | 2014-02-02 | 2014-02-02 19:30 | Calculated | 1512 | 1512 - Recloser 1512 |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 172 | 24556 | 12212 | 0.49731 | 0.0070044 | 1143 | 81152 | 2013/2014 | February-2014 | 2 | 2014
30037 | Birds | 2014-02-02 21:07 | 2014-02-02 | 2014-02-02 22:43 | Calculated | TF9L2 | TF9L2 - Transformer Fuse: TF9L2 |  | 408SEG5916-5241 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 96 | 3 | 24556 | 288 | 0.01173 | 0.00012217 | 15 | 1440 | 2013/2014 | February-2014 | 2 | 2014
30038 | Earth & O/Current | 2014-02-02 23:16 | 2014-02-02 | 2014-02-02 23:56 | Calculated | 594 | 594 - Recloser 594 |  | No Segment | 205-01 Gadsby Road | Urban A | No Feeder |  |  | Asset Related | Other | FAIL:FOLD:FOLS | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 1363 | 24556 | 2726 | 0.11101 | 0.055506 | 11962.5 | 23924 | 2013/2014 | February-2014 | 2 | 2014
30039 | Blown HV Fuse | 2014-02-03 06:46 | 2014-02-03 | 2014-02-03 08:12 | Calculated | TF700 | TF700 - Transformer Fuse: TF700 |  | 118SEG1742-463 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 2 | 24556 | 172 | 0.007 | 8.1446e-05 | 30 | 2580 | 2013/2014 | February-2014 | 2 | 2014
30042 | Blown HV Fuse | 2014-02-03 09:10 | 2014-02-03 | 2014-02-03 10:27 | Calculated | TF1726 | TF1726 - Transformer Fuse: TF1726 |  | 116SEG1327-1340 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 2 | 24556 | 154 | 0.00627 | 8.1446e-05 | 25 | 1925 | 2013/2014 | February-2014 | 2 | 2014
30043 | Birds | 2014-02-03 09:38 | 2014-02-03 | 2014-02-03 11:26 | Calculated | TF9L2 | TF9L2 - Transformer Fuse: TF9L2 |  | 408SEG5916-5241 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 108 | 3 | 24556 | 324 | 0.01319 | 0.00012217 | 15 | 1620 | 2013/2014 | February-2014 | 2 | 2014
30040 | Refer 2014 / 48 Replace Pole 1150259 at 784 Takiri Road | 2014-02-03 10:15 | 2014-02-03 | 2014-02-03 13:53 | Calculated | 1725 | 1725 - Fused Link 1725 |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 218 | 5 | 24556 | 1090 | 0.04439 | 0.00020362 | 60 | 13080 | 2013/2014 | February-2014 | 2 | 2014
30041 | Refer 2014 / PTPS 1165 | 2014-02-03 10:15 | 2014-02-03 | 2014-02-03 14:20 | Calculated | TF2126 | TF2126 - Transformer Fuse: TF2126 |  | 128SEG1605-1607 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 245 | 3 | 24556 | 735 | 0.02993 | 0.00012217 | 25 | 6124 | 2013/2014 | February-2014 | 2 | 2014
30044 | Refer 2014 / 51 Pole & Arm Replacement | 2014-02-05 08:11 | 2014-02-05 | 2014-02-05 15:44 | Calculated | 5631 | 5631 - Fused Link 5631 |  | 410SEG5631 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 453 | 8 | 24556 | 3624 | 0.14758 | 0.00032579 | 31 | 14042 | 2013/2014 | February-2014 | 2 | 2014
30045 | Blown HV Fuse | 2014-02-07 19:12 | 2014-02-07 | 2014-02-07 21:28 | Calculated | TF2182 | TF2182 - Transformer Fuse: TF2182 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 136 | 1 | 24556 | 136 | 0.00554 | 4.0723e-05 | 5 | 680 | 2013/2014 | February-2014 | 2 | 2014
30046 | Truck Accident | 2014-02-08 01:02 | 2014-02-08 | 2014-02-08 03:55 | Calculated | 5905 | 5905 - Earth Working Link 5905 |  | 417SEG5905 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 173 | 30 | 24556 | 5190 | 0.21135 | 0.0012217 | 130 | 22489 | 2013/2014 | February-2014 | 2 | 2014
30047 | Lightning | 2014-02-08 10:35 | 2014-02-08 | 2014-02-08 12:30 | Calculated | TF3E2 | TF3E2 - Transformer Fuse: TF3E2 |  | 422SEG5753 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 115 | 1 | 24556 | 115 | 0.00468 | 4.0723e-05 | 3 | 345 | 2013/2014 | February-2014 | 2 | 2014
30048 | Jumper Off | 2014-02-08 18:50 | 2014-02-08 | 2014-02-08 21:42 | Calculated | TF2822 | TF2822 - Transformer Fuse: TF2822 |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 1 | 24556 | 172 | 0.007 | 4.0723e-05 | 15 | 2580 | 2013/2014 | February-2014 | 2 | 2014
30049 | Blown HV Fuse - Old Age | 2014-02-09 07:37 | 2014-02-09 | 2014-02-09 08:06 | Calculated | TF20L62 | TF20L62 - Transformer Fuse: TF20L62 |  | 414SEG6644-5643 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 11 | 24556 | 319 | 0.01299 | 0.00044796 | 100 | 2899 | 2013/2014 | February-2014 | 2 | 2014
30050 | Blown HV Fuse - Old Age | 2014-02-09 09:15 | 2014-02-09 | 2014-02-09 09:29 | Calculated | TF4114 | TF4114 - Transformer Fuse: TF4114 |  | 416SEG5718-5677 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 3 | 24556 | 42 | 0.00171 | 0.00012217 | 15 | 210 | 2013/2014 | February-2014 | 2 | 2014
30051 | Refer 2014 / 58 Replace 3 Poles & Pot Head Tawa St | 2014-02-10 07:54 | 2014-02-10 | 2014-02-10 17:24 | Calculated | TF1003 | TF1003 - Transformer Fuse: TF1003 |  | 108SEG287 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 381 | 105 | 24556 | 17160 | 0.69881 | 0.0042759 | 500 | 114199 | 2013/2014 | February-2014 | 2 | 2014
30054 | Lightning | 2014-02-11 08:06 | 2014-02-11 | 2014-02-11 10:02 | Calculated | TF7Q4 | TF7Q4 - Transformer Fuse: TF7Q4 |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 1 | 24556 | 116 | 0.00472 | 4.0723e-05 | 10 | 1160 | 2013/2014 | February-2014 | 2 | 2014
30053 | Refer 2014 / 59 Repalce Poles & X Arms | 2014-02-11 09:16 | 2014-02-11 | 2014-02-11 16:16 | Calculated | TF87 | TF87 - Transformer Fuse: T87 |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 420 | 26 | 24556 | 9248 | 0.37661 | 0.0010588 | 130 | 42059 | 2013/2014 | February-2014 | 2 | 2014
30055 | Lightning | 2014-02-11 13:23 | 2014-02-11 | 2014-02-11 14:27 | Calculated | TF7J20 | TF7J20 - Transformer Fuse: TF7J20 |  | 402SEG5635 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 64 | 1 | 24556 | 64 | 0.00261 | 4.0723e-05 | 10 | 640 | 2013/2014 | February-2014 | 2 | 2014
30056 | Lightning | 2014-02-11 15:40 | 2014-02-11 | 2014-02-11 18:07 | Calculated | TF5E8 | TF5E8 - Transformer Fuse: TF5E8 |  | 412SEG6741-5227 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 147 | 1 | 24556 | 147 | 0.00599 | 4.0723e-05 | 3 | 441 | 2013/2014 | February-2014 | 2 | 2014
30057 | Refer 2014 /56 Isolation For Treecutting Under 3 Phase 11Kv Mananui Feeder | 2014-02-12 08:08 | 2014-02-12 | 2014-02-12 14:34 | Calculated | 5218 | 5218 - Recloser with Bypass 5218 |  | 408SEG5275-5218 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 294 | 178 | 24556 | 11155 | 0.45427 | 0.0072487 | 1366.25 | 84333 | 2013/2014 | February-2014 | 2 | 2014
30058 | Lightning | 2014-02-12 09:14 | 2014-02-12 | 2014-02-12 13:53 | Calculated | TO08E06 | TO08E06 - TAP OFF FUSE: TO08E06 |  | 413SEG5572-5579 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 279 | 1 | 24556 | 279 | 0.01136 | 4.0723e-05 | 7.5 | 2092 | 2013/2014 | February-2014 | 2 | 2014
30059 | Blown HV Links | 2014-02-12 18:25 | 2014-02-12 | 2014-02-12 20:14 | Calculated | 5705 | 5705 - Fused Link 5705 |  | 415SEG5705 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 7 | 24556 | 763 | 0.03107 | 0.00028506 | 55 | 5995 | 2013/2014 | February-2014 | 2 | 2014
30061 | Faulty Switch | 2014-02-14 09:54 | 2014-02-14 | 2014-02-14 12:50 | Calculated | 5124 | 5124 - Air Break Switch 5124 |  | 603SEG5607-5124 | Nihoniho 603-02 | Urban A | Nihoniho 33 | Direct from Ongarue Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 157 | 433 | 24556 | 57843 | 2.3556 | 0.017633 | 3108 | 427247 | 2013/2014 | February-2014 | 2 | 2014
30062 | Private Trees In Line | 2014-02-14 15:09 | 2014-02-14 | 2014-02-15 | Calculated | 5378 | 5378 - Recloser 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 531 | 60 | 24556 | 12186 | 0.49625 | 0.0024434 | 383 | 77178 | 2013/2014 | February-2014 | 2 | 2014
30063 | Faulty Lightning Arrestors | 2014-02-14 20:58 | 2014-02-14 | 2014-02-15 02:18 | Calculated | 1544 | 1544 - Air Break Switch 1544 |  | 309SEG1544-1349 | Mahoenui 309-02 | Urban A | Wairere / Mahoenui 33 | Wairere Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 320 | 648 | 24556 | 207360 | 8.4444 | 0.026389 | 4084.5 | 1307039 | 2013/2014 | February-2014 | 2 | 2014
30064 | Birds | 2014-02-15 10:08 | 2014-02-15 | 2014-02-15 11:13 | Calculated | 2061 | 2061 - Fused Link 2061 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 2 | 24556 | 130 | 0.00529 | 8.1446e-05 | 45 | 2925 | 2013/2014 | February-2014 | 2 | 2014
30065 | Blown HV Fuse | 2014-02-15 12:11 | 2014-02-15 | 2014-02-15 13:40 | Calculated | TF07R10 | TF07R10 - Transformer Fuse: TF7R10 |  | 426SEG5110-5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 2 | 24556 | 178 | 0.00725 | 8.1446e-05 | 7.5 | 667 | 2013/2014 | February-2014 | 2 | 2014
30066 | Blown HV Fuse | 2014-02-16 09:15 | 2014-02-16 | 2014-02-16 11:05 | Calculated | TF517 | TF517 - Transformer Fuse: TF517 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 1 | 24556 | 110 | 0.00448 | 4.0723e-05 | 13 | 1430 | 2013/2014 | February-2014 | 2 | 2014
30067 | Old Age | 2014-02-16 13:42 | 2014-02-16 | 2014-02-16 15:00 | Calculated | TF12J05 | TF12J05 - Transformer Fuse: TF12J05 |  | 409SEG5748-5743 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 78 | 1 | 24556 | 78 | 0.00318 | 4.0723e-05 | 15 | 1170 | 2013/2014 | February-2014 | 2 | 2014
30068 | Refer 2014 / 67 Replace Poles & XArms @ Tx 1205 | 2014-02-17 09:01 | 2014-02-17 | 2014-02-17 16:40 | Calculated | TF1205 | TF1205 - Transformer Fuse: TF1205 |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 459 | 27 | 24556 | 12393 | 0.50468 | 0.0010995 | 100 | 45899 | 2013/2014 | February-2014 | 2 | 2014
30069 | Refer 2014 / 68 Install Jena Mueller Rack To Tx 3069 | 2014-02-17 09:56 | 2014-02-17 | 2014-02-17 11:34 | Calculated | 597 | 597 - Air Break Switch 597 |  | 106SEG597 | Rangitoto 106-07 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 98 | 10 | 24556 | 980 | 0.03991 | 0.00040723 | 100 | 9800 | 2013/2014 | February-2014 | 2 | 2014
30070 | Blown HV Fuse | 2014-02-17 10:14 | 2014-02-17 | 2014-02-17 12:30 | Calculated | TO08E06 | TO08E06 - TAP OFF FUSE: TO08E06 |  | 413SEG5572-5579 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 136 | 1 | 24556 | 136 | 0.00554 | 4.0723e-05 | 7.5 | 1020 | 2013/2014 | February-2014 | 2 | 2014
30071 | Refer 2014 / 73 Replace Poles & X Arms | 2014-02-18 09:01 | 2014-02-18 | 2014-02-18 15:59 | Calculated | 5458 | 5458 - Fused Link 5458 |  | 413SEG5458-5567 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 418 | 33 | 24556 | 11803 | 0.48066 | 0.0013439 | 320.5 | 121334 | 2013/2014 | February-2014 | 2 | 2014
30072 | Broken X Arm 33KV | 2014-02-18 14:19 | 2014-02-18 | 2014-02-18 19:21 | Calculated | 6143 | 6143 - Circuit Breaker Manunui 33kV 6143 |  | 608SEG6144-5629 | Taumarunui / Kuratau 608-03 | Urban A | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 24 | 5 | 24556 | 99 | 0.00403 | 0.00020362 | 9479.75 | 10830 | 2013/2014 | February-2014 | 2 | 2014
30073 | Refer 2014 / 74 Replace Poles & X Arms | 2014-02-19 09:08 | 2014-02-19 | 2014-02-19 16:09 | Calculated | 5568 | 5568 - Fused Link 5568 |  | 413SEG5568-5302 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 421 | 12 | 24556 | 5022 | 0.20451 | 0.00048868 | 158 | 65543 | 2013/2014 | February-2014 | 2 | 2014
30074 | Tree On Line | 2014-02-19 14:19 | 2014-02-19 | 2014-02-19 17:37 | Calculated | 5653 | 5653 - Fused Link 5653 |  | 403SEG5653 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 198 | 1 | 24556 | 198 | 0.00806 | 4.0723e-05 | 3 | 594 | 2013/2014 | February-2014 | 2 | 2014
30075 | Birds | 2014-02-20 14:31 | 2014-02-20 | 2014-02-20 16:05 | Calculated | TF08Q11 | TF08Q11 - Transformer Fuse: 08Q11 |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 4 | 24556 | 376 | 0.01531 | 0.00016289 | 15 | 1410 | 2013/2014 | February-2014 | 2 | 2014
30076 | Faulty Sectionaliser | 2014-02-20 17:40 | 2014-02-20 | 2014-02-20 20:35 | Calculated | 5863 | 5863 - Recloser with Bypass & Links 5863 |  | 403SEG5863-5862 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 175 | 39 | 24556 | 5745 | 0.23396 | 0.0015882 | 260 | 37479 | 2013/2014 | February-2014 | 2 | 2014
30077 | Piripiri Sub fault | 2014-02-20 20:38 | 2014-02-20 | 2014-02-21 13:08 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | No Feeder |  |  | Asset Related | Other | FAIL:FOLD:FOLS | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24556 |  | 0 | 0 |  |  | 2013/2014 | February-2014 | 2 | 2014
30078 | Refer 2014 / 77 Line Renewal | 2014-02-21 09:35 | 2014-02-21 | 2014-02-21 13:25 | Calculated | 5569 | 5569 - Fused Link 5569 |  | 413SEG5569-5437 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 230 | 11 | 24556 | 2530 | 0.10303 | 0.00044796 | 87.5 | 20125 | 2013/2014 | February-2014 | 2 | 2014
30079 | Unknown/Manual Reclose | 2014-02-21 10:13 | 2014-02-21 | 2014-02-21 10:14 | Calculated | 5132 | 5132 - Circuit Breaker Manunui SF6 5132 |  | 409SEG5132-5900 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLS | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 612 | 24556 | 612 | 0.02492 | 0.024923 | 4367.5 | 4367 | 2013/2014 | February-2014 | 2 | 2014
30080 | Lightning | 2014-02-21 11:00 | 2014-02-21 | 2014-02-21 13:12 | Calculated | TF05E04 | TF05E04 - Transformer Fuse: 05E04 |  | 412SEG5564 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 132 | 1 | 24556 | 132 | 0.00538 | 4.0723e-05 | 3 | 396 | 2013/2014 | February-2014 | 2 | 2014
30081 | Blown High Voltage Fuses | 2014-02-21 11:53 | 2014-02-21 | 2014-02-21 15:27 | Calculated | TF1333 | TF1333 - Transformer Fuse: TF1333 |  | 106SEG256 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 214 | 5 | 24556 | 1070 | 0.04357 | 0.00020362 | 30 | 6420 | 2013/2014 | February-2014 | 2 | 2014
30082 | Unknown | 2014-02-21 19:35 | 2014-02-21 | 2014-02-21 20:50 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 75 | 34 | 24556 | 2550 | 0.10384 | 0.0013846 | 208.5 | 15637 | 2013/2014 | February-2014 | 2 | 2014
30084 | Blown HV Links | 2014-02-22 09:35 | 2014-02-22 | 2014-02-22 11:48 | Calculated | 1528 | 1528 - Fused Link 1528 |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 12 | 24556 | 1596 | 0.06499 | 0.00048868 | 58 | 7713 | 2013/2014 | February-2014 | 2 | 2014
30085 | Birds | 2014-02-22 11:17 | 2014-02-22 | 2014-02-22 13:46 | Calculated | TF02R02 | TF02R02 - Transformer Fuse: 02R02 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 2 | 24556 | 298 | 0.01214 | 8.1446e-05 | 10 | 1490 | 2013/2014 | February-2014 | 2 | 2014
30086 | Birds/L/A/Faulty | 2014-02-22 13:44 | 2014-02-22 | 2014-02-22 17:13 | Calculated | 5114 | 5114 - Fused Link 5114 |  | 409SEG5114 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 209 | 9 | 24556 | 841 | 0.03425 | 0.00036651 | 130.5 | 12259 | 2013/2014 | February-2014 | 2 | 2014
30088 | Blown Tap Off Links | 2014-02-23 05:17 | 2014-02-23 | 2014-02-23 06:30 | Calculated | 775 | 775 - Solid Link 775 |  | 101SEG679-267 | Caves 101-06 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 8 | 24556 | 584 | 0.02378 | 0.00032579 | 95 | 6935 | 2013/2014 | February-2014 | 2 | 2014
30089 | Birds | 2014-02-23 10:55 | 2014-02-23 | 2014-02-23 12:09 | Calculated | TF14N02 | TF14N02 - Transformer Fuse: 14N02 |  | 609SEG5158-5159 | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 74 | 2 | 24556 | 148 | 0.00603 | 8.1446e-05 | 15 | 1110 | 2013/2014 | February-2014 | 2 | 2014
30090 | Refer 2014 / 78 High Load Passing Through Area | 2014-02-24 04:30 | 2014-02-24 | 2014-02-24 05:02 | Calculated | TF4114 | TF4114 - Transformer Fuse: T4114 |  | 416SEG5718-5677 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 14 | 11 | 24556 | 54 | 0.0022 | 0.00044796 | 75 | 360 | 2013/2014 | February-2014 | 2 | 2014
30091 | Refer 2014/86 Replace Tx 1003 & HV U/G Cable | 2014-02-24 08:46 | 2014-02-24 | 2014-02-24 18:26 | Calculated | TF4114 | TF4114 - Transformer Fuse: T4114 |  | 416SEG5718-5677 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 17 | 60 | 24556 | 1020 | 0.04154 | 0.0024434 | 200 | 3399 | 2013/2014 | February-2014 | 2 | 2014
30093 | Refer 2014/82 Resag Lines | 2014-02-24 09:38 | 2014-02-24 | 2014-02-24 12:16 | Calculated | 252 | 252 - Fused Link 252 |  | 106SEG252-803 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 158 | 10 | 24556 | 1580 | 0.06434 | 0.00040723 | 50 | 7900 | 2013/2014 | February-2014 | 2 | 2014
30094 | Tractor Vs Line | 2014-02-25 10:50 | 2014-02-25 | 2014-02-25 15:15 | Calculated | TPOhakune CB38 | TPOhakune CB38 - 11kV Minimum Oil Circuit Breaker TP38 |  | No Segment | 517-01 Transpower Ohakune | Urban A | No Feeder |  |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 265 | 1984 | 24556 | 50474 | 2.0555 | 0.080795 | 15219.895 | 387077 | 2013/2014 | February-2014 | 2 | 2014
30096 | Lightning | 2014-02-26 14:41 | 2014-02-26 | 2014-02-26 15:16 | Calculated | TF09E16 | TF09E16 - Transformer Fuse: 09E16 |  | 413SEG5569-5437 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 35 | 1 | 24556 | 35 | 0.00143 | 4.0723e-05 | 15 | 525 | 2013/2014 | February-2014 | 2 | 2014
30097 | Faulty DDO | 2014-02-28 06:13 | 2014-02-28 | 2014-02-28 07:01 | Calculated | TF287 | TF287 - Transformer Fuse: T287 |  | 111SEG360-395 | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 3 | 24556 | 144 | 0.00586 | 0.00012217 | 25 | 1199 | 2013/2014 | February-2014 | 2 | 2014
30099 | Birds | 2014-02-28 09:05 | 2014-02-28 | 2014-02-28 12:50 | Calculated | TF02J14 | TF02J14 - Transformer Fuse: 02J14 |  | 421SEG5364-5874 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 225 | 1 | 24556 | 225 | 0.00916 | 4.0723e-05 | 15 | 3375 | 2013/2014 | February-2014 | 2 | 2014
30098 | Refer 2014 / 93 Install Prop Pole To Tx 7I23 | 2014-02-28 09:07 | 2014-02-28 | 2014-02-28 11:36 | Calculated | 5486 | 5486 - Fused Link 5486 |  | 402SEG5486-5781 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 149 | 28 | 24556 | 4172 | 0.1699 | 0.0011403 | 232.5 | 34642 | 2013/2014 | February-2014 | 2 | 2014
30100 | Birds - Tx 08K03 | 2014-03-01 09:31 | 2014-03-01 | 2014-03-01 11:51 | Calculated | 5936 | 5936 - Fused Link 5936 |  | 408SEG5936-5557 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 140 | 36 | 24560 | 5040 | 0.20521 | 0.0014658 | 161 | 22539 | 2013/2014 | March-2014 | 3 | 2014
30101 | Birds | 2014-03-01 10:27 | 2014-03-01 | 2014-03-01 11:51 | Calculated | TF08Q11 | TF08Q11 - Transformer Fuse: 08Q11 |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 4 | 24560 | 336 | 0.01368 | 0.00016287 | 15 | 1260 | 2013/2014 | March-2014 | 3 | 2014
30102 | Underground Cable Blown | 2014-03-02 10:36 | 2014-03-02 | 2014-03-07 13:09 | Calculated | TPN/Park 212 | TPN/Park 212 - 33kV Minimum Oil Circuit Breaker TPN/Park 212 |  | No Segment | 516-01 Transpower National Park | Rural D | No Feeder |  |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 9 | 659 | 24560 | 5207 | 0.21201 | 0.026832 | 5230.5 | 40701 | 2013/2014 | March-2014 | 3 | 2014
30104 | Birds | 2014-03-02 17:11 | 2014-03-02 | 2014-03-02 18:56 | Calculated | 5555 | 5555 - Fused Link 5555 |  | 416SEG5555 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 5 | 24560 | 525 | 0.02138 | 0.00020358 | 55 | 5775 | 2013/2014 | March-2014 | 3 | 2014
30105 | Refer 2014 / 101 Fit HV Fuses For Private Line Near ABS 545 | 2014-03-03 09:15 | 2014-03-03 | 2014-03-03 15:07 | Calculated | 288 | 288 - Air Break Switch 288 |  | 112SEG326-288 | Otorohanga 112-06 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 188 | 7 | 24560 | 1316 | 0.05358 | 0.00028502 | 43 | 8084 | 2013/2014 | March-2014 | 3 | 2014
30106 | Refer 2014 / 92 Cut Away Jumpers To Tx 458 - Total Dimantle | 2014-03-03 10:31 | 2014-03-03 | 2014-03-03 10:43 | Calculated | 544 | 544 - Air Break Switch 544 |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 12 | 32 | 24560 | 384 | 0.01564 | 0.0013029 | 310 | 3719 | 2013/2014 | March-2014 | 3 | 2014
30109 | Refer 2014 / 99 Service Tap Changer T1 | 2014-03-04 09:02 | 2014-03-04 | 2014-03-04 15:39 | Calculated | 6005 | 6005 - Recloser 6005 |  | 610SEG6005-6004 | 516-01 Transpower National Park | Rural D | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 9 | 1632 | 24560 | 14688 | 0.59805 | 0.06645 | 8688.5 | 78196 | 2013/2014 | March-2014 | 3 | 2014
30113 | Birds | 2014-03-04 09:13 | 2014-03-04 | 2014-03-04 10:22 | Calculated | TF02R02 | TF02R02 - Transformer Fuse: 02R02 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 2 | 24560 | 138 | 0.00562 | 8.1433e-05 | 10 | 690 | 2013/2014 | March-2014 | 3 | 2014
30110 | Refer 2014 / 95 Replace Pole 1011173, Replace Tx 1013, Fit Stay To Pole 1011172 | 2014-03-04 09:31 | 2014-03-04 | 2014-03-04 14:03 | Calculated | 552 | 552 - Air Break Switch 552 |  | 101SEG289-552 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 13 | 24560 | 3536 | 0.14397 | 0.00052932 | 95 | 25839 | 2013/2014 | March-2014 | 3 | 2014
30111 | Refer 2014 / 98 Replace Poles & X Arms | 2014-03-04 09:38 | 2014-03-04 | 2014-03-04 15:12 | Calculated | 6775 | 6775 - Fused Link 6775 |  | 413SEG5569-5437 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 334 | 4 | 24560 | 1336 | 0.0544 | 0.00016287 | 30 | 10020 | 2013/2014 | March-2014 | 3 | 2014
30114 | EarthFault | 2014-03-04 11:32 | 2014-03-04 | 2014-03-04 13:15 | Calculated | 687 | 687 - Circuit Breaker 687 |  | 117SEG687-1289 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLS | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 229 | 24560 | 12735 | 0.51853 | 0.0093241 | 1899.5 | 106106 | 2013/2014 | March-2014 | 3 | 2014
30115 | Refer 2014 / 96 Fit New Stub Pole To Pole 123 | 2014-03-05 09:38 | 2014-03-05 | 2014-03-05 12:10 | Calculated | 547 | 547 - Fused Link 547 |  | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 152 | 25 | 24560 | 3800 | 0.15472 | 0.0010179 | 275 | 41800 | 2013/2014 | March-2014 | 3 | 2014
30117 | Tree Cutting | 2014-03-05 10:06 | 2014-03-05 | 2014-03-05 11:51 | Calculated | TF08K02 | TF08K02 - Transformer Fuse: 08K02 |  | 408SEG5386-5935 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:ETRE1 | Tree Clearing/Trimming Activities | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 105 | 4 | 24560 | 420 | 0.0171 | 0.00016287 | 30 | 3150 | 2013/2014 | March-2014 | 3 | 2014
30119 | Blown HV fuse from Wind Clashing | 2014-03-06 08:28 | 2014-03-06 | 2014-03-06 09:45 | Calculated | TF1639 | TF1639 - Transformer Fuse: T1639 |  | 113SEG1526-1525 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 2 | 24560 | 154 | 0.00627 | 8.1433e-05 | 15 | 1155 | 2013/2014 | March-2014 | 3 | 2014
30120 | L/V Fault | 2014-03-06 11:36 | 2014-03-06 | 2014-03-06 11:45 | Calculated | TF08L14 | TF08L14 - Transformer Fuse: 08L14 |  | 408SEG5233-5514 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Low Voltage | FAIL:HCVS7K:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 9 | 2 | 24560 | 18 | 0.00073 | 8.1433e-05 | 15 | 135 | 2013/2014 | March-2014 | 3 | 2014
30121 | SWER Earth Testing | 2014-03-06 12:54 | 2014-03-06 | 2014-03-06 14:08 | Calculated | TF08L14 | TF08L14 - Transformer Fuse: 08L14 |  | 408SEG5233-5514 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 74 | 2 | 24560 | 148 | 0.00603 | 8.1433e-05 | 15 | 1110 | 2013/2014 | March-2014 | 3 | 2014
30122 | Possum & Bird dead at the base of pole | 2014-03-07 11:37 | 2014-03-07 | 2014-03-07 13:12 | Calculated | TF09D09 | TF09D09 - Transformer Fuse: 09D09 |  | 413SEG5562-5437 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 95 | 1 | 24560 | 95 | 0.00387 | 4.0717e-05 | 3 | 285 | 2013/2014 | March-2014 | 3 | 2014
30123 | Broken Insulator | 2014-03-10 10:45 | 2014-03-10 | 2014-03-10 12:40 | Calculated | 5596 | 5596 - Fused Link 5596 |  | 402SEG5352-5596 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 115 | 35 | 24560 | 4025 | 0.16388 | 0.0014251 | 287.5 | 33062 | 2013/2014 | March-2014 | 3 | 2014
30125 | Refer 2014 / 110 Replace Poles & X Arms | 2014-03-11 09:14 | 2014-03-11 | 2014-03-11 16:23 | Calculated | 5646 | 5646 - Fused Link 5646 |  | 413SEG5646-5883 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 429 | 6 | 24560 | 2574 | 0.1048 | 0.0002443 | 40 | 17160 | 2013/2014 | March-2014 | 3 | 2014
30126 | Refer 2014 / NP11314 | 2014-03-11 09:49 | 2014-03-11 | 2014-03-11 10:41 | Calculated | TF1846 | TF1846 - Transformer Fuse: T1846 |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 52 | 4 | 24560 | 208 | 0.00847 | 0.00016287 | 30 | 1560 | 2013/2014 | March-2014 | 3 | 2014
30127 | Refer 2014 / NP | 2014-03-11 13:00 | 2014-03-11 | 2014-03-11 13:39 | Calculated | TF378 | TF378 - Transformer Fuse: T378 |  | 108SEG181-219 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 39 | 16 | 24560 | 624 | 0.02541 | 0.00065147 | 100 | 3900 | 2013/2014 | March-2014 | 3 | 2014
30124 | Faulty DDO | 2014-03-11 17:48 | 2014-03-11 | 2014-03-11 18:17 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 29 | 16 | 24560 | 464 | 0.01889 | 0.00065147 | 132.5 | 3842 | 2013/2014 | March-2014 | 3 | 2014
30129 | Refer 2014 / 107 Replace Poles & X Arms | 2014-03-12 08:35 | 2014-03-12 | 2014-03-12 14:58 | Calculated | 344 | 344 - Air Break Switch 344 |  | 109SEG344-541 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 47 | 24560 | 16074 | 0.65448 | 0.0019137 | 410 | 140219 | 2013/2014 | March-2014 | 3 | 2014
30128 | Tree Cutting | 2014-03-12 11:07 | 2014-03-12 | 2014-03-12 11:40 | Calculated | TF12F03 | TF12F03 - Transformer Fuse: TF12F03 |  | 403SEG5541 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 33 | 3 | 24560 | 99 | 0.00403 | 0.00012215 | 15 | 497 | 2013/2014 | March-2014 | 3 | 2014
30130 | Blown HV Fuse | 2014-03-12 14:15 | 2014-03-12 | 2014-03-12 15:57 | Calculated | TF4122 | TF4122 - Transformer Fuse: T4122 |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 1 | 24560 | 102 | 0.00415 | 4.0717e-05 | 15 | 1530 | 2013/2014 | March-2014 | 3 | 2014
30131 | Refer 2014 /111 Replace Poles & X Arms | 2014-03-13 09:17 | 2014-03-13 | 2014-03-13 15:46 | Calculated | 5647 | 5647 - Fused Link 5647 |  | 413SEG5647-5646 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 389 | 13 | 24560 | 5057 | 0.2059 | 0.00052932 | 80 | 31120 | 2013/2014 | March-2014 | 3 | 2014
30132 | Refer 2014 / 108 Replace Poles & X Arms | 2014-03-14 09:03 | 2014-03-14 | 2014-03-14 15:17 | Calculated | 333 | 333 - Fused Link 333 |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 374 | 29 | 24560 | 10846 | 0.44161 | 0.0011808 | 335 | 125289 | 2013/2014 | March-2014 | 3 | 2014
30133 | Refer 2014 / 115 Replace Insulator Pole 1142104 | 2014-03-14 10:11 | 2014-03-14 | 2014-03-14 11:43 | Calculated | 1126 | 1126 - Recloser with Bypass & Links 1126 |  | 114SEG1126-1127 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 92 | 30 | 24560 | 2760 | 0.11238 | 0.0012215 | 215 | 19779 | 2013/2014 | March-2014 | 3 | 2014
30134 | Jumper Off | 2014-03-15 08:41 | 2014-03-15 | 2014-03-15 12:07 | Calculated | TF3222 | TF3222 - Transformer Fuse: T3222 |  | 126SEG509 | Rural 126-02 | Rural D | Rural | Taharoa Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 206 | 9 | 24560 | 678 | 0.02761 | 0.00036645 | 68 | 5482 | 2013/2014 | March-2014 | 3 | 2014
30135 | Line Down | 2014-03-15 11:04 | 2014-03-15 | 2014-03-15 16:16 | Calculated | 1072 | 1072 - Circuit Breaker 1072 Huirimu |  | 121SEG1072-753 | Huirimu 121-01 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 155 | 24560 | 7176 | 0.29218 | 0.0063111 | 1716.5 | 116725 | 2013/2014 | March-2014 | 3 | 2014
30137 | Wind | 2014-03-15 11:47 | 2014-03-15 | 2014-03-15 13:39 | Calculated | 1755 | 1755 - Fused Link 1755 |  | 109SEG1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 5 | 24560 | 560 | 0.0228 | 0.00020358 | 105 | 11760 | 2013/2014 | March-2014 | 3 | 2014
30138 | Wind | 2014-03-15 12:08 | 2014-03-15 | 2014-03-15 13:58 | Calculated | 2144 | 2144 - Fused Link 2144 |  | 110SEG390-2144 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 6 | 24560 | 660 | 0.02687 | 0.0002443 | 65 | 7150 | 2013/2014 | March-2014 | 3 | 2014
30136 | Tree On Line | 2014-03-15 13:24 | 2014-03-15 | 2014-03-18 14:54 | Calculated | 669 | 669 - Recloser with Bypass & Links 669 |  | 103SEG REG14-669 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 630 | 342 | 24560 | 26302 | 1.0709 | 0.013925 | 4634.5 | 265631 | 2013/2014 | March-2014 | 3 | 2014
30142 | Wind | 2014-03-15 14:18 | 2014-03-15 | 2014-03-15 16:24 | Calculated | 1787 | 1787 - Fused Link 1787 |  | 117SEG770-1787 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 6 | 24560 | 756 | 0.03078 | 0.0002443 | 50 | 6300 | 2013/2014 | March-2014 | 3 | 2014
30141 | Jumper Off on DDO | 2014-03-15 15:42 | 2014-03-15 | 2014-03-15 18:32 | Calculated | TF2543 | TF2543 - Transformer Fuse: T2543 |  | 109SEG334-396 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 74 | 24560 | 4778 | 0.19454 | 0.003013 | 525 | 32519 | 2013/2014 | March-2014 | 3 | 2014
30140 | Tree On Line | 2014-03-15 15:43 | 2014-03-15 | 2014-03-15 19:42 | Calculated | 684 | 684 - Circuit Breaker 684 |  | No Segment | 207-01 Wairere Falls | Rural D | No Feeder |  |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 239 | 260 | 24560 | 22205 | 0.90411 | 0.010586 | 1943 | 165597 | 2013/2014 | March-2014 | 3 | 2014
30143 | Wind | 2014-03-15 19:23 | 2014-03-15 | 2014-03-15 20:40 | Calculated | TF643 | TF643 - Transformer Fuse: T643 |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 3 | 24560 | 231 | 0.00941 | 0.00012215 | 25 | 1924 | 2013/2014 | March-2014 | 3 | 2014
30146 | Wind | 2014-03-15 19:56 | 2014-03-15 | 2014-03-15 21:59 | Calculated | 1108 | 1108 - Recloser with Bypass 1108 |  | 114SEG1110-1107 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 58 | 24560 | 7134 | 0.29047 | 0.0023616 | 395 | 48584 | 2013/2014 | March-2014 | 3 | 2014
30145 | Tree on line | 2014-03-15 20:00 | 2014-03-15 | 2014-03-15 23:32 | Calculated | TF464 | TF464 - Transformer Fuse: T464 |  | 106SEG590 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 212 | 80 | 24560 | 14230 | 0.5794 | 0.0032573 | 500 | 87799 | 2013/2014 | March-2014 | 3 | 2014
30148 | Wind - Blew TapOff fuses | 2014-03-15 20:51 | 2014-03-15 | 2014-03-16 08:52 | Calculated | 1651 | 1651 - Fused Link 1651 |  | 103SEG1651-2227 | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 721 | 22 | 24560 | 15862 | 0.64585 | 0.00089577 | 195 | 140595 | 2013/2014 | March-2014 | 3 | 2014
30147 | Wind | 2014-03-15 21:11 | 2014-03-15 | 2014-03-17 13:49 | Calculated | 272 | 272 - Fused Link 272 |  | 116SEG272 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 902 | 75 | 24560 | 14565 | 0.59304 | 0.0030537 | 632.5 | 123824 | 2013/2014 | March-2014 | 3 | 2014
30153 | Broken LV Jumpers | 2014-03-16 08:02 | 2014-03-16 | 2014-03-16 15:27 | Calculated | 289 | 289 - Fused Link 289 |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 445 | 14 | 24560 | 2138 | 0.08705 | 0.00057003 | 105 | 11384 | 2013/2014 | March-2014 | 3 | 2014
30150 | Wind | 2014-03-16 08:23 | 2014-03-16 | 2014-03-16 11:26 | Calculated | TF1451 | TF1451 - Transformer Fuse: T1451 |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 183 | 3 | 24560 | 549 | 0.02235 | 0.00012215 | 30 | 5490 | 2013/2014 | March-2014 | 3 | 2014
30149 | Wind | 2014-03-16 08:45 | 2014-03-16 | 2014-03-16 09:10 | Calculated | 1787 | 1787 - Fused Link 1787 |  | 117SEG770-1787 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 6 | 24560 | 150 | 0.00611 | 0.0002443 | 50 | 1250 | 2013/2014 | March-2014 | 3 | 2014
30151 | Wind | 2014-03-16 09:16 | 2014-03-16 | 2014-03-16 14:51 | Calculated | TF13K07 | TF13K07 - Transformer Fuse: TF13K07 |  | 410SEG5703-5805 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 335 | 66 | 24560 | 10566 | 0.43021 | 0.0026873 | 428.5 | 67574 | 2013/2014 | March-2014 | 3 | 2014
30155 | Wind | 2014-03-16 10:43 | 2014-03-16 | 2014-03-16 13:02 | Calculated | 1112 | 1112 - Fused Link 1112 |  | 114SEG1107-1116 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 8 | 24560 | 1112 | 0.04528 | 0.00032573 | 40 | 5559 | 2013/2014 | March-2014 | 3 | 2014
30152 | Branch On Line | 2014-03-16 11:23 | 2014-03-16 | 2014-03-16 11:26 | Calculated | 1784 | 1784 - Circuit Breaker 1784 |  | 110SEG1784-600 | McDonalds 110-01 | Urban A | McDonalds | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 451 | 24560 | 1353 | 0.05509 | 0.018363 | 5345 | 16034 | 2013/2014 | March-2014 | 3 | 2014
30156 | Birds | 2014-03-17 07:27 | 2014-03-17 | 2014-03-17 07:40 | Calculated | 727 | 727 - Circuit Breaker 727 |  | 305SEG657-126 | Te Kawa Street 304-01 | Urban A | Te Kawa St 33 | Direct from Hangatiki Supply |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 12 | 5 | 24560 | 60 | 0.00244 | 0.00020358 | 800 | 9599 | 2013/2014 | March-2014 | 3 | 2014
30157 | Wind - Replace broken pole | 2014-03-17 10:17 | 2014-03-17 | 2014-03-17 13:50 | Calculated | 1105 | 1105 - Air Break Switch 1105 |  | 114SEG1106-1105 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 213 | 15 | 24560 | 3195 | 0.13009 | 0.00061075 | 110 | 23429 | 2013/2014 | March-2014 | 3 | 2014
30158 | Wind - Blown HV fuse | 2014-03-17 10:27 | 2014-03-17 | 2014-03-17 12:00 | Calculated | TF272 | TF272 - Transformer Fuse: T272 |  | 111SEG579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 2 | 24560 | 186 | 0.00757 | 8.1433e-05 | 15 | 1395 | 2013/2014 | March-2014 | 3 | 2014
30159 | Broken X Arm | 2014-03-17 20:04 | 2014-03-17 | 2014-03-17 23:08 | Calculated | 544 | 544 - Air Break Switch 544 |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 184 | 32 | 24560 | 2558 | 0.10415 | 0.0013029 | 310 | 28179 | 2013/2014 | March-2014 | 3 | 2014
30161 | Refer 2014 / 128 Repalce Poles & X Arms | 2014-03-18 09:04 | 2014-03-18 | 2014-03-18 17:11 | Calculated | 333 | 333 - Fused Link 333 |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 388 | 29 | 24560 | 10896 | 0.44365 | 0.0011808 | 335 | 112179 | 2013/2014 | March-2014 | 3 | 2014
30162 | Refer 2014 / 126 Replace broken Insulator @ Pole 281419 | 2014-03-18 09:08 | 2014-03-18 | 2014-03-18 10:09 | Calculated | 5811 | 5811 - Sectionaliser with Incoming Link 5811 |  | 403SEG5811-5315 | Western 403-03 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 61 | 25 | 24560 | 1525 | 0.06209 | 0.0010179 | 193 | 11773 | 2013/2014 | March-2014 | 3 | 2014
30160 | Blown HV fuse | 2014-03-18 09:15 | 2014-03-18 | 2014-03-18 13:28 | Calculated | TF11E02 | TF11E02 - Transformer Fuse: 11E02 |  | 413SEG5646-5883 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 253 | 1 | 24560 | 253 | 0.0103 | 4.0717e-05 | 10 | 2530 | 2013/2014 | March-2014 | 3 | 2014
30163 | Refer 2014 / TG 911 | 2014-03-18 09:30 | 2014-03-18 | 2014-03-18 16:36 | Calculated | TF667 | TF667 - Transformer Fuse: T667 |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 426 | 2 | 24560 | 852 | 0.03469 | 8.1433e-05 | 15 | 6390 | 2013/2014 | March-2014 | 3 | 2014
30164 | Refer 2014 / 122 Resag Line @ Pole 1030135 | 2014-03-18 10:10 | 2014-03-18 | 2014-03-18 11:27 | Calculated | 260 | 260 - Fused Link 260 |  | 103SEG669-REG4 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 77 | 22 | 24560 | 1694 | 0.06897 | 0.00089577 | 190.5 | 14668 | 2013/2014 | March-2014 | 3 | 2014
30165 | Refer 2014 / MT00366 | 2014-03-18 12:04 | 2014-03-18 | 2014-03-18 12:08 | Calculated | 5348 | 5348 - Electronic Sectionaliser 5348 |  | 422SEG5348-5538 | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 4 | 20 | 24560 | 80 | 0.00326 | 0.00081433 | 155.5 | 622 | 2013/2014 | March-2014 | 3 | 2014
30166 | Broken DDO | 2014-03-18 14:33 | 2014-03-18 | 2014-03-18 17:01 | Calculated | 5391 | 5391 - Solid Link 5391 |  | 408SEG5391 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 2 | 24560 | 296 | 0.01205 | 8.1433e-05 | 15 | 2220 | 2013/2014 | March-2014 | 3 | 2014
30167 | Old Age | 2014-03-18 18:40 | 2014-03-18 | 2014-03-18 19:51 | Calculated | TF05H04 | TF05H04 - Transformer Fuse: 05H04 |  | 422SEG5105-5279 | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 71 | 2 | 24560 | 142 | 0.00578 | 8.1433e-05 | 15 | 1065 | 2013/2014 | March-2014 | 3 | 2014
30168 | Unknown | 2014-03-19 08:27 | 2014-03-19 | 2014-03-19 10:48 | Calculated | 5744 | 5744 - Sectionaliser with Bypass 5744 |  | 410SEG5744-5631 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 141 | 11 | 24560 | 1551 | 0.06315 | 0.00044788 | 48.5 | 6838 | 2013/2014 | March-2014 | 3 | 2014
30169 | Tractor vs Line - line taken out by tractor | 2014-03-19 10:02 | 2014-03-19 | 2014-03-19 12:05 | Calculated | TF911 | TF911 - Transformer Fuse: T911 |  | 103SEG453-459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 2 | 24560 | 246 | 0.01002 | 8.1433e-05 | 10 | 1230 | 2013/2014 | March-2014 | 3 | 2014
30170 | Old Age | 2014-03-20 16:57 | 2014-03-20 | 2014-03-20 17:04 | Calculated | TF2276 | TF2276 - Transformer Fuse: T2276 |  | 123SEG473 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Ageing Equipment | FAIL:6UQKC2:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 7 | 24560 | 49 | 0.002 | 0.00028502 | 30 | 209 | 2013/2014 | March-2014 | 3 | 2014
30171 | Refer 2014 / 129 Install Links For Recloser & Bypass, Remove Redundant SWER on Common Poles | 2014-03-21 08:45 | 2014-03-21 | 2014-03-21 14:38 | Calculated | 5935 | 5935 - Fused Link 5935 |  | 408SEG5935-5936 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 287 | 87 | 24560 | 10950 | 0.44585 | 0.0035423 | 521 | 78808 | 2013/2014 | March-2014 | 3 | 2014
30172 | Refer 2014 / 123 Replace Pole 1071181, Resag Line @ Pole 1071140 | 2014-03-21 08:59 | 2014-03-21 | 2014-03-21 13:48 | Calculated | 234 | 234 - Fused Link 234 |  | 107SEG234 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 162 | 17 | 24560 | 2754 | 0.11213 | 0.00069218 | 107.5 | 17414 | 2013/2014 | March-2014 | 3 | 2014
30175 | Refer 2014 /124 Resag @ Pole 1071174 | 2014-03-21 13:34 | 2014-03-21 | 2014-03-21 15:27 | Calculated | 239 | 239 - Fused Link 239 |  | 107SEG239-508 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 35 | 24560 | 3955 | 0.16103 | 0.0014251 | 215 | 24294 | 2013/2014 | March-2014 | 3 | 2014
30176 | Unknown - Blown HV Fuse | 2014-03-21 13:49 | 2014-03-21 | 2014-03-21 15:35 | Calculated | TF292 | TF292 - Transformer Fuse: T292 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 2 | 24560 | 212 | 0.00863 | 8.1433e-05 | 25 | 2650 | 2013/2014 | March-2014 | 3 | 2014
30177 | Unknown - Blown HV Fuse | 2014-03-21 21:44 | 2014-03-21 | 2014-03-21 23:16 | Calculated | TF2575 | TF2575 - Transformer Fuse: T2575 |  | 101SEG500-186 | Caves 101-07 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 3 | 24560 | 276 | 0.01124 | 0.00012215 | 10 | 919 | 2013/2014 | March-2014 | 3 | 2014
30178 | L/V Line Clash | 2014-03-22 09:24 | 2014-03-22 | 2014-03-22 10:35 | Calculated | TF5 | TF5 - Transformer Fuse: T5 |  | 106SEG389-227 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 5 | 24560 | 355 | 0.01445 | 0.00020358 | 30 | 2130 | 2013/2014 | March-2014 | 3 | 2014
30179 | Refer 2014 / 132 Replace Poles & X Arms Taupiri street | 2014-03-23 05:40 | 2014-03-23 | 2014-03-23 16:36 | Calculated | 2130 | 2130 - Fused Link 2130 |  | 105SEG2130 | Te Kuiti Town 105-01 | Urban A | Te Kuiti Town | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 362 | 72 | 24560 | 25857 | 1.0528 | 0.0029316 | 639.6552 | 230086 | 2013/2014 | March-2014 | 3 | 2014
30180 | Lightning - Blown HV Fuse | 2014-03-24 07:01 | 2014-03-24 | 2014-03-24 08:18 | Calculated | TF08G11 | TF08G11 - Transformer Fuse: 08G11 |  | 403SEG5766-5460 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 77 | 1 | 24560 | 77 | 0.00314 | 4.0717e-05 | 15 | 1155 | 2013/2014 | March-2014 | 3 | 2014
30182 | Refer 2014 / 152 Replace Poles & X Arms | 2014-03-25 08:07 | 2014-03-25 | 2014-03-25 16:30 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | 410SEG5511-5517 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 503 | 25 | 24560 | 12575 | 0.51201 | 0.0010179 | 183.5 | 92300 | 2013/2014 | March-2014 | 3 | 2014
30184 | Truck vs L/V Pole | 2014-03-25 16:18 | 2014-03-25 | 2014-03-26 00:46 | Calculated | TF10S01 | TF10S01 - Transformer Fuse: 10S01 |  | 424SEG6652-5168 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 508 | 61 | 24560 | 30988 | 1.2617 | 0.0024837 | 200 | 101599 | 2013/2014 | March-2014 | 3 | 2014
30185 | Bolt Out Of X/arm @ P 90 | 2014-03-25 18:43 | 2014-03-25 | 2014-03-25 19:13 | Calculated | 5161 | 5161 - Air Break Switch 5161 |  | 410SEG5161-5235 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 30 | 14 | 24560 | 420 | 0.0171 | 0.00057003 | 155 | 4650 | 2013/2014 | March-2014 | 3 | 2014
30186 | Cable Fault | 2014-03-26 04:45 | 2014-03-26 | 2014-03-26 14:58 | Calculated | 5773 | 5773 - Recloser 5773 |  | 419SEG5773-5998 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 571 | 39 | 24560 | 14257 | 0.5805 | 0.0015879 | 1640 | 579379 | 2013/2014 | March-2014 | 3 | 2014
30187 | Refer 2014 / 138 Replace Poles & X Arms | 2014-03-26 08:38 | 2014-03-26 | 2014-03-26 16:30 | Calculated | 344 | 344 - Air Break Switch 344 |  | 109SEG344-541 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 376 | 26 | 24560 | 9776 | 0.39805 | 0.0010586 | 215 | 80839 | 2013/2014 | March-2014 | 3 | 2014
30189 | Line Down | 2014-03-27 05:09 | 2014-03-27 | 2014-03-27 11:32 | Calculated | 705 | 705 - Recloser with Bypass & Links 705 |  | 103SEG705-1736 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 381 | 22 | 24560 | 6424 | 0.26156 | 0.00089577 | 147.5 | 43982 | 2013/2014 | March-2014 | 3 | 2014
30190 | PD Analysis | 2014-03-27 09:23 | 2014-03-27 | 2014-03-27 17:49 | Calculated | 5973 | 5973 - Load Break Switch 5973 |  | 419SEG5973 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 96 | 6 | 24560 | 368 | 0.01498 | 0.0002443 | 2450 | 152600 | 2013/2014 | March-2014 | 3 | 2014
30191 | Faulty Transformer | 2014-03-27 10:11 | 2014-03-27 | 2014-03-27 11:57 | Calculated | TF2048 | TF2048 - Transformer Fuse: T2048 |  | 117SEG1729 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 106 | 2 | 24560 | 212 | 0.00863 | 8.1433e-05 | 10 | 1060 | 2013/2014 | March-2014 | 3 | 2014
30192 | Birds | 2014-03-27 14:11 | 2014-03-27 | 2014-03-27 16:32 | Calculated | TF17H02 | TF17H02 - Transformer Fuse: 17H02 |  | 410SEG5511-5517 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 141 | 2 | 24560 | 282 | 0.01148 | 8.1433e-05 | 10 | 1410 | 2013/2014 | March-2014 | 3 | 2014
30193 | Birds | 2014-03-27 18:40 | 2014-03-27 | 2014-03-27 19:32 | Calculated | TF02R02 | TF02R02 - Transformer Fuse: 02R02 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 2 | 24560 | 104 | 0.00423 | 8.1433e-05 | 10 | 520 | 2013/2014 | March-2014 | 3 | 2014
30195 | PD Analysis Whakapapa | 2014-03-28 10:41 | 2014-03-28 | 2014-03-28 17:40 | Calculated | 5973 | 5973 - Load Break Switch 5973 |  | 419SEG5973 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 41 | 5 | 24560 | 205 | 0.00835 | 0.00020358 | 900 | 36900 | 2013/2014 | March-2014 | 3 | 2014
30196 | Partial Discharge Analysis Whakapapa (Cable testing) | 2014-03-29 09:43 | 2014-03-29 | 2014-03-29 17:58 | Calculated | 5973 | 5973 - Load Break Switch 5973 |  | 419SEG5973 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 211 | 19 | 24560 | 4009 | 0.16323 | 0.00077362 | 775 | 163524 | 2013/2014 | March-2014 | 3 | 2014
30198 | Hv Fuse Blown - Branch on Line | 2014-03-29 12:39 | 2014-03-29 | 2014-03-29 15:18 | Calculated | TF2748 | TF2748 - Transformer Fuse: T2748 |  | 128SEG1637 | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 159 | 1 | 24560 | 159 | 0.00647 | 4.0717e-05 | 10 | 1590 | 2013/2014 | March-2014 | 3 | 2014
30197 | Faulty DDO | 2014-03-29 13:25 | 2014-03-29 | 2014-03-29 17:13 | Calculated | 5905 | 5905 - Earth Working Link 5905 |  | 417SEG5905 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 228 | 30 | 24560 | 6840 | 0.2785 | 0.0012215 | 130 | 29639 | 2013/2014 | March-2014 | 3 | 2014
30200 | P.D Analysis Whakapapa | 2014-03-30 14:15 | 2014-03-30 | 2014-03-30 16:26 | Calculated | 6774 | 6774 - Circuit Breaker 6774 |  | 419SEG6774-6172 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 49 | 138 | 24560 | 4053 | 0.16502 | 0.0056189 | 12065 | 385069 | 2013/2014 | March-2014 | 3 | 2014
30202 | Refer 2014 / 157 Pole & X Arm replacement | 2014-03-31 09:04 | 2014-03-31 | 2014-03-31 17:18 | Calculated | 5646 | 5646 - Fused Link 5646 |  | 413SEG5646-5883 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 492 | 67 | 24560 | 14611 | 0.59491 | 0.002728 | 437.5 | 87252 | 2013/2014 | March-2014 | 3 | 2014
30201 | Refer 2014 / 135 Install New Poles, Relpace X Arms, Install 3rd Conductor | 2014-03-31 09:05 | 2014-03-31 | 2014-03-31 16:12 | Calculated | 371 | 371 - Air Break Switch 371 |  | 122SEG371-633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 427 | 46 | 24560 | 8518 | 0.34682 | 0.001873 | 315 | 66524 | 2013/2014 | March-2014 | 3 | 2014
Formulas:
calcByDate = INT([Interrupted])

## (2b)_2010-14_dailyAggregates
2010-2014 daily aggregate data |  |  | Boundaries | SAIDI | SAIFI | IF(SAIDI_Actual>refSAIDI,refSAIDI,SAIDI_Actual)
Outage Extra Records from Basix : 19 September 2014 |  |  | int(Interrupted) | 21.6659 | 0.26757 | IF(SAIFI_Actual>refSAIFI,refSAIFI,SAIFI_Actual)
NB: 2014 records have audited following the 53ZD information request.
FinYear | Row Labels | SAIDI Actual | SAIFI Actual | SAIDI Normalised | SAIFI Normalised
2009/2010 | 2009-04-01 | 0.24504 | 0.00078418 | 0.24504 | 0.00078418
2009/2010 | 2009-04-02 | 0.26539 | 0.00086673 | 0.26539 | 0.00086673
2009/2010 | 2009-04-03 | 0.66759 | 0.0019811 | 0.66759 | 0.0019811
2009/2010 | 2009-04-04 | 0.00182 | 0.00016509 | 0.00182 | 0.00016509
2009/2010 | 2009-04-06 | 0.11358 | 0.00066037 | 0.11358 | 0.00066037
2009/2010 | 2009-04-07 | 0.41801 | 0.021875 | 0.41801 | 0.021875
2009/2010 | 2009-04-08 | 1.869 | 0.0061084 | 1.869 | 0.0061084
2009/2010 | 2009-04-09 | 1.0522 | 0.0054067 | 1.0522 | 0.0054067
2009/2010 | 2009-04-10 | 0.10772 | 0.0023938 | 0.10772 | 0.0023938
2009/2010 | 2009-04-12 | 0.14 | 0.0021875 | 0.14 | 0.0021875
2009/2010 | 2009-04-14 | 0.80795 | 0.0055306 | 0.80795 | 0.0055306
2009/2010 | 2009-04-15 | 3.1447 | 0.03826 | 3.1447 | 0.03826
2009/2010 | 2009-04-16 | 1.9524 | 0.012423 | 1.9524 | 0.012423
2009/2010 | 2009-04-17 | 0.49184 | 0.0028891 | 0.49184 | 0.0028891
2009/2010 | 2009-04-19 | 1.2382 | 0.011061 | 1.2382 | 0.011061
2009/2010 | 2009-04-20 | 3.1468 | 0.016509 | 3.1468 | 0.016509
2009/2010 | 2009-04-21 | 0.62826 | 0.00227 | 0.62826 | 0.00227
2009/2010 | 2009-04-22 | 0.95038 | 0.0061497 | 0.95038 | 0.0061497
2009/2010 | 2009-04-23 | 0.11433 | 0.000454 | 0.11433 | 0.000454
2009/2010 | 2009-04-24 | 0.02836 | 0.00041273 | 0.02836 | 0.00041273
2009/2010 | 2009-04-25 | 0.01197 | 8.2546e-05 | 0.01197 | 8.2546e-05
2009/2010 | 2009-04-26 | 0.03727 | 0.00028891 | 0.03727 | 0.00028891
2009/2010 | 2009-04-27 | 0.15461 | 0.00070164 | 0.15461 | 0.00070164
2009/2010 | 2009-04-29 | 0.71839 | 0.0027653 | 0.71839 | 0.0027653
2009/2010 | 2009-04-30 | 0.0229 | 0.001362 | 0.0229 | 0.001362
2009/2010 | 2009-05-01 | 1.0165 | 0.0046187 | 1.0165 | 0.0046187
2009/2010 | 2009-05-02 | 0.8743 | 0.0015258 | 0.8743 | 0.0015258
2009/2010 | 2009-05-03 | 0.0019 | 4.1239e-05 | 0.0019 | 4.1239e-05
2009/2010 | 2009-05-05 | 0.27168 | 0.0030104 | 0.27168 | 0.0030104
2009/2010 | 2009-05-06 | 1.8955 | 0.012867 | 1.8955 | 0.012867
2009/2010 | 2009-05-07 | 0.35725 | 0.0014021 | 0.35725 | 0.0014021
2009/2010 | 2009-05-08 | 0.22038 | 0.0012784 | 0.22038 | 0.0012784
2009/2010 | 2009-05-09 | 0.1659 | 0.0032991 | 0.1659 | 0.0032991
2009/2010 | 2009-05-10 | 0.16186 | 0.001031 | 0.16186 | 0.001031
2009/2010 | 2009-05-11 | 0.23424 | 0.0032579 | 0.23424 | 0.0032579
2009/2010 | 2009-05-12 | 0.29956 | 0.084952 | 0.29956 | 0.084952
2009/2010 | 2009-05-13 | 0.95456 | 0.016001 | 0.95456 | 0.016001
2009/2010 | 2009-05-14 | 0.58554 | 0.0051136 | 0.58554 | 0.0051136
2009/2010 | 2009-05-15 | 1.7515 | 0.01464 | 1.7515 | 0.01464
2009/2010 | 2009-05-18 | 0.22999 | 0.0019382 | 0.22999 | 0.0019382
2009/2010 | 2009-05-19 | 1.1885 | 0.0091138 | 1.1885 | 0.0091138
2009/2010 | 2009-05-20 | 0.11287 | 0.00028867 | 0.11287 | 0.00028867
2009/2010 | 2009-05-21 | 1.4954 | 0.0086602 | 1.4954 | 0.0086602
2009/2010 | 2009-05-22 | 0.06082 | 0.001031 | 0.06082 | 0.001031
2009/2010 | 2009-05-25 | 0.30283 | 0.0018145 | 0.30283 | 0.0018145
2009/2010 | 2009-05-26 | 0.35115 | 0.001031 | 0.35115 | 0.001031
2009/2010 | 2009-05-27 | 0.9311 | 0.015258 | 0.9311 | 0.015258
2009/2010 | 2009-05-28 | 0.36393 | 0.001031 | 0.36393 | 0.001031
2009/2010 | 2009-05-29 | 0.03678 | 0.00037115 | 0.03678 | 0.00037115
2009/2010 | 2009-05-30 | 0.00495 | 8.2478e-05 | 0.00495 | 8.2478e-05
2009/2010 | 2009-06-01 | 0.20461 | 0.0041227 | 0.20461 | 0.0041227
2009/2010 | 2009-06-02 | 0.58476 | 0.0016491 | 0.58476 | 0.0016491
2009/2010 | 2009-06-03 | 0.60768 | 0.0017315 | 0.60768 | 0.0017315
2009/2010 | 2009-06-04 | 0.42554 | 0.0035043 | 0.42554 | 0.0035043
2009/2010 | 2009-06-05 | 1.55 | 0.020531 | 1.55 | 0.020531
2009/2010 | 2009-06-06 | 0.14503 | 0.0016903 | 0.14503 | 0.0016903
2009/2010 | 2009-06-07 | 0.00911 | 4.1227e-05 | 0.00911 | 4.1227e-05
2009/2010 | 2009-06-08 | 0 | 0 | 0 | 0
2009/2010 | 2009-06-09 | 0.0975 | 0.00065963 | 0.0975 | 0.00065963
2009/2010 | 2009-06-10 | 0.96397 | 0.0028859 | 0.96397 | 0.0028859
2009/2010 | 2009-06-11 | 0.85917 | 0.0065139 | 0.85917 | 0.0065139
2009/2010 | 2009-06-12 | 2.103 | 0.0068437 | 2.103 | 0.0068437
2009/2010 | 2009-06-14 | 0.08889 | 0.00082454 | 0.08889 | 0.00082454
2009/2010 | 2009-06-16 | 0.05409 | 0.00032982 | 0.05409 | 0.00032982
2009/2010 | 2009-06-17 | 3.0812 | 0.019995 | 3.0812 | 0.019995
2009/2010 | 2009-06-18 | 1.3013 | 0.0042464 | 1.3013 | 0.0042464
2009/2010 | 2009-06-19 | 0.51695 | 0.012079 | 0.51695 | 0.012079
2009/2010 | 2009-06-21 | 0.05256 | 0.00070086 | 0.05256 | 0.00070086
2009/2010 | 2009-06-22 | 0.10389 | 0.0014429 | 0.10389 | 0.0014429
2009/2010 | 2009-06-23 | 1.7693 | 0.010059 | 1.7693 | 0.010059
2009/2010 | 2009-06-24 | 0.24822 | 0.00082454 | 0.24822 | 0.00082454
2009/2010 | 2009-06-25 | 0.30364 | 0.00090699 | 0.30364 | 0.00090699
2009/2010 | 2009-06-26 | 18.8544 | 0.069715 | 18.8544 | 0.069715
2009/2010 | 2009-06-28 | 19.4222 | 0.058377 | 19.4222 | 0.058377
2009/2010 | 2009-06-29 | 1.3145 | 0.017068 | 1.3145 | 0.017068
2009/2010 | 2009-06-30 | 0.06976 | 0.0030096 | 0.06976 | 0.0030096
2009/2010 | 2009-07-02 | 1.0163 | 0.0040104 | 1.0163 | 0.0040104
2009/2010 | 2009-07-03 | 0.31807 | 0.0068218 | 0.31807 | 0.0068218
2009/2010 | 2009-07-06 | 0.09467 | 0.00057882 | 0.09467 | 0.00057882
2009/2010 | 2009-07-07 | 0.27449 | 0.0032249 | 0.27449 | 0.0032249
2009/2010 | 2009-07-09 | 0.66957 | 0.00492 | 0.66957 | 0.00492
2009/2010 | 2009-07-10 | 0.7905 | 0.0027287 | 0.7905 | 0.0027287
2009/2010 | 2009-07-12 | 1.2157 | 0.0075247 | 1.2157 | 0.0075247
2009/2010 | 2009-07-13 | 0.13656 | 0.0007442 | 0.13656 | 0.0007442
2009/2010 | 2009-07-14 | 0.5042 | 0.0015297 | 0.5042 | 0.0015297
2009/2010 | 2009-07-16 | 3.1057 | 0.014553 | 3.1057 | 0.014553
2009/2010 | 2009-07-17 | 0.86625 | 0.0040104 | 0.86625 | 0.0040104
2009/2010 | 2009-07-18 | 0.28561 | 0.025964 | 0.28561 | 0.025964
2009/2010 | 2009-07-19 | 0.57892 | 0.01137 | 0.57892 | 0.01137
2009/2010 | 2009-07-20 | 3.9398 | 0.020342 | 3.9398 | 0.020342
2009/2010 | 2009-07-22 | 0.02427 | 0.00020672 | 0.02427 | 0.00020672
2009/2010 | 2009-07-23 | 1.2897 | 0.03229 | 1.2897 | 0.03229
2009/2010 | 2009-07-24 | 0.10406 | 0.0024807 | 0.10406 | 0.0024807
2009/2010 | 2009-07-26 | 1.0246 | 0.1397 | 1.0246 | 0.1397
2009/2010 | 2009-07-27 | 4.8343 | 0.042998 | 4.8343 | 0.042998
2009/2010 | 2009-07-28 | 0.53629 | 0.017199 | 0.53629 | 0.017199
2009/2010 | 2009-07-29 | 0.005 | 4.1345e-05 | 0.005 | 4.1345e-05
2009/2010 | 2009-07-30 | 0.03465 | 0.0003721 | 0.03465 | 0.0003721
2009/2010 | 2009-07-31 | 0.45264 | 0.002646 | 0.45264 | 0.002646
2009/2010 | 2009-08-01 | 0.31366 | 0.013352 | 0.31366 | 0.013352
2009/2010 | 2009-08-02 | 0.34326 | 0.00053737 | 0.34326 | 0.00053737
2009/2010 | 2009-08-03 | 0.01513 | 0.00012401 | 0.01513 | 0.00012401
2009/2010 | 2009-08-04 | 0.00637 | 8.2672e-05 | 0.00637 | 8.2672e-05
2009/2010 | 2009-08-05 | 0.1317 | 0.0033069 | 0.1317 | 0.0033069
2009/2010 | 2009-08-06 | 0 | 0 | 0 | 0
2009/2010 | 2009-08-07 | 0.18936 | 0.00062004 | 0.18936 | 0.00062004
2009/2010 | 2009-08-09 | 0.05266 | 0.0010747 | 0.05266 | 0.0010747
2009/2010 | 2009-08-11 | 1.2763 | 0.0083085 | 1.2763 | 0.0083085
2009/2010 | 2009-08-12 | 0.39352 | 0.0012814 | 0.39352 | 0.0012814
2009/2010 | 2009-08-13 | 0.0038 | 4.1336e-05 | 0.0038 | 4.1336e-05
2009/2010 | 2009-08-14 | 0.28646 | 0.0022735 | 0.28646 | 0.0022735
2009/2010 | 2009-08-15 | 0.01819 | 0.00016534 | 0.01819 | 0.00016534
2009/2010 | 2009-08-17 | 0.08644 | 0.00037202 | 0.08644 | 0.00037202
2009/2010 | 2009-08-18 | 0.2452 | 0.0028108 | 0.2452 | 0.0028108
2009/2010 | 2009-08-19 | 0.00219 | 4.1336e-05 | 0.00219 | 4.1336e-05
2009/2010 | 2009-08-20 | 0.98495 | 0.0064897 | 0.98495 | 0.0064897
2009/2010 | 2009-08-21 | 0.54088 | 0.005167 | 0.54088 | 0.005167
2009/2010 | 2009-08-22 | 0.00347 | 8.2672e-05 | 0.00347 | 8.2672e-05
2009/2010 | 2009-08-23 | 0.80035 | 0.0026042 | 0.80035 | 0.0026042
2009/2010 | 2009-08-24 | 0.14902 | 0.0014054 | 0.14902 | 0.0014054
2009/2010 | 2009-08-25 | 7.6826 | 0.13327 | 7.6826 | 0.13327
2009/2010 | 2009-08-26 | 5.5894 | 0.009714 | 5.5894 | 0.009714
2009/2010 | 2009-08-27 | 0.2605 | 0.0019015 | 0.2605 | 0.0019015
2009/2010 | 2009-08-28 | 0.46448 | 0.0033482 | 0.46448 | 0.0033482
2009/2010 | 2009-08-30 | 3.5683 | 0.036045 | 3.5683 | 0.036045
2009/2010 | 2009-08-31 | 4.8942 | 0.020503 | 4.8942 | 0.020503
2009/2010 | 2009-09-01 | 0.1215 | 0.0037592 | 0.1215 | 0.0037592
2009/2010 | 2009-09-02 | 0.04808 | 0.00049572 | 0.04808 | 0.00049572
2009/2010 | 2009-09-03 | 0.28698 | 0.0017763 | 0.28698 | 0.0017763
2009/2010 | 2009-09-04 | 0.03883 | 0.00020655 | 0.03883 | 0.00020655
2009/2010 | 2009-09-05 | 0.06816 | 8.2621e-05 | 0.06816 | 8.2621e-05
2009/2010 | 2009-09-06 | 0.09997 | 0.0014046 | 0.09997 | 0.0014046
2009/2010 | 2009-09-07 | 0.01677 | 0.00016524 | 0.01677 | 0.00016524
2009/2010 | 2009-09-09 | 0.17152 | 0.00049572 | 0.17152 | 0.00049572
2009/2010 | 2009-09-10 | 0.04895 | 0.00037179 | 0.04895 | 0.00037179
2009/2010 | 2009-09-11 | 0 | 0 | 0 | 0
2009/2010 | 2009-09-12 | 0.24005 | 0.0016111 | 0.24005 | 0.0016111
2009/2010 | 2009-09-13 | 0.00454 | 4.131e-05 | 0.00454 | 4.131e-05
2009/2010 | 2009-09-14 | 0.14206 | 0.00066097 | 0.14206 | 0.00066097
2009/2010 | 2009-09-16 | 1.7763 | 0.0049572 | 1.7763 | 0.0049572
2009/2010 | 2009-09-17 | 2.2102 | 0.0078903 | 2.2102 | 0.0078903
2009/2010 | 2009-09-18 | 0.03586 | 0.00016524 | 0.03586 | 0.00016524
2009/2010 | 2009-09-19 | 4.2579 | 0.017226 | 4.2579 | 0.017226
2009/2010 | 2009-09-21 | 0.10637 | 0.00037179 | 0.10637 | 0.00037179
2009/2010 | 2009-09-22 | 0.95584 | 0.0051638 | 0.95584 | 0.0051638
2009/2010 | 2009-09-23 | 0.73768 | 0.0092122 | 0.73768 | 0.0092122
2009/2010 | 2009-09-24 | 0.63593 | 0.0049159 | 0.63593 | 0.0049159
2009/2010 | 2009-09-25 | 0.06081 | 0.0012806 | 0.06081 | 0.0012806
2009/2010 | 2009-09-26 | 0.36808 | 0.0033461 | 0.36808 | 0.0033461
2009/2010 | 2009-09-27 | 1.3981 | 0.01388 | 1.3981 | 0.01388
2009/2010 | 2009-09-28 | 0.04858 | 0.00057835 | 0.04858 | 0.00057835
2009/2010 | 2009-09-29 | 0.73838 | 0.016442 | 0.73838 | 0.016442
2009/2010 | 2009-09-30 | 0.05226 | 4.131e-05 | 0.05226 | 4.131e-05
2009/2010 | 2009-10-01 | 0.03604 | 4.1288e-05 | 0.03604 | 4.1288e-05
2009/2010 | 2009-10-02 | 1.5336 | 0.015277 | 1.5336 | 0.015277
2009/2010 | 2009-10-03 | 0.0114 | 0.0037985 | 0.0114 | 0.0037985
2009/2010 | 2009-10-04 | 47.5593 | 0.10756 | 21.6659 | 0.10756
2009/2010 | 2009-10-05 | 3.364 | 0.032989 | 3.364 | 0.032989
2009/2010 | 2009-10-06 | 0.01742 | 0.00012386 | 0.01742 | 0.00012386
2009/2010 | 2009-10-07 | 0.05161 | 0.00078448 | 0.05161 | 0.00078448
2009/2010 | 2009-10-08 | 1.7371 | 0.014368 | 1.7371 | 0.014368
2009/2010 | 2009-10-09 | 0.03266 | 0.00041288 | 0.03266 | 0.00041288
2009/2010 | 2009-10-10 | 0.45313 | 0.0020644 | 0.45313 | 0.0020644
2009/2010 | 2009-10-11 | 0.53515 | 0.015111 | 0.53515 | 0.015111
2009/2010 | 2009-10-13 | 0.50835 | 0.0094963 | 0.50835 | 0.0094963
2009/2010 | 2009-10-14 | 1.1135 | 0.0059042 | 1.1135 | 0.0059042
2009/2010 | 2009-10-15 | 0.02514 | 0.00024773 | 0.02514 | 0.00024773
2009/2010 | 2009-10-16 | 0.01817 | 0.00020644 | 0.01817 | 0.00020644
2009/2010 | 2009-10-17 | 1.4839 | 0.054707 | 1.4839 | 0.054707
2009/2010 | 2009-10-18 | 0.01259 | 0.00020644 | 0.01259 | 0.00020644
2009/2010 | 2009-10-19 | 0.09413 | 0.00037159 | 0.09413 | 0.00037159
2009/2010 | 2009-10-20 | 0.00611 | 8.2576e-05 | 0.00611 | 8.2576e-05
2009/2010 | 2009-10-22 | 0.74967 | 0.0040875 | 0.74967 | 0.0040875
2009/2010 | 2009-10-23 | 0.19245 | 0.00078448 | 0.19245 | 0.00078448
2009/2010 | 2009-10-26 | 0.00595 | 0.00012386 | 0.00595 | 0.00012386
2009/2010 | 2009-10-27 | 0.33947 | 0.0043353 | 0.33947 | 0.0043353
2009/2010 | 2009-10-28 | 3.1221 | 0.068456 | 3.1221 | 0.068456
2009/2010 | 2009-10-29 | 0.50541 | 0.0068538 | 0.50541 | 0.0068538
2009/2010 | 2009-10-30 | 0.00227 | 4.1288e-05 | 0.00227 | 4.1288e-05
2009/2010 | 2009-11-01 | 0.06857 | 0.00037068 | 0.06857 | 0.00037068
2009/2010 | 2009-11-02 | 0.05433 | 0.00045305 | 0.05433 | 0.00045305
2009/2010 | 2009-11-03 | 0.04325 | 0.0012356 | 0.04325 | 0.0012356
2009/2010 | 2009-11-04 | 1.2839 | 0.0049423 | 1.2839 | 0.0049423
2009/2010 | 2009-11-05 | 1.2691 | 0.087932 | 1.2691 | 0.087932
2009/2010 | 2009-11-06 | 0.10848 | 0.00070016 | 0.10848 | 0.00070016
2009/2010 | 2009-11-07 | 0 | 0 | 0 | 0
2009/2010 | 2009-11-09 | 0.03476 | 0.00016474 | 0.03476 | 0.00016474
2009/2010 | 2009-11-10 | 0.68212 | 0.0031301 | 0.68212 | 0.0031301
2009/2010 | 2009-11-11 | 0.02059 | 0.00041186 | 0.02059 | 0.00041186
2009/2010 | 2009-11-12 | 0.05437 | 0.00020593 | 0.05437 | 0.00020593
2009/2010 | 2009-11-13 | 0.01874 | 0.0002883 | 0.01874 | 0.0002883
2009/2010 | 2009-11-14 | 0.26936 | 0.0035832 | 0.26936 | 0.0035832
2009/2010 | 2009-11-16 | 0.54321 | 0.0046129 | 0.54321 | 0.0046129
2009/2010 | 2009-11-17 | 0.15911 | 0.00086491 | 0.15911 | 0.00086491
2009/2010 | 2009-11-18 | 0.95927 | 0.069399 | 0.95927 | 0.069399
2009/2010 | 2009-11-19 | 0.07071 | 0.00032949 | 0.07071 | 0.00032949
2009/2010 | 2009-11-20 | 0.09456 | 0.00032949 | 0.09456 | 0.00032949
2009/2010 | 2009-11-21 | 0.11417 | 0.0017298 | 0.11417 | 0.0017298
2009/2010 | 2009-11-23 | 0.17694 | 0.00065898 | 0.17694 | 0.00065898
2009/2010 | 2009-11-24 | 0.96421 | 0.017381 | 0.96421 | 0.017381
2009/2010 | 2009-11-25 | 0.01256 | 4.1186e-05 | 0.01256 | 4.1186e-05
2009/2010 | 2009-11-26 | 2.4819 | 0.0065486 | 2.4819 | 0.0065486
2009/2010 | 2009-11-27 | 0.17925 | 0.0021417 | 0.17925 | 0.0021417
2009/2010 | 2009-11-28 | 0.00527 | 4.1186e-05 | 0.00527 | 4.1186e-05
2009/2010 | 2009-11-29 | 0.05869 | 0.00078254 | 0.05869 | 0.00078254
2009/2010 | 2009-11-30 | 0.0089 | 0.00016474 | 0.0089 | 0.00016474
2009/2010 | 2009-12-01 | 0.01547 | 8.2332e-05 | 0.01547 | 8.2332e-05
2009/2010 | 2009-12-02 | 0.20995 | 0.016549 | 0.20995 | 0.016549
2009/2010 | 2009-12-03 | 0.10012 | 0.00065865 | 0.10012 | 0.00065865
2009/2010 | 2009-12-04 | 0.0175 | 0.00020583 | 0.0175 | 0.00020583
2009/2010 | 2009-12-05 | 0.00412 | 8.2332e-05 | 0.00412 | 8.2332e-05
2009/2010 | 2009-12-06 | 0.01787 | 0.00028816 | 0.01787 | 0.00028816
2009/2010 | 2009-12-07 | 0.01111 | 0.00053516 | 0.01111 | 0.00053516
2009/2010 | 2009-12-08 | 0.0466 | 0.0046517 | 0.0466 | 0.0046517
2009/2010 | 2009-12-09 | 0.11518 | 0.0012761 | 0.11518 | 0.0012761
2009/2010 | 2009-12-10 | 1.4094 | 0.0048987 | 1.4094 | 0.0048987
2009/2010 | 2009-12-11 | 2.6696 | 0.014285 | 2.6696 | 0.014285
2009/2010 | 2009-12-12 | 0.09859 | 0.0013996 | 0.09859 | 0.0013996
2009/2010 | 2009-12-13 | 0.00823 | 8.2332e-05 | 0.00823 | 8.2332e-05
2009/2010 | 2009-12-14 | 1.3172 | 0.0083155 | 1.3172 | 0.0083155
2009/2010 | 2009-12-15 | 0.99066 | 0.01165 | 0.99066 | 0.01165
2009/2010 | 2009-12-16 | 0.01511 | 0.0026346 | 0.01511 | 0.0026346
2009/2010 | 2009-12-17 | 0.94381 | 0.0040754 | 0.94381 | 0.0040754
2009/2010 | 2009-12-18 | 0.40668 | 0.016178 | 0.40668 | 0.016178
2009/2010 | 2009-12-19 | 0.05495 | 0.00028816 | 0.05495 | 0.00028816
2009/2010 | 2009-12-20 | 4.4197 | 0.11403 | 4.4197 | 0.11403
2009/2010 | 2009-12-21 | 0.02824 | 0.00057632 | 0.02824 | 0.00057632
2009/2010 | 2009-12-22 | 2.6403 | 0.024988 | 2.6403 | 0.024988
2009/2010 | 2009-12-23 | 0.10251 | 0.0024288 | 0.10251 | 0.0024288
2009/2010 | 2009-12-24 | 0.26972 | 0.0016055 | 0.26972 | 0.0016055
2009/2010 | 2009-12-25 | 0.00181 | 4.1166e-05 | 0.00181 | 4.1166e-05
2009/2010 | 2009-12-26 | 0.23617 | 0.0025523 | 0.23617 | 0.0025523
2009/2010 | 2009-12-27 | 0.00531 | 0.0001235 | 0.00531 | 0.0001235
2009/2010 | 2009-12-28 | 0.0881 | 0.0016878 | 0.0881 | 0.0016878
2009/2010 | 2009-12-30 | 0.06599 | 0.001482 | 0.06599 | 0.001482
2009/2010 | 2009-12-31 | 0.06937 | 0.011197 | 0.06937 | 0.011197
2009/2010 | 2010-01-01 | 0.00415 | 4.1103e-05 | 0.00415 | 4.1103e-05
2009/2010 | 2010-01-02 | 0.04764 | 0.00078096 | 0.04764 | 0.00078096
2009/2010 | 2010-01-03 | 0 | 0 | 0 | 0
2009/2010 | 2010-01-04 | 1.8017 | 0.016976 | 1.8017 | 0.016976
2009/2010 | 2010-01-05 | 0.38989 | 0.002795 | 0.38989 | 0.002795
2009/2010 | 2010-01-06 | 0.02429 | 0.00024662 | 0.02429 | 0.00024662
2009/2010 | 2010-01-07 | 0.052 | 0.001192 | 0.052 | 0.001192
2009/2010 | 2010-01-10 | 0.09918 | 0.00049324 | 0.09918 | 0.00049324
2009/2010 | 2010-01-11 | 0.02631 | 0.00065765 | 0.02631 | 0.00065765
2009/2010 | 2010-01-12 | 1.1966 | 0.021374 | 1.1966 | 0.021374
2009/2010 | 2010-01-13 | 0 | 0 | 0 | 0
2009/2010 | 2010-01-14 | 1.5713 | 0.0050968 | 1.5713 | 0.0050968
2009/2010 | 2010-01-15 | 0.01545 | 0.00016441 | 0.01545 | 0.00016441
2009/2010 | 2010-01-17 | 0.01171 | 0.00012331 | 0.01171 | 0.00012331
2009/2010 | 2010-01-18 | 0.55138 | 0.0048913 | 0.55138 | 0.0048913
2009/2010 | 2010-01-19 | 0.05344 | 0.00057544 | 0.05344 | 0.00057544
2009/2010 | 2010-01-20 | 0.1294 | 0.0012742 | 0.1294 | 0.0012742
2009/2010 | 2010-01-21 | 0.08571 | 0.0013153 | 0.08571 | 0.0013153
2009/2010 | 2010-01-22 | 0.17382 | 0.00049324 | 0.17382 | 0.00049324
2009/2010 | 2010-01-24 | 0.00654 | 0.00012331 | 0.00654 | 0.00012331
2009/2010 | 2010-01-25 | 0.22356 | 0.001973 | 0.22356 | 0.001973
2009/2010 | 2010-01-26 | 10.2799 | 0.16528 | 10.2799 | 0.16528
2009/2010 | 2010-01-27 | 6.38 | 0.02347 | 6.38 | 0.02347
2009/2010 | 2010-01-28 | 0.45531 | 0.0024251 | 0.45531 | 0.0024251
2009/2010 | 2010-01-29 | 0.11389 | 0.00045214 | 0.11389 | 0.00045214
2009/2010 | 2010-01-30 | 0.16372 | 0.0020141 | 0.16372 | 0.0020141
2009/2010 | 2010-01-31 | 0.88206 | 0.021086 | 0.88206 | 0.021086
2009/2010 | 2010-02-01 | 1.0298 | 0.001023 | 1.0298 | 0.001023
2009/2010 | 2010-02-02 | 0.87225 | 0.015346 | 0.87225 | 0.015346
2009/2010 | 2010-02-03 | 0 | 0 | 0 | 0
2009/2010 | 2010-02-04 | 0.01768 | 0.00012276 | 0.01768 | 0.00012276
2009/2010 | 2010-02-05 | 0.22457 | 0.005197 | 0.22457 | 0.005197
2009/2010 | 2010-02-06 | 0 | 0 | 0 | 0
2009/2010 | 2010-02-07 | 0.55838 | 0.0050743 | 0.55838 | 0.0050743
2009/2010 | 2010-02-08 | 0.00618 | 8.1843e-05 | 0.00618 | 8.1843e-05
2009/2010 | 2010-02-09 | 0.27038 | 0.0035602 | 0.27038 | 0.0035602
2009/2010 | 2010-02-10 | 0.22204 | 0.001555 | 0.22204 | 0.001555
2009/2010 | 2010-02-11 | 1.4723 | 0.013668 | 1.4723 | 0.013668
2009/2010 | 2010-02-12 | 0.09683 | 0.00053198 | 0.09683 | 0.00053198
2009/2010 | 2010-02-13 | 0.20465 | 0.0013913 | 0.20465 | 0.0013913
2009/2010 | 2010-02-15 | 0.56088 | 0.0038875 | 0.56088 | 0.0038875
2009/2010 | 2010-02-16 | 0.19966 | 0.0061792 | 0.19966 | 0.0061792
2009/2010 | 2010-02-17 | 0.00344 | 4.0922e-05 | 0.00344 | 4.0922e-05
2009/2010 | 2010-02-18 | 0.98994 | 0.007325 | 0.98994 | 0.007325
2009/2010 | 2010-02-19 | 0.05885 | 0.0017596 | 0.05885 | 0.0017596
2009/2010 | 2010-02-20 | 0.06511 | 0.0017596 | 0.06511 | 0.0017596
2009/2010 | 2010-02-21 | 0.07317 | 0.012195 | 0.07317 | 0.012195
2009/2010 | 2010-02-22 | 0.14282 | 0.00040922 | 0.14282 | 0.00040922
2009/2010 | 2010-02-23 | 0.02451 | 0.00020461 | 0.02451 | 0.00020461
2009/2010 | 2010-02-24 | 1.8542 | 0.0064247 | 1.8542 | 0.0064247
2009/2010 | 2010-02-25 | 1.0494 | 0.0050743 | 1.0494 | 0.0050743
2009/2010 | 2010-02-26 | 0.26627 | 0.00061382 | 0.26627 | 0.00061382
2009/2010 | 2010-02-28 | 0.00278 | 0.00016369 | 0.00278 | 0.00016369
2009/2010 | 2010-03-01 | 0.03171 | 0.00045017 | 0.03171 | 0.00045017
2009/2010 | 2010-03-02 | 0.876 | 0.0020462 | 0.876 | 0.0020462
2009/2010 | 2010-03-03 | 0.52933 | 0.0039697 | 0.52933 | 0.0039697
2009/2010 | 2010-03-04 | 0.23655 | 0.0015961 | 0.23655 | 0.0015961
2009/2010 | 2010-03-05 | 0.33067 | 0.002169 | 0.33067 | 0.002169
2009/2010 | 2010-03-06 | 0.00237 | 4.0925e-05 | 0.00237 | 4.0925e-05
2009/2010 | 2010-03-08 | 0.07801 | 0.001064 | 0.07801 | 0.001064
2009/2010 | 2010-03-09 | 0.07858 | 0.0003274 | 0.07858 | 0.0003274
2009/2010 | 2010-03-10 | 0.45439 | 0.0045836 | 0.45439 | 0.0045836
2009/2010 | 2010-03-11 | 0 | 0 | 0 | 0
2009/2010 | 2010-03-12 | 1.2133 | 0.013342 | 1.2133 | 0.013342
2009/2010 | 2010-03-16 | 0.63998 | 0.0038879 | 0.63998 | 0.0038879
2009/2010 | 2010-03-17 | 0.51041 | 0.0046245 | 0.51041 | 0.0046245
2009/2010 | 2010-03-18 | 2.8341 | 0.015388 | 2.8341 | 0.015388
2009/2010 | 2010-03-19 | 0.04476 | 0.0056886 | 0.04476 | 0.0056886
2009/2010 | 2010-03-21 | 0.32625 | 0.036423 | 0.32625 | 0.036423
2009/2010 | 2010-03-22 | 1.3925 | 0.011827 | 1.3925 | 0.011827
2009/2010 | 2010-03-23 | 0.27673 | 0.0023736 | 0.27673 | 0.0023736
2009/2010 | 2010-03-24 | 0.5671 | 0.0042153 | 0.5671 | 0.0042153
2009/2010 | 2010-03-25 | 0.32265 | 0.080377 | 0.32265 | 0.080377
2009/2010 | 2010-03-26 | 0.05386 | 0.00057295 | 0.05386 | 0.00057295
2009/2010 | 2010-03-29 | 0.69179 | 0.004911 | 0.69179 | 0.004911
2009/2010 | 2010-03-30 | 0.046 | 0.0001637 | 0.046 | 0.0001637
2009/2010 | 2010-03-31 | 0.60413 | 0.0061387 | 0.60413 | 0.0061387
2010/2011 | 2010-04-03 | 0.01997 | 0.0099853 | 0.01997 | 0.0099853
2010/2011 | 2010-04-04 | 0.00282 | 4.0923e-05 | 0.00282 | 4.0923e-05
2010/2011 | 2010-04-06 | 0.32518 | 0.0014732 | 0.32518 | 0.0014732
2010/2011 | 2010-04-07 | 0.028 | 0.00024554 | 0.028 | 0.00024554
2010/2011 | 2010-04-08 | 0.01207 | 0.00016369 | 0.01207 | 0.00016369
2010/2011 | 2010-04-09 | 0.07616 | 0.0045016 | 0.07616 | 0.0045016
2010/2011 | 2010-04-10 | 0.1321 | 0.0055656 | 0.1321 | 0.0055656
2010/2011 | 2010-04-12 | 0.0453 | 0.00036831 | 0.0453 | 0.00036831
2010/2011 | 2010-04-13 | 0.02164 | 0.00040923 | 0.02164 | 0.00040923
2010/2011 | 2010-04-14 | 0.79689 | 0.011172 | 0.79689 | 0.011172
2010/2011 | 2010-04-15 | 0.0072 | 8.1846e-05 | 0.0072 | 8.1846e-05
2010/2011 | 2010-04-16 | 0.38284 | 0.0024963 | 0.38284 | 0.0024963
2010/2011 | 2010-04-19 | 0.40104 | 0.0021689 | 0.40104 | 0.0021689
2010/2011 | 2010-04-20 | 0.5097 | 0.0033557 | 0.5097 | 0.0033557
2010/2011 | 2010-04-21 | 0.0755 | 0.00020462 | 0.0755 | 0.00020462
2010/2011 | 2010-04-22 | 0.49099 | 0.006384 | 0.49099 | 0.006384
2010/2011 | 2010-04-25 | 0.19619 | 0.00069569 | 0.19619 | 0.00069569
2010/2011 | 2010-04-26 | 1.333 | 0.0066296 | 1.333 | 0.0066296
2010/2011 | 2010-04-27 | 0.50732 | 0.0045016 | 0.50732 | 0.0045016
2010/2011 | 2010-04-28 | 0.66562 | 0.0029465 | 0.66562 | 0.0029465
2010/2011 | 2010-04-29 | 0.39439 | 0.0022917 | 0.39439 | 0.0022917
2010/2011 | 2010-04-30 | 1.3851 | 0.010886 | 1.3851 | 0.010886
2010/2011 | 2010-05-01 | 1.1932 | 0.01551 | 1.1932 | 0.01551
2010/2011 | 2010-05-03 | 0.9234 | 0.021648 | 0.9234 | 0.021648
2010/2011 | 2010-05-04 | 0.05332 | 0.00028646 | 0.05332 | 0.00028646
2010/2011 | 2010-05-05 | 0.22594 | 0.0043379 | 0.22594 | 0.0043379
2010/2011 | 2010-05-06 | 0.80806 | 0.0066705 | 0.80806 | 0.0066705
2010/2011 | 2010-05-07 | 0.20977 | 0.011131 | 0.20977 | 0.011131
2010/2011 | 2010-05-08 | 0.07231 | 0.0012686 | 0.07231 | 0.0012686
2010/2011 | 2010-05-10 | 0.2011 | 0.00073662 | 0.2011 | 0.00073662
2010/2011 | 2010-05-11 | 0.48383 | 0.0016779 | 0.48383 | 0.0016779
2010/2011 | 2010-05-12 | 0.36786 | 0.0025372 | 0.36786 | 0.0025372
2010/2011 | 2010-05-13 | 2.4187 | 0.013832 | 2.4187 | 0.013832
2010/2011 | 2010-05-14 | 0.37568 | 0.0024963 | 0.37568 | 0.0024963
2010/2011 | 2010-05-15 | 0.1941 | 0.00069569 | 0.1941 | 0.00069569
2010/2011 | 2010-05-16 | 0.07587 | 4.0923e-05 | 0.07587 | 4.0923e-05
2010/2011 | 2010-05-17 | 1.3817 | 0.0081028 | 1.3817 | 0.0081028
2010/2011 | 2010-05-18 | 7.078 | 0.03503 | 7.078 | 0.03503
2010/2011 | 2010-05-19 | 0.43493 | 0.0014732 | 0.43493 | 0.0014732
2010/2011 | 2010-05-20 | 0.36028 | 0.0037649 | 0.36028 | 0.0037649
2010/2011 | 2010-05-21 | 0.63096 | 0.0052791 | 0.63096 | 0.0052791
2010/2011 | 2010-05-22 | 0.04641 | 0.0028237 | 0.04641 | 0.0028237
2010/2011 | 2010-05-23 | 0.1479 | 8.1846e-05 | 0.1479 | 8.1846e-05
2010/2011 | 2010-05-25 | 0.02169 | 0.00024554 | 0.02169 | 0.00024554
2010/2011 | 2010-05-26 | 1.7246 | 0.012318 | 1.7246 | 0.012318
2010/2011 | 2010-05-27 | 0.93002 | 0.03147 | 0.93002 | 0.03147
2010/2011 | 2010-05-28 | 0.8388 | 0.0031102 | 0.8388 | 0.0031102
2010/2011 | 2010-05-29 | 1.6976 | 0.023326 | 1.6976 | 0.023326
2010/2011 | 2010-05-30 | 3.33 | 0.056106 | 3.33 | 0.056106
2010/2011 | 2010-05-31 | 0.25156 | 0.00081846 | 0.25156 | 0.00081846
2010/2011 | 2010-06-01 | 1.7362 | 0.014894 | 1.7362 | 0.014894
2010/2011 | 2010-06-02 | 0.773 | 0.0019179 | 0.773 | 0.0019179
2010/2011 | 2010-06-03 | 0.12356 | 0.0024484 | 0.12356 | 0.0024484
2010/2011 | 2010-06-04 | 0.22399 | 0.00061209 | 0.22399 | 0.00061209
2010/2011 | 2010-06-06 | 53.7472 | 0.064066 | 21.6659 | 0.064066
2010/2011 | 2010-06-07 | 4.7741 | 0.094834 | 4.7741 | 0.094834
2010/2011 | 2010-06-08 | 0.05382 | 0.00028564 | 0.05382 | 0.00028564
2010/2011 | 2010-06-09 | 0.00461 | 4.0806e-05 | 0.00461 | 4.0806e-05
2010/2011 | 2010-06-10 | 2.4988 | 0.051538 | 2.4988 | 0.051538
2010/2011 | 2010-06-14 | 0.95259 | 0.0090182 | 0.95259 | 0.0090182
2010/2011 | 2010-06-15 | 0.62369 | 0.013752 | 0.62369 | 0.013752
2010/2011 | 2010-06-16 | 0.04998 | 0.0013874 | 0.04998 | 0.0013874
2010/2011 | 2010-06-17 | 0.1571 | 0.0011018 | 0.1571 | 0.0011018
2010/2011 | 2010-06-18 | 0.21815 | 0.0036318 | 0.21815 | 0.0036318
2010/2011 | 2010-06-20 | 0.02204 | 0.00024484 | 0.02204 | 0.00024484
2010/2011 | 2010-06-21 | 0.51216 | 0.0035502 | 0.51216 | 0.0035502
2010/2011 | 2010-06-22 | 1.4836 | 0.016037 | 1.4836 | 0.016037
2010/2011 | 2010-06-23 | 0.88505 | 0.0077532 | 0.88505 | 0.0077532
2010/2011 | 2010-06-24 | 0.17705 | 0.001265 | 0.17705 | 0.001265
2010/2011 | 2010-06-25 | 0.56093 | 0.012119 | 0.56093 | 0.012119
2010/2011 | 2010-06-26 | 0.23088 | 0.0035093 | 0.23088 | 0.0035093
2010/2011 | 2010-06-28 | 0.04872 | 8.1613e-05 | 0.04872 | 8.1613e-05
2010/2011 | 2010-06-29 | 1.0349 | 0.0032237 | 1.0349 | 0.0032237
2010/2011 | 2010-06-30 | 0.54274 | 0.0040806 | 0.54274 | 0.0040806
2010/2011 | 2010-07-01 | 0.87135 | 0.066955 | 0.87135 | 0.066955
2010/2011 | 2010-07-02 | 0.03162 | 0.031621 | 0.03162 | 0.031621
2010/2011 | 2010-07-05 | 0.35938 | 0.0036313 | 0.35938 | 0.0036313
2010/2011 | 2010-07-06 | 0.49644 | 0.0019177 | 0.49644 | 0.0019177
2010/2011 | 2010-07-07 | 0.18964 | 0.00057122 | 0.18964 | 0.00057122
2010/2011 | 2010-07-08 | 0.44823 | 0.0064466 | 0.44823 | 0.0064466
2010/2011 | 2010-07-09 | 0.25008 | 0.0023665 | 0.25008 | 0.0023665
2010/2011 | 2010-07-10 | 0.23134 | 0.00085683 | 0.23134 | 0.00085683
2010/2011 | 2010-07-11 | 0.55409 | 0.0062834 | 0.55409 | 0.0062834
2010/2011 | 2010-07-12 | 0.11612 | 0.001428 | 0.11612 | 0.001428
2010/2011 | 2010-07-13 | 0.00767 | 0.0001224 | 0.00767 | 0.0001224
2010/2011 | 2010-07-14 | 0.31271 | 0.0022033 | 0.31271 | 0.0022033
2010/2011 | 2010-07-15 | 2.3036 | 0.017708 | 2.3036 | 0.017708
2010/2011 | 2010-07-16 | 0.31319 | 0.007589 | 0.31319 | 0.007589
2010/2011 | 2010-07-17 | 0.20238 | 0.0015505 | 0.20238 | 0.0015505
2010/2011 | 2010-07-18 | 0.0164 | 0.00024481 | 0.0164 | 0.00024481
2010/2011 | 2010-07-19 | 0.05214 | 0.00024481 | 0.05214 | 0.00024481
2010/2011 | 2010-07-20 | 0.15451 | 0.032315 | 0.15451 | 0.032315
2010/2011 | 2010-07-21 | 0.16337 | 0.031743 | 0.16337 | 0.031743
2010/2011 | 2010-07-22 | 0.12991 | 0.0024073 | 0.12991 | 0.0024073
2010/2011 | 2010-07-25 | 0.46734 | 0.0042433 | 0.46734 | 0.0042433
2010/2011 | 2010-07-26 | 0.83077 | 0.0082011 | 0.83077 | 0.0082011
2010/2011 | 2010-07-27 | 1.4163 | 0.027255 | 1.4163 | 0.027255
2010/2011 | 2010-07-28 | 0.02142 | 0.0001224 | 0.02142 | 0.0001224
2010/2011 | 2010-07-29 | 0.07687 | 0.00016321 | 0.07687 | 0.00016321
2010/2011 | 2010-07-31 | 0.08654 | 0.0016321 | 0.08654 | 0.0016321
2010/2011 | 2010-08-01 | 1.6121 | 0.013997 | 1.6121 | 0.013997
2010/2011 | 2010-08-02 | 0.10512 | 8.1613e-05 | 0.10512 | 8.1613e-05
2010/2011 | 2010-08-03 | 0.01926 | 0.00032645 | 0.01926 | 0.00032645
2010/2011 | 2010-08-04 | 0.18865 | 0.0028156 | 0.18865 | 0.0028156
2010/2011 | 2010-08-05 | 0.62805 | 0.0021627 | 0.62805 | 0.0021627
2010/2011 | 2010-08-06 | 0.41916 | 0.0044071 | 0.41916 | 0.0044071
2010/2011 | 2010-08-09 | 0 | 0 | 0 | 0
2010/2011 | 2010-08-13 | 0.16123 | 0.00073451 | 0.16123 | 0.00073451
2010/2011 | 2010-08-14 | 0.07974 | 0.00057129 | 0.07974 | 0.00057129
2010/2011 | 2010-08-16 | 2.0676 | 0.075777 | 2.0676 | 0.075777
2010/2011 | 2010-08-17 | 0.55228 | 0.0055497 | 0.55228 | 0.0055497
2010/2011 | 2010-08-18 | 0.39468 | 0.0012242 | 0.39468 | 0.0012242
2010/2011 | 2010-08-19 | 0.42589 | 0.0012242 | 0.42589 | 0.0012242
2010/2011 | 2010-08-20 | 0.37893 | 0.001469 | 0.37893 | 0.001469
2010/2011 | 2010-08-22 | 7.6009 | 0.040357 | 7.6009 | 0.040357
2010/2011 | 2010-08-23 | 0.36873 | 0.001265 | 0.36873 | 0.001265
2010/2011 | 2010-08-24 | 0.69909 | 0.0032237 | 0.69909 | 0.0032237
2010/2011 | 2010-08-25 | 0.23378 | 0.088631 | 0.23378 | 0.088631
2010/2011 | 2010-08-27 | 0.24868 | 0.00089774 | 0.24868 | 0.00089774
2010/2011 | 2010-08-30 | 0.00767 | 4.0806e-05 | 0.00767 | 4.0806e-05
2010/2011 | 2010-08-31 | 0.04852 | 0.00061209 | 0.04852 | 0.00061209
2010/2011 | 2010-09-01 | 0.02677 | 0.00016323 | 0.02677 | 0.00016323
2010/2011 | 2010-09-03 | 0.65682 | 0.015874 | 0.65682 | 0.015874
2010/2011 | 2010-09-04 | 0.0235 | 0.00016323 | 0.0235 | 0.00016323
2010/2011 | 2010-09-06 | 0.09578 | 0.0040806 | 0.09578 | 0.0040806
2010/2011 | 2010-09-07 | 0.0553 | 0.00044887 | 0.0553 | 0.00044887
2010/2011 | 2010-09-08 | 0.23431 | 0.00073451 | 0.23431 | 0.00073451
2010/2011 | 2010-09-09 | 0.96561 | 0.011834 | 0.96561 | 0.011834
2010/2011 | 2010-09-10 | 0.00167 | 4.0806e-05 | 0.00167 | 4.0806e-05
2010/2011 | 2010-09-11 | 0.42912 | 0.02126 | 0.42912 | 0.02126
2010/2011 | 2010-09-12 | 0.02187 | 0.00016323 | 0.02187 | 0.00016323
2010/2011 | 2010-09-13 | 0.54199 | 0.002326 | 0.54199 | 0.002326
2010/2011 | 2010-09-15 | 0.07366 | 0.00020403 | 0.07366 | 0.00020403
2010/2011 | 2010-09-16 | 0.04383 | 0.00012242 | 0.04383 | 0.00012242
2010/2011 | 2010-09-17 | 7.1079 | 0.035257 | 7.1079 | 0.035257
2010/2011 | 2010-09-18 | 5.3998 | 0.031135 | 5.3998 | 0.031135
2010/2011 | 2010-09-19 | 5.1689 | 0.037542 | 5.1689 | 0.037542
2010/2011 | 2010-09-20 | 0.08798 | 0.00069371 | 0.08798 | 0.00069371
2010/2011 | 2010-09-21 | 1.0865 | 0.0066106 | 1.0865 | 0.0066106
2010/2011 | 2010-09-22 | 5.9216 | 0.076675 | 5.9216 | 0.076675
2010/2011 | 2010-09-23 | 8.3068 | 0.085979 | 8.3068 | 0.085979
2010/2011 | 2010-09-24 | 3.4772 | 0.057088 | 3.4772 | 0.057088
2010/2011 | 2010-09-25 | 0.08912 | 0.0017139 | 0.08912 | 0.0017139
2010/2011 | 2010-09-27 | 0.07264 | 0.0010202 | 0.07264 | 0.0010202
2010/2011 | 2010-09-28 | 1.2942 | 0.015955 | 1.2942 | 0.015955
2010/2011 | 2010-09-29 | 0.41953 | 0.0013466 | 0.41953 | 0.0013466
2010/2011 | 2010-09-30 | 0.44912 | 0.0037542 | 0.44912 | 0.0037542
2010/2011 | 2010-10-01 | 0.43103 | 0.0020405 | 0.43103 | 0.0020405
2010/2011 | 2010-10-02 | 0.04938 | 0.00032648 | 0.04938 | 0.00032648
2010/2011 | 2010-10-03 | 0.93675 | 0.026404 | 0.93675 | 0.026404
2010/2011 | 2010-10-04 | 1.4331 | 0.0082844 | 1.4331 | 0.0082844
2010/2011 | 2010-10-05 | 0.48624 | 0.0044483 | 0.48624 | 0.0044483
2010/2011 | 2010-10-06 | 0.83084 | 0.014406 | 0.83084 | 0.014406
2010/2011 | 2010-10-07 | 0.47205 | 0.0016324 | 0.47205 | 0.0016324
2010/2011 | 2010-10-08 | 1.2825 | 0.086108 | 1.2825 | 0.086108
2010/2011 | 2010-10-09 | 3.8648 | 0.015344 | 3.8648 | 0.015344
2010/2011 | 2010-10-10 | 0.51604 | 0.0027751 | 0.51604 | 0.0027751
2010/2011 | 2010-10-11 | 11.0026 | 0.07056 | 11.0026 | 0.07056
2010/2011 | 2010-10-12 | 0.48629 | 0.0073457 | 0.48629 | 0.0073457
2010/2011 | 2010-10-13 | 0.14108 | 0.0023262 | 0.14108 | 0.0023262
2010/2011 | 2010-10-14 | 0.37835 | 0.0055093 | 0.37835 | 0.0055093
2010/2011 | 2010-10-15 | 0.84456 | 0.0084068 | 0.84456 | 0.0084068
2010/2011 | 2010-10-17 | 0.28893 | 0.010202 | 0.28893 | 0.010202
2010/2011 | 2010-10-18 | 0.17099 | 0.0026118 | 0.17099 | 0.0026118
2010/2011 | 2010-10-19 | 0.01077 | 8.1619e-05 | 0.01077 | 8.1619e-05
2010/2011 | 2010-10-20 | 0.16577 | 0.0011427 | 0.16577 | 0.0011427
2010/2011 | 2010-10-21 | 0.37945 | 0.022609 | 0.37945 | 0.022609
2010/2011 | 2010-10-22 | 0.38912 | 0.0014283 | 0.38912 | 0.0014283
2010/2011 | 2010-10-23 | 0.01261 | 0.00012243 | 0.01261 | 0.00012243
2010/2011 | 2010-10-25 | 0.71168 | 0.0031423 | 0.71168 | 0.0031423
2010/2011 | 2010-10-26 | 1.2562 | 0.045544 | 1.2562 | 0.045544
2010/2011 | 2010-10-27 | 0.05322 | 0.00044891 | 0.05322 | 0.00044891
2010/2011 | 2010-10-28 | 1.0817 | 0.0074682 | 1.0817 | 0.0074682
2010/2011 | 2010-10-29 | 0.7549 | 0.0039177 | 0.7549 | 0.0039177
2010/2011 | 2010-10-30 | 0.00286 | 4.081e-05 | 0.00286 | 4.081e-05
2010/2011 | 2010-10-31 | 0.01204 | 0.00020405 | 0.01204 | 0.00020405
2010/2011 | 2010-11-01 | 0.09201 | 0.00089844 | 0.09201 | 0.00089844
2010/2011 | 2010-11-03 | 0.00641 | 8.1676e-05 | 0.00641 | 8.1676e-05
2010/2011 | 2010-11-04 | 0.06951 | 0.00061257 | 0.06951 | 0.00061257
2010/2011 | 2010-11-05 | 0.35831 | 0.0016335 | 0.35831 | 0.0016335
2010/2011 | 2010-11-06 | 0.9037 | 0.0019194 | 0.9037 | 0.0019194
2010/2011 | 2010-11-07 | 0.03773 | 0.00028587 | 0.03773 | 0.00028587
2010/2011 | 2010-11-08 | 0.21395 | 0.00069425 | 0.21395 | 0.00069425
2010/2011 | 2010-11-09 | 0.30657 | 0.0019194 | 0.30657 | 0.0019194
2010/2011 | 2010-11-11 | 0.41565 | 0.0023278 | 0.41565 | 0.0023278
2010/2011 | 2010-11-12 | 0.29939 | 0.0024094 | 0.29939 | 0.0024094
2010/2011 | 2010-11-14 | 0.01045 | 0.00016335 | 0.01045 | 0.00016335
2010/2011 | 2010-11-16 | 0.16193 | 0.0013885 | 0.16193 | 0.0013885
2010/2011 | 2010-11-17 | 0.25646 | 0.053784 | 0.25646 | 0.053784
2010/2011 | 2010-11-19 | 0.2536 | 0.017969 | 0.2536 | 0.017969
2010/2011 | 2010-11-20 | 0.2387 | 0.0018377 | 0.2387 | 0.0018377
2010/2011 | 2010-11-21 | 0.00368 | 0.00020419 | 0.00368 | 0.00020419
2010/2011 | 2010-11-22 | 0.38417 | 0.0094744 | 0.38417 | 0.0094744
2010/2011 | 2010-11-23 | 0.03312 | 0.0014293 | 0.03312 | 0.0014293
2010/2011 | 2010-11-24 | 0.58443 | 0.0034712 | 0.58443 | 0.0034712
2010/2011 | 2010-11-25 | 0.04982 | 0.00016335 | 0.04982 | 0.00016335
2010/2011 | 2010-11-26 | 0.21419 | 0.0022053 | 0.21419 | 0.0022053
2010/2011 | 2010-11-27 | 0.0343 | 0.00028587 | 0.0343 | 0.00028587
2010/2011 | 2010-11-28 | 0.47519 | 0.0011026 | 0.47519 | 0.0011026
2010/2011 | 2010-11-29 | 0.36608 | 0.0037979 | 0.36608 | 0.0037979
2010/2011 | 2010-11-30 | 0.00474 | 4.0838e-05 | 0.00474 | 4.0838e-05
2010/2011 | 2010-12-01 | 2.5054 | 0.019806 | 2.5054 | 0.019806
2010/2011 | 2010-12-02 | 0.24732 | 0.0010618 | 0.24732 | 0.0010618
2010/2011 | 2010-12-03 | 0.0312 | 0.00016335 | 0.0312 | 0.00016335
2010/2011 | 2010-12-04 | 0.0158 | 0.00036754 | 0.0158 | 0.00036754
2010/2011 | 2010-12-05 | 0.01176 | 0.00024503 | 0.01176 | 0.00024503
2010/2011 | 2010-12-06 | 0.71952 | 0.0057582 | 0.71952 | 0.0057582
2010/2011 | 2010-12-07 | 2.4477 | 0.0067383 | 2.4477 | 0.0067383
2010/2011 | 2010-12-08 | 0.20505 | 0.00065341 | 0.20505 | 0.00065341
2010/2011 | 2010-12-09 | 0.34079 | 0.0024911 | 0.34079 | 0.0024911
2010/2011 | 2010-12-10 | 0.35924 | 0.0026953 | 0.35924 | 0.0026953
2010/2011 | 2010-12-11 | 0.69371 | 0.0074325 | 0.69371 | 0.0074325
2010/2011 | 2010-12-12 | 0.05513 | 0.00061257 | 0.05513 | 0.00061257
2010/2011 | 2010-12-13 | 0.03773 | 0.00016335 | 0.03773 | 0.00016335
2010/2011 | 2010-12-14 | 0.11026 | 0.00053089 | 0.11026 | 0.00053089
2010/2011 | 2010-12-15 | 0.24482 | 0.0016335 | 0.24482 | 0.0016335
2010/2011 | 2010-12-17 | 0.02001 | 0.00020419 | 0.02001 | 0.00020419
2010/2011 | 2010-12-18 | 0.44881 | 0.0021236 | 0.44881 | 0.0021236
2010/2011 | 2010-12-19 | 3.1928 | 0.11761 | 3.1928 | 0.11761
2010/2011 | 2010-12-20 | 4.0328 | 0.20051 | 4.0328 | 0.20051
2010/2011 | 2010-12-21 | 1.3191 | 0.0077184 | 1.3191 | 0.0077184
2010/2011 | 2010-12-22 | 0.39314 | 0.0034304 | 0.39314 | 0.0034304
2010/2011 | 2010-12-23 | 1.1518 | 0.004288 | 1.1518 | 0.004288
2010/2011 | 2010-12-24 | 0.09793 | 0.0044105 | 0.09793 | 0.0044105
2010/2011 | 2010-12-26 | 0.00225 | 4.0838e-05 | 0.00225 | 4.0838e-05
2010/2011 | 2010-12-27 | 1.5784 | 0.0011843 | 1.5784 | 0.0011843
2010/2011 | 2010-12-28 | 6.0638 | 0.062891 | 6.0638 | 0.062891
2010/2011 | 2010-12-29 | 0.01519 | 0.00012251 | 0.01519 | 0.00012251
2010/2011 | 2010-12-30 | 0.00082 | 4.0838e-05 | 0.00082 | 4.0838e-05
2010/2011 | 2010-12-31 | 0.01936 | 0.00024503 | 0.01936 | 0.00024503
2010/2011 | 2011-01-02 | 0.039 | 0.00073508 | 0.039 | 0.00073508
2010/2011 | 2011-01-03 | 0.0145 | 0.00020419 | 0.0145 | 0.00020419
2010/2011 | 2011-01-05 | 0.51677 | 0.042635 | 0.51677 | 0.042635
2010/2011 | 2011-01-06 | 0.01625 | 4.0838e-05 | 0.01625 | 4.0838e-05
2010/2011 | 2011-01-07 | 0.7493 | 0.0024094 | 0.7493 | 0.0024094
2010/2011 | 2011-01-08 | 0.00314 | 4.0838e-05 | 0.00314 | 4.0838e-05
2010/2011 | 2011-01-10 | 0.08539 | 0.00020419 | 0.08539 | 0.00020419
2010/2011 | 2011-01-11 | 0.17401 | 0.00089844 | 0.17401 | 0.00089844
2010/2011 | 2011-01-12 | 0.17813 | 0.00077592 | 0.17813 | 0.00077592
2010/2011 | 2011-01-13 | 0.8117 | 0.0021236 | 0.8117 | 0.0021236
2010/2011 | 2011-01-14 | 1.6741 | 0.0062891 | 1.6741 | 0.0062891
2010/2011 | 2011-01-15 | 0.01621 | 0.00016335 | 0.01621 | 0.00016335
2010/2011 | 2011-01-17 | 1.333 | 0.0089844 | 1.333 | 0.0089844
2010/2011 | 2011-01-18 | 2.2818 | 0.053824 | 2.2818 | 0.053824
2010/2011 | 2011-01-19 | 0.4692 | 0.018908 | 0.4692 | 0.018908
2010/2011 | 2011-01-20 | 0.27582 | 0.0029812 | 0.27582 | 0.0029812
2010/2011 | 2011-01-21 | 0.0555 | 0.00081676 | 0.0555 | 0.00081676
2010/2011 | 2011-01-23 | 1.5418 | 0.0041246 | 1.5418 | 0.0041246
2010/2011 | 2011-01-24 | 5.8033 | 0.072079 | 5.8033 | 0.072079
2010/2011 | 2011-01-25 | 0.1524 | 0.0011026 | 0.1524 | 0.0011026
2010/2011 | 2011-01-26 | 0.21996 | 0.0048189 | 0.21996 | 0.0048189
2010/2011 | 2011-01-27 | 3.2322 | 0.036427 | 3.2322 | 0.036427
2010/2011 | 2011-01-28 | 0.12737 | 0.00036754 | 0.12737 | 0.00036754
2010/2011 | 2011-01-29 | 0.55147 | 0.045085 | 0.55147 | 0.045085
2010/2011 | 2011-01-30 | 1.3279 | 0.0069833 | 1.3279 | 0.0069833
2010/2011 | 2011-01-31 | 0.18303 | 0.0067791 | 0.18303 | 0.0067791
2010/2011 | 2011-02-01 | 0.14311 | 0.001552 | 0.14311 | 0.001552
2010/2011 | 2011-02-02 | 0.11546 | 0.00069433 | 0.11546 | 0.00069433
2010/2011 | 2011-02-03 | 0.00413 | 4.0843e-05 | 0.00413 | 4.0843e-05
2010/2011 | 2011-02-04 | 0.08254 | 0.0054321 | 0.08254 | 0.0054321
2010/2011 | 2011-02-05 | 0.04815 | 0.013478 | 0.04815 | 0.013478
2010/2011 | 2011-02-06 | 0.00466 | 8.1686e-05 | 0.00466 | 8.1686e-05
2010/2011 | 2011-02-07 | 0.45116 | 0.003635 | 0.45116 | 0.003635
2010/2011 | 2011-02-08 | 1.9012 | 0.020544 | 1.9012 | 0.020544
2010/2011 | 2011-02-09 | 0.49894 | 0.004942 | 0.49894 | 0.004942
2010/2011 | 2011-02-10 | 3.5492 | 0.037331 | 3.5492 | 0.037331
2010/2011 | 2011-02-11 | 1.2902 | 0.0069842 | 1.2902 | 0.0069842
2010/2011 | 2011-02-14 | 0.18077 | 0.0013887 | 0.18077 | 0.0013887
2010/2011 | 2011-02-15 | 0.18105 | 0.0022872 | 0.18105 | 0.0022872
2010/2011 | 2011-02-16 | 0.05473 | 0.0015929 | 0.05473 | 0.0015929
2010/2011 | 2011-02-17 | 0.6641 | 0.13911 | 0.6641 | 0.13911
2010/2011 | 2011-02-18 | 0.61396 | 0.0031858 | 0.61396 | 0.0031858
2010/2011 | 2011-02-21 | 0.10117 | 0.00081686 | 0.10117 | 0.00081686
2010/2011 | 2011-02-22 | 0.49531 | 0.0076785 | 0.49531 | 0.0076785
2010/2011 | 2011-02-23 | 0.52532 | 0.0020013 | 0.52532 | 0.0020013
2010/2011 | 2011-02-24 | 0.752 | 0.0025323 | 0.752 | 0.0025323
2010/2011 | 2011-02-25 | 0.10611 | 0.001552 | 0.10611 | 0.001552
2010/2011 | 2011-02-26 | 0.08941 | 0.0008577 | 0.08941 | 0.0008577
2010/2011 | 2011-02-27 | 0.06282 | 0.0012253 | 0.06282 | 0.0012253
2010/2011 | 2011-02-28 | 0.73391 | 0.028794 | 0.73391 | 0.028794
2010/2011 | 2011-03-01 | 0.51586 | 0.0024516 | 0.51586 | 0.0024516
2010/2011 | 2011-03-02 | 0.14987 | 0.0027785 | 0.14987 | 0.0027785
2010/2011 | 2011-03-03 | 1.9116 | 0.010297 | 1.9116 | 0.010297
2010/2011 | 2011-03-04 | 0.09435 | 0.025292 | 0.09435 | 0.025292
2010/2011 | 2011-03-05 | 0.12793 | 0.0017978 | 0.12793 | 0.0017978
2010/2011 | 2011-03-07 | 0.5819 | 0.0039634 | 0.5819 | 0.0039634
2010/2011 | 2011-03-08 | 0.1913 | 0.0006129 | 0.1913 | 0.0006129
2010/2011 | 2011-03-09 | 6.5887 | 0.25059 | 6.5887 | 0.25059
2010/2011 | 2011-03-10 | 2.5217 | 0.0152 | 2.5217 | 0.0152
2010/2011 | 2011-03-11 | 0.05761 | 0.00053118 | 0.05761 | 0.00053118
2010/2011 | 2011-03-12 | 0.01569 | 0.00024516 | 0.01569 | 0.00024516
2010/2011 | 2011-03-13 | 0.06546 | 0.00069461 | 0.06546 | 0.00069461
2010/2011 | 2011-03-14 | 0.35225 | 0.0018387 | 0.35225 | 0.0018387
2010/2011 | 2011-03-15 | 3.7555 | 0.02758 | 3.7555 | 0.02758
2010/2011 | 2011-03-16 | 1.658 | 0.078287 | 1.658 | 0.078287
2010/2011 | 2011-03-17 | 0.25027 | 0.0024924 | 0.25027 | 0.0024924
2010/2011 | 2011-03-19 | 0.16369 | 0.0025333 | 0.16369 | 0.0025333
2010/2011 | 2011-03-20 | 0.26101 | 0.035834 | 0.26101 | 0.035834
2010/2011 | 2011-03-21 | 0.51155 | 0.0047397 | 0.51155 | 0.0047397
2010/2011 | 2011-03-22 | 0.00911 | 8.1719e-05 | 0.00911 | 8.1719e-05
2010/2011 | 2011-03-23 | 4.4772 | 0.028929 | 4.4772 | 0.028929
2010/2011 | 2011-03-24 | 0.01087 | 0.0002043 | 0.01087 | 0.0002043
2010/2011 | 2011-03-25 | 0.76731 | 0.002615 | 0.76731 | 0.002615
2010/2011 | 2011-03-27 | 1.3309 | 0.007559 | 1.3309 | 0.007559
2010/2011 | 2011-03-28 | 0.01308 | 0.0002043 | 0.01308 | 0.0002043
2010/2011 | 2011-03-29 | 0.2005 | 0.0031462 | 0.2005 | 0.0031462
2010/2011 | 2011-03-30 | 1.0262 | 0.053404 | 1.0262 | 0.053404
2010/2011 | 2011-03-31 | 0.25807 | 0.0021656 | 0.25807 | 0.0021656
2011/2012 | 2011-04-01 | 0.2204 | 0.0011012 | 0.2204 | 0.0011012
2011/2012 | 2011-04-02 | 0.00392 | 0.00016314 | 0.00392 | 0.00016314
2011/2012 | 2011-04-04 | 0.00208 | 4.0785e-05 | 0.00208 | 4.0785e-05
2011/2012 | 2011-04-05 | 0.07267 | 0.0029365 | 0.07267 | 0.0029365
2011/2012 | 2011-04-06 | 0.408 | 0.064154 | 0.408 | 0.064154
2011/2012 | 2011-04-07 | 0.19757 | 0.0031404 | 0.19757 | 0.0031404
2011/2012 | 2011-04-08 | 0.29194 | 0.0036706 | 0.29194 | 0.0036706
2011/2012 | 2011-04-09 | 0.02268 | 0.00020392 | 0.02268 | 0.00020392
2011/2012 | 2011-04-11 | 0.00954 | 0.00085648 | 0.00954 | 0.00085648
2011/2012 | 2011-04-12 | 0.45169 | 0.0025694 | 0.45169 | 0.0025694
2011/2012 | 2011-04-13 | 0.85783 | 0.0022839 | 0.85783 | 0.0022839
2011/2012 | 2011-04-14 | 0.3156 | 0.03173 | 0.3156 | 0.03173
2011/2012 | 2011-04-15 | 0.00653 | 8.1569e-05 | 0.00653 | 8.1569e-05
2011/2012 | 2011-04-16 | 0.20213 | 0.0038745 | 0.20213 | 0.0038745
2011/2012 | 2011-04-17 | 0.00661 | 8.1569e-05 | 0.00661 | 8.1569e-05
2011/2012 | 2011-04-18 | 2.6643 | 0.01713 | 2.6643 | 0.01713
2011/2012 | 2011-04-19 | 0.07056 | 0.00028549 | 0.07056 | 0.00028549
2011/2012 | 2011-04-20 | 1.3315 | 0.0044455 | 1.3315 | 0.0044455
2011/2012 | 2011-04-21 | 1.9814 | 0.011297 | 1.9814 | 0.011297
2011/2012 | 2011-04-22 | 0.18704 | 0.0021208 | 0.18704 | 0.0021208
2011/2012 | 2011-04-23 | 0.16347 | 0.0026918 | 0.16347 | 0.0026918
2011/2012 | 2011-04-24 | 0.08402 | 0.00069334 | 0.08402 | 0.00069334
2011/2012 | 2011-04-25 | 2.0728 | 0.011624 | 2.0728 | 0.011624
2011/2012 | 2011-04-26 | 28.9743 | 0.23109 | 21.6659 | 0.23109
2011/2012 | 2011-04-27 | 1.0579 | 0.012113 | 1.0579 | 0.012113
2011/2012 | 2011-04-28 | 0.93101 | 0.01713 | 0.93101 | 0.01713
2011/2012 | 2011-04-29 | 0.36347 | 0.0028141 | 0.36347 | 0.0028141
2011/2012 | 2011-05-01 | 0.50647 | 0.0066754 | 0.50647 | 0.0066754
2011/2012 | 2011-05-02 | 1.1989 | 0.054222 | 1.1989 | 0.054222
2011/2012 | 2011-05-03 | 0.49402 | 0.0013515 | 0.49402 | 0.0013515
2011/2012 | 2011-05-04 | 0.55598 | 0.0014334 | 0.55598 | 0.0014334
2011/2012 | 2011-05-05 | 0.10807 | 0.00028667 | 0.10807 | 0.00028667
2011/2012 | 2011-05-06 | 0.06196 | 0.00045049 | 0.06196 | 0.00045049
2011/2012 | 2011-05-07 | 0.03895 | 0.0031944 | 0.03895 | 0.0031944
2011/2012 | 2011-05-09 | 0.21382 | 0.0042592 | 0.21382 | 0.0042592
2011/2012 | 2011-05-10 | 0.10571 | 0.00094193 | 0.10571 | 0.00094193
2011/2012 | 2011-05-11 | 0.21005 | 0.002662 | 0.21005 | 0.002662
2011/2012 | 2011-05-12 | 2.1858 | 0.023221 | 2.1858 | 0.023221
2011/2012 | 2011-05-13 | 0.31346 | 0.0031534 | 0.31346 | 0.0031534
2011/2012 | 2011-05-15 | 0.01892 | 0.00032763 | 0.01892 | 0.00032763
2011/2012 | 2011-05-16 | 0.12232 | 0.0058563 | 0.12232 | 0.0058563
2011/2012 | 2011-05-17 | 1.37 | 0.15796 | 1.37 | 0.15796
2011/2012 | 2011-05-18 | 1.1987 | 0.0036449 | 1.1987 | 0.0036449
2011/2012 | 2011-05-19 | 0.20906 | 0.0028667 | 0.20906 | 0.0028667
2011/2012 | 2011-05-20 | 0.03502 | 0.00012286 | 0.03502 | 0.00012286
2011/2012 | 2011-05-22 | 0.44757 | 0.025842 | 0.44757 | 0.025842
2011/2012 | 2011-05-23 | 0.00639 | 8.1907e-05 | 0.00639 | 8.1907e-05
2011/2012 | 2011-05-24 | 1.2889 | 0.013351 | 1.2889 | 0.013351
2011/2012 | 2011-05-25 | 2.9682 | 0.027725 | 2.9682 | 0.027725
2011/2012 | 2011-05-26 | 1.2931 | 0.065157 | 1.2931 | 0.065157
2011/2012 | 2011-05-27 | 0.48301 | 0.0014743 | 0.48301 | 0.0014743
2011/2012 | 2011-05-30 | 0.0068 | 8.1907e-05 | 0.0068 | 8.1907e-05
2011/2012 | 2011-05-31 | 0.01622 | 8.1907e-05 | 0.01622 | 8.1907e-05
2011/2012 | 2011-06-01 | 0.15965 | 0.0014334 | 0.15965 | 0.0014334
2011/2012 | 2011-06-02 | 0.11435 | 0.0018839 | 0.11435 | 0.0018839
2011/2012 | 2011-06-03 | 0.415 | 0.0042593 | 0.415 | 0.0042593
2011/2012 | 2011-06-04 | 0.1734 | 0.002703 | 0.1734 | 0.002703
2011/2012 | 2011-06-05 | 0.43408 | 0.0013515 | 0.43408 | 0.0013515
2011/2012 | 2011-06-07 | 1.3325 | 0.0068395 | 1.3325 | 0.0068395
2011/2012 | 2011-06-09 | 0.30229 | 0.0013106 | 0.30229 | 0.0013106
2011/2012 | 2011-06-10 | 0.01225 | 0.00016382 | 0.01225 | 0.00016382
2011/2012 | 2011-06-11 | 0.01458 | 0.00016382 | 0.01458 | 0.00016382
2011/2012 | 2011-06-12 | 1.1312 | 0.0020068 | 1.1312 | 0.0020068
2011/2012 | 2011-06-13 | 0.42634 | 0.053242 | 0.42634 | 0.053242
2011/2012 | 2011-06-14 | 0.09403 | 0.00032764 | 0.09403 | 0.00032764
2011/2012 | 2011-06-15 | 0.00406 | 0.00061433 | 0.00406 | 0.00061433
2011/2012 | 2011-06-16 | 0.23422 | 0.0029078 | 0.23422 | 0.0029078
2011/2012 | 2011-06-17 | 0.5271 | 0.0065119 | 0.5271 | 0.0065119
2011/2012 | 2011-06-18 | 0.43912 | 0.0017201 | 0.43912 | 0.0017201
2011/2012 | 2011-06-19 | 1.3201 | 0.014334 | 1.3201 | 0.014334
2011/2012 | 2011-06-20 | 0.0215 | 0.00028669 | 0.0215 | 0.00028669
2011/2012 | 2011-06-21 | 0.01122 | 0.00016382 | 0.01122 | 0.00016382
2011/2012 | 2011-06-22 | 0.41828 | 0.001843 | 0.41828 | 0.001843
2011/2012 | 2011-06-23 | 0.17259 | 0.00090101 | 0.17259 | 0.00090101
2011/2012 | 2011-06-24 | 3.1629 | 0.018962 | 3.1629 | 0.018962
2011/2012 | 2011-06-28 | 0.0483 | 0.0062661 | 0.0483 | 0.0062661
2011/2012 | 2011-06-29 | 1.3573 | 0.0047098 | 1.3573 | 0.0047098
2011/2012 | 2011-06-30 | 0.86927 | 0.0020887 | 0.86927 | 0.0020887
2011/2012 | 2011-07-01 | 0.62557 | 0.0057751 | 0.62557 | 0.0057751
2011/2012 | 2011-07-04 | 0.48347 | 0.0025394 | 0.48347 | 0.0025394
2011/2012 | 2011-07-05 | 0.06877 | 0.00036863 | 0.06877 | 0.00036863
2011/2012 | 2011-07-06 | 4.2835 | 0.24456 | 4.2835 | 0.24456
2011/2012 | 2011-07-07 | 0.10448 | 0.00077821 | 0.10448 | 0.00077821
2011/2012 | 2011-07-08 | 0.8838 | 0.0066762 | 0.8838 | 0.0066762
2011/2012 | 2011-07-09 | 1.1348 | 0.01368 | 1.1348 | 0.01368
2011/2012 | 2011-07-10 | 1.8819 | 0.0089699 | 1.8819 | 0.0089699
2011/2012 | 2011-07-11 | 8.1333 | 0.086013 | 8.1333 | 0.086013
2011/2012 | 2011-07-12 | 5.6387 | 0.18947 | 5.6387 | 0.18947
2011/2012 | 2011-07-13 | 0.40135 | 0.0051198 | 0.40135 | 0.0051198
2011/2012 | 2011-07-14 | 2.9798 | 0.013967 | 2.9798 | 0.013967
2011/2012 | 2011-07-15 | 0.88745 | 0.00053246 | 0.88745 | 0.00053246
2011/2012 | 2011-07-16 | 0.18297 | 0.0004915 | 0.18297 | 0.0004915
2011/2012 | 2011-07-18 | 0.42596 | 0.002908 | 0.42596 | 0.002908
2011/2012 | 2011-07-19 | 0.52664 | 0.001966 | 0.52664 | 0.001966
2011/2012 | 2011-07-20 | 0.64839 | 0.0062666 | 0.64839 | 0.0062666
2011/2012 | 2011-07-21 | 0.45602 | 0.0030309 | 0.45602 | 0.0030309
2011/2012 | 2011-07-22 | 1.116 | 0.015237 | 1.116 | 0.015237
2011/2012 | 2011-07-24 | 0.229 | 0.0024575 | 0.229 | 0.0024575
2011/2012 | 2011-07-25 | 0.9382 | 0.0087651 | 0.9382 | 0.0087651
2011/2012 | 2011-07-26 | 0.29641 | 0.0013516 | 0.29641 | 0.0013516
2011/2012 | 2011-07-27 | 0.23788 | 0.00073725 | 0.23788 | 0.00073725
2011/2012 | 2011-07-28 | 0.78353 | 0.0045054 | 0.78353 | 0.0045054
2011/2012 | 2011-07-30 | 0.02596 | 0.00028671 | 0.02596 | 0.00028671
2011/2012 | 2011-08-01 | 0.029 | 8.1917e-05 | 0.029 | 8.1917e-05
2011/2012 | 2011-08-02 | 0.13399 | 0.0016383 | 0.13399 | 0.0016383
2011/2012 | 2011-08-03 | 0.15102 | 0.00094204 | 0.15102 | 0.00094204
2011/2012 | 2011-08-04 | 1.01 | 0.0063486 | 1.01 | 0.0063486
2011/2012 | 2011-08-05 | 1.8053 | 0.0065943 | 1.8053 | 0.0065943
2011/2012 | 2011-08-06 | 0.02117 | 0.00020479 | 0.02117 | 0.00020479
2011/2012 | 2011-08-07 | 17.3787 | 0.2403 | 17.3787 | 0.2403
2011/2012 | 2011-08-08 | 0.44009 | 0.0031538 | 0.44009 | 0.0031538
2011/2012 | 2011-08-09 | 0.75212 | 0.0020479 | 0.75212 | 0.0020479
2011/2012 | 2011-08-10 | 1.1305 | 0.0065124 | 1.1305 | 0.0065124
2011/2012 | 2011-08-11 | 0.12751 | 0.0015974 | 0.12751 | 0.0015974
2011/2012 | 2011-08-12 | 1.2952 | 0.0075773 | 1.2952 | 0.0075773
2011/2012 | 2011-08-14 | 0.08732 | 0.015318 | 0.08732 | 0.015318
2011/2012 | 2011-08-15 | 0.34401 | 0.015032 | 0.34401 | 0.015032
2011/2012 | 2011-08-16 | 0.49285 | 0.0016793 | 0.49285 | 0.0016793
2011/2012 | 2011-08-17 | 0.39775 | 0.0038091 | 0.39775 | 0.0038091
2011/2012 | 2011-08-18 | 0.53381 | 0.0035224 | 0.53381 | 0.0035224
2011/2012 | 2011-08-19 | 1.0212 | 0.0093795 | 1.0212 | 0.0093795
2011/2012 | 2011-08-20 | 0 | 0 | 0 | 0
2011/2012 | 2011-08-22 | 0.28257 | 0.0027442 | 0.28257 | 0.0027442
2011/2012 | 2011-08-23 | 3.9027 | 0.013148 | 3.9027 | 0.013148
2011/2012 | 2011-08-24 | 0.69307 | 0.0028671 | 0.69307 | 0.0028671
2011/2012 | 2011-08-25 | 0.41863 | 0.0013107 | 0.41863 | 0.0013107
2011/2012 | 2011-08-26 | 0.0557 | 0.00036863 | 0.0557 | 0.00036863
2011/2012 | 2011-08-28 | 0.16109 | 0.0025394 | 0.16109 | 0.0025394
2011/2012 | 2011-08-29 | 0.09908 | 0.00065533 | 0.09908 | 0.00065533
2011/2012 | 2011-08-30 | 1.2203 | 0.043866 | 1.2203 | 0.043866
2011/2012 | 2011-08-31 | 2.2473 | 0.0095843 | 2.2473 | 0.0095843
2011/2012 | 2011-09-01 | 0.66046 | 0.020021 | 0.66046 | 0.020021
2011/2012 | 2011-09-02 | 7.5918 | 0.045079 | 7.5918 | 0.045079
2011/2012 | 2011-09-05 | 0 | 0 | 0 | 0
2011/2012 | 2011-09-06 | 0.00201 | 4.0943e-05 | 0.00201 | 4.0943e-05
2011/2012 | 2011-09-07 | 0.03988 | 0.0002866 | 0.03988 | 0.0002866
2011/2012 | 2011-09-08 | 0.1989 | 0.00081887 | 0.1989 | 0.00081887
2011/2012 | 2011-09-10 | 0.47138 | 0.053636 | 0.47138 | 0.053636
2011/2012 | 2011-09-11 | 1.2542 | 0.012856 | 1.2542 | 0.012856
2011/2012 | 2011-09-12 | 4.0997 | 0.022273 | 4.0997 | 0.022273
2011/2012 | 2011-09-13 | 5.105 | 0.037995 | 5.105 | 0.037995
2011/2012 | 2011-09-14 | 3.5059 | 0.02301 | 3.5059 | 0.02301
2011/2012 | 2011-09-15 | 0.29586 | 0.020676 | 0.29586 | 0.020676
2011/2012 | 2011-09-16 | 1.2548 | 0.031772 | 1.2548 | 0.031772
2011/2012 | 2011-09-17 | 0.00553 | 0.00012283 | 0.00553 | 0.00012283
2011/2012 | 2011-09-18 | 0.10408 | 0.0011055 | 0.10408 | 0.0011055
2011/2012 | 2011-09-19 | 1.8478 | 0.02039 | 1.8478 | 0.02039
2011/2012 | 2011-09-20 | 0.22748 | 0.00098264 | 0.22748 | 0.00098264
2011/2012 | 2011-09-21 | 0.56285 | 0.0055274 | 0.56285 | 0.0055274
2011/2012 | 2011-09-22 | 0.43891 | 0.0079021 | 0.43891 | 0.0079021
2011/2012 | 2011-09-23 | 0.03983 | 0.00045038 | 0.03983 | 0.00045038
2011/2012 | 2011-09-24 | 0 | 0 | 0 | 0
2011/2012 | 2011-09-27 | 3.4956 | 0.081191 | 3.4956 | 0.081191
2011/2012 | 2011-09-28 | 0.07005 | 0.030462 | 0.07005 | 0.030462
2011/2012 | 2011-10-02 | 0.03585 | 0.00024526 | 0.03585 | 0.00024526
2011/2012 | 2011-10-03 | 2.9797 | 0.02751 | 2.9797 | 0.02751
2011/2012 | 2011-10-04 | 0.64362 | 0.0051504 | 0.64362 | 0.0051504
2011/2012 | 2011-10-05 | 0.06045 | 0.0008584 | 0.06045 | 0.0008584
2011/2012 | 2011-10-06 | 0.34148 | 0.0012263 | 0.34148 | 0.0012263
2011/2012 | 2011-10-07 | 0.17049 | 0.00077665 | 0.17049 | 0.00077665
2011/2012 | 2011-10-10 | 0.47188 | 0.0040468 | 0.47188 | 0.0040468
2011/2012 | 2011-10-11 | 0.13968 | 0.0006949 | 0.13968 | 0.0006949
2011/2012 | 2011-10-12 | 0.61502 | 0.0061723 | 0.61502 | 0.0061723
2011/2012 | 2011-10-13 | 0.20307 | 0.0058862 | 0.20307 | 0.0058862
2011/2012 | 2011-10-14 | 0.00123 | 4.0876e-05 | 0.00123 | 4.0876e-05
2011/2012 | 2011-10-15 | 0.01582 | 0.00032701 | 0.01582 | 0.00032701
2011/2012 | 2011-10-18 | 0.81741 | 0.011445 | 0.81741 | 0.011445
2011/2012 | 2011-10-19 | 0.34847 | 0.0047825 | 0.34847 | 0.0047825
2011/2012 | 2011-10-20 | 0.12013 | 0.00077665 | 0.12013 | 0.00077665
2011/2012 | 2011-10-21 | 0.31303 | 0.0019621 | 0.31303 | 0.0019621
2011/2012 | 2011-10-22 | 0.23087 | 0.0019212 | 0.23087 | 0.0019212
2011/2012 | 2011-10-24 | 0.01177 | 8.1753e-05 | 0.01177 | 8.1753e-05
2011/2012 | 2011-10-25 | 0.46722 | 0.0077256 | 0.46722 | 0.0077256
2011/2012 | 2011-10-26 | 0.50781 | 0.0015124 | 0.50781 | 0.0015124
2011/2012 | 2011-10-27 | 0.10947 | 0.0022073 | 0.10947 | 0.0022073
2011/2012 | 2011-10-28 | 0.11976 | 0.0024526 | 0.11976 | 0.0024526
2011/2012 | 2011-10-29 | 0.77617 | 0.086045 | 0.77617 | 0.086045
2011/2012 | 2011-10-30 | 0.41305 | 0.0020847 | 0.41305 | 0.0020847
2011/2012 | 2011-10-31 | 0.40328 | 0.0020847 | 0.40328 | 0.0020847
2011/2012 | 2011-11-01 | 0.472 | 0.008706 | 0.472 | 0.008706
2011/2012 | 2011-11-02 | 1.3894 | 0.016063 | 1.3894 | 0.016063
2011/2012 | 2011-11-03 | 0.55415 | 0.0088695 | 0.55415 | 0.0088695
2011/2012 | 2011-11-04 | 0.60148 | 0.0095234 | 0.60148 | 0.0095234
2011/2012 | 2011-11-05 | 0.0067 | 0.00016349 | 0.0067 | 0.00016349
2011/2012 | 2011-11-06 | 0.00699 | 0.00012262 | 0.00699 | 0.00012262
2011/2012 | 2011-11-07 | 0.44604 | 0.005477 | 0.44604 | 0.005477
2011/2012 | 2011-11-08 | 0.59598 | 0.013039 | 0.59598 | 0.013039
2011/2012 | 2011-11-09 | 0.12797 | 0.0089103 | 0.12797 | 0.0089103
2011/2012 | 2011-11-10 | 0.00352 | 4.0873e-05 | 0.00352 | 4.0873e-05
2011/2012 | 2011-11-11 | 0.0484 | 0.00036786 | 0.0484 | 0.00036786
2011/2012 | 2011-11-12 | 0.00225 | 4.0873e-05 | 0.00225 | 4.0873e-05
2011/2012 | 2011-11-14 | 0.95883 | 0.0046187 | 0.95883 | 0.0046187
2011/2012 | 2011-11-15 | 0.56597 | 0.0024115 | 0.56597 | 0.0024115
2011/2012 | 2011-11-16 | 0.73273 | 0.0024115 | 0.73273 | 0.0024115
2011/2012 | 2011-11-17 | 0.48365 | 0.0044143 | 0.48365 | 0.0044143
2011/2012 | 2011-11-18 | 1.2808 | 0.028897 | 1.2808 | 0.028897
2011/2012 | 2011-11-19 | 2.2614 | 0.015573 | 2.2614 | 0.015573
2011/2012 | 2011-11-20 | 0.26036 | 0.0060901 | 0.26036 | 0.0060901
2011/2012 | 2011-11-21 | 0.03936 | 0.00049048 | 0.03936 | 0.00049048
2011/2012 | 2011-11-22 | 1.5615 | 0.02763 | 1.5615 | 0.02763
2011/2012 | 2011-11-23 | 0.34759 | 0.0017575 | 0.34759 | 0.0017575
2011/2012 | 2011-11-24 | 2.4895 | 0.014837 | 2.4895 | 0.014837
2011/2012 | 2011-11-25 | 0.34093 | 0.0041691 | 0.34093 | 0.0041691
2011/2012 | 2011-11-26 | 1.6612 | 0.049293 | 1.6612 | 0.049293
2011/2012 | 2011-11-27 | 0.05755 | 0.00085833 | 0.05755 | 0.00085833
2011/2012 | 2011-11-28 | 0.19697 | 0.00081746 | 0.19697 | 0.00081746
2011/2012 | 2011-11-29 | 0.76808 | 0.013039 | 0.76808 | 0.013039
2011/2012 | 2011-11-30 | 0.01733 | 0.00012262 | 0.01733 | 0.00012262
2011/2012 | 2011-12-01 | 0.43657 | 0.0033925 | 0.43657 | 0.0033925
2011/2012 | 2011-12-02 | 0.20961 | 0.00085833 | 0.20961 | 0.00085833
2011/2012 | 2011-12-03 | 0.28525 | 0.0033107 | 0.28525 | 0.0033107
2011/2012 | 2011-12-04 | 1.0142 | 0.0017984 | 1.0142 | 0.0017984
2011/2012 | 2011-12-05 | 0.00233 | 4.0873e-05 | 0.00233 | 4.0873e-05
2011/2012 | 2011-12-06 | 0.76767 | 0.0049865 | 0.76767 | 0.0049865
2011/2012 | 2011-12-07 | 0.4787 | 0.003556 | 0.4787 | 0.003556
2011/2012 | 2011-12-08 | 0.97221 | 0.055587 | 0.97221 | 0.055587
2011/2012 | 2011-12-09 | 0.48378 | 0.001921 | 0.48378 | 0.001921
2011/2012 | 2011-12-11 | 0.0871 | 0.0016758 | 0.0871 | 0.0016758
2011/2012 | 2011-12-12 | 0.288 | 0.0013897 | 0.288 | 0.0013897
2011/2012 | 2011-12-13 | 3.3739 | 0.053544 | 3.3739 | 0.053544
2011/2012 | 2011-12-14 | 0.1547 | 0.0013488 | 0.1547 | 0.0013488
2011/2012 | 2011-12-15 | 0.20155 | 0.0017984 | 0.20155 | 0.0017984
2011/2012 | 2011-12-16 | 0.00396 | 4.0873e-05 | 0.00396 | 4.0873e-05
2011/2012 | 2011-12-17 | 0.03155 | 0.00012262 | 0.03155 | 0.00012262
2011/2012 | 2011-12-18 | 0.05869 | 0.00077659 | 0.05869 | 0.00077659
2011/2012 | 2011-12-19 | 0.35768 | 0.0023706 | 0.35768 | 0.0023706
2011/2012 | 2011-12-20 | 0.89623 | 0.011363 | 0.89623 | 0.011363
2011/2012 | 2011-12-21 | 4.8016 | 0.01733 | 4.8016 | 0.01733
2011/2012 | 2011-12-22 | 0.57827 | 0.0050274 | 0.57827 | 0.0050274
2011/2012 | 2011-12-24 | 0.01361 | 0.00012262 | 0.01361 | 0.00012262
2011/2012 | 2011-12-25 | 0.09965 | 0.0011036 | 0.09965 | 0.0011036
2011/2012 | 2011-12-26 | 0.00687 | 0.00016349 | 0.00687 | 0.00016349
2011/2012 | 2011-12-27 | 0.00102 | 4.0873e-05 | 0.00102 | 4.0873e-05
2011/2012 | 2011-12-28 | 0.04431 | 0.00032698 | 0.04431 | 0.00032698
2011/2012 | 2011-12-29 | 0.05501 | 0.00057222 | 0.05501 | 0.00057222
2011/2012 | 2011-12-31 | 0.30254 | 0.0026976 | 0.30254 | 0.0026976
2011/2012 | 2012-01-01 | 0.99698 | 0.064852 | 0.99698 | 0.064852
2011/2012 | 2012-01-02 | 0.71182 | 0.012954 | 0.71182 | 0.012954
2011/2012 | 2012-01-04 | 0.12287 | 0.0018389 | 0.12287 | 0.0018389
2011/2012 | 2012-01-05 | 1.5604 | 0.01087 | 1.5604 | 0.01087
2011/2012 | 2012-01-06 | 0.95382 | 0.012178 | 0.95382 | 0.012178
2011/2012 | 2012-01-07 | 0.53378 | 0.0059254 | 0.53378 | 0.0059254
2011/2012 | 2012-01-08 | 0.62474 | 0.0123 | 0.62474 | 0.0123
2011/2012 | 2012-01-09 | 0.15059 | 0.00098075 | 0.15059 | 0.00098075
2011/2012 | 2012-01-10 | 0.02305 | 0.019656 | 0.02305 | 0.019656
2011/2012 | 2012-01-11 | 0.12255 | 0.00093989 | 0.12255 | 0.00093989
2011/2012 | 2012-01-12 | 0.02771 | 0.0011033 | 0.02771 | 0.0011033
2011/2012 | 2012-01-13 | 2.307 | 0.10858 | 2.307 | 0.10858
2011/2012 | 2012-01-14 | 0.00609 | 4.0865e-05 | 0.00609 | 4.0865e-05
2011/2012 | 2012-01-16 | 0.68363 | 0.0079686 | 0.68363 | 0.0079686
2011/2012 | 2012-01-17 | 0.30457 | 0.0017572 | 0.30457 | 0.0017572
2011/2012 | 2012-01-18 | 0.88705 | 0.0068653 | 0.88705 | 0.0068653
2011/2012 | 2012-01-19 | 0.56761 | 0.0025745 | 0.56761 | 0.0025745
2011/2012 | 2012-01-20 | 0.31245 | 0.0011033 | 0.31245 | 0.0011033
2011/2012 | 2012-01-21 | 0.05575 | 0.00065384 | 0.05575 | 0.00065384
2011/2012 | 2012-01-23 | 0.32266 | 0.0013894 | 0.32266 | 0.0013894
2011/2012 | 2012-01-24 | 0.15426 | 0.00044951 | 0.15426 | 0.00044951
2011/2012 | 2012-01-25 | 0.87826 | 0.010175 | 0.87826 | 0.010175
2011/2012 | 2012-01-26 | 3.5634 | 0.011156 | 3.5634 | 0.011156
2011/2012 | 2012-01-27 | 0.46892 | 0.021413 | 0.46892 | 0.021413
2011/2012 | 2012-01-28 | 0.02006 | 0.00077643 | 0.02006 | 0.00077643
2011/2012 | 2012-01-29 | 0.48192 | 0.003637 | 0.48192 | 0.003637
2011/2012 | 2012-01-30 | 0.02256 | 0.00012259 | 0.02256 | 0.00012259
2011/2012 | 2012-01-31 | 0.30697 | 0.0051898 | 0.30697 | 0.0051898
2011/2012 | 2012-02-01 | 0.72404 | 0.0081863 | 0.72404 | 0.0081863
2011/2012 | 2012-02-02 | 0.34964 | 0.0050346 | 0.34964 | 0.0050346
2011/2012 | 2012-02-03 | 0.32319 | 0.0058942 | 0.32319 | 0.0058942
2011/2012 | 2012-02-04 | 0.48152 | 0.0040522 | 0.48152 | 0.0040522
2011/2012 | 2012-02-06 | 0.06426 | 0.001187 | 0.06426 | 0.001187
2011/2012 | 2012-02-07 | 0.01658 | 0.00028652 | 0.01658 | 0.00028652
2011/2012 | 2012-02-08 | 0.0779 | 0.00036838 | 0.0779 | 0.00036838
2011/2012 | 2012-02-09 | 0.42172 | 0.0033564 | 0.42172 | 0.0033564
2011/2012 | 2012-02-10 | 0.31497 | 0.0030699 | 0.31497 | 0.0030699
2011/2012 | 2012-02-11 | 0 | 0 | 0 | 0
2011/2012 | 2012-02-13 | 0.60105 | 0.0045843 | 0.60105 | 0.0045843
2011/2012 | 2012-02-14 | 0.07363 | 0.0020056 | 0.07363 | 0.0020056
2011/2012 | 2012-02-15 | 1.332 | 0.0065081 | 1.332 | 0.0065081
2011/2012 | 2012-02-16 | 0.25828 | 0.0055667 | 0.25828 | 0.0055667
2011/2012 | 2012-02-17 | 1.2842 | 0.0080226 | 1.2842 | 0.0080226
2011/2012 | 2012-02-18 | 0.05145 | 0.00053211 | 0.05145 | 0.00053211
2011/2012 | 2012-02-19 | 0.00524 | 4.0932e-05 | 0.00524 | 4.0932e-05
2011/2012 | 2012-02-20 | 0.31505 | 0.020793 | 0.31505 | 0.020793
2011/2012 | 2012-02-21 | 1.0523 | 0.0085547 | 1.0523 | 0.0085547
2011/2012 | 2012-02-22 | 0.96493 | 0.027465 | 0.96493 | 0.027465
2011/2012 | 2012-02-23 | 1.4028 | 0.0062625 | 1.4028 | 0.0062625
2011/2012 | 2012-02-24 | 0.38738 | 0.0031517 | 0.38738 | 0.0031517
2011/2012 | 2012-02-25 | 0 | 0 | 0 | 0
2011/2012 | 2012-02-26 | 0.04719 | 0.00085956 | 0.04719 | 0.00085956
2011/2012 | 2012-02-27 | 0.70386 | 0.0020466 | 0.70386 | 0.0020466
2011/2012 | 2012-02-28 | 1.2327 | 0.011543 | 1.2327 | 0.011543
2011/2012 | 2012-02-29 | 0.07826 | 0.0035201 | 0.07826 | 0.0035201
2011/2012 | 2012-03-01 | 0.41476 | 0.0052876 | 0.41476 | 0.0052876
2011/2012 | 2012-03-02 | 2.0122 | 0.035061 | 2.0122 | 0.035061
2011/2012 | 2012-03-03 | 22.7722 | 0.15444 | 21.6659 | 0.15444
2011/2012 | 2012-03-04 | 0.04762 | 0.00089482 | 0.04762 | 0.00089482
2011/2012 | 2012-03-05 | 0.13845 | 0.0010982 | 0.13845 | 0.0010982
2011/2012 | 2012-03-06 | 0.12479 | 0.00069145 | 0.12479 | 0.00069145
2011/2012 | 2012-03-07 | 0.4958 | 0.0028471 | 0.4958 | 0.0028471
2011/2012 | 2012-03-08 | 0.43026 | 0.00423 | 0.43026 | 0.00423
2011/2012 | 2012-03-09 | 0.77438 | 0.0036199 | 0.77438 | 0.0036199
2011/2012 | 2012-03-11 | 0.20869 | 0.00081347 | 0.20869 | 0.00081347
2011/2012 | 2012-03-12 | 2.9924 | 0.048117 | 2.9924 | 0.048117
2011/2012 | 2012-03-13 | 0.33869 | 0.0010982 | 0.33869 | 0.0010982
2011/2012 | 2012-03-14 | 2.4488 | 0.0072399 | 2.4488 | 0.0072399
2011/2012 | 2012-03-15 | 0.09253 | 0.0029692 | 0.09253 | 0.0029692
2011/2012 | 2012-03-16 | 0.57159 | 0.012853 | 0.57159 | 0.012853
2011/2012 | 2012-03-17 | 0.00793 | 0.00012202 | 0.00793 | 0.00012202
2011/2012 | 2012-03-19 | 8.9671 | 0.030953 | 8.9671 | 0.030953
2011/2012 | 2012-03-20 | 25.893 | 0.12605 | 21.6659 | 0.12605
2011/2012 | 2012-03-21 | 5.3315 | 0.054055 | 5.3315 | 0.054055
2011/2012 | 2012-03-22 | 0.71312 | 0.0046775 | 0.71312 | 0.0046775
2011/2012 | 2012-03-23 | 0.14061 | 0.0019117 | 0.14061 | 0.0019117
2011/2012 | 2012-03-24 | 0.00207 | 4.0674e-05 | 0.00207 | 4.0674e-05
2011/2012 | 2012-03-25 | 0.30961 | 0.0073212 | 0.30961 | 0.0073212
2011/2012 | 2012-03-26 | 0.31144 | 0.005735 | 0.31144 | 0.005735
2011/2012 | 2012-03-27 | 0.48332 | 0.0013829 | 0.48332 | 0.0013829
2011/2012 | 2012-03-28 | 0.50984 | 0.0024404 | 0.50984 | 0.0024404
2011/2012 | 2012-03-29 | 1.0906 | 0.003864 | 1.0906 | 0.003864
2011/2012 | 2012-03-30 | 0.08192 | 0.00024404 | 0.08192 | 0.00024404
2012/2013 | 2012-04-02 | 0.01257 | 0.00016267 | 0.01257 | 0.00016267
2012/2013 | 2012-04-03 | 0.31626 | 0.0013013 | 0.31626 | 0.0013013
2012/2013 | 2012-04-04 | 0.38491 | 0.0047987 | 0.38491 | 0.0047987
2012/2013 | 2012-04-05 | 0.6362 | 0.002928 | 0.6362 | 0.002928
2012/2013 | 2012-04-06 | 0.00569 | 4.0667e-05 | 0.00569 | 4.0667e-05
2012/2013 | 2012-04-07 | 0.02558 | 0.00016267 | 0.02558 | 0.00016267
2012/2013 | 2012-04-08 | 0.01301 | 0.00020333 | 0.01301 | 0.00020333
2012/2013 | 2012-04-09 | 0.02086 | 0.00020333 | 0.02086 | 0.00020333
2012/2013 | 2012-04-10 | 0.01143 | 0.000122 | 0.01143 | 0.000122
2012/2013 | 2012-04-11 | 0.06714 | 0.000244 | 0.06714 | 0.000244
2012/2013 | 2012-04-12 | 0.83181 | 0.0049614 | 0.83181 | 0.0049614
2012/2013 | 2012-04-13 | 1.4847 | 0.00549 | 1.4847 | 0.00549
2012/2013 | 2012-04-14 | 0.05734 | 0.00065067 | 0.05734 | 0.00065067
2012/2013 | 2012-04-16 | 0.68523 | 0.0028467 | 0.68523 | 0.0028467
2012/2013 | 2012-04-17 | 0.67227 | 0.0037007 | 0.67227 | 0.0037007
2012/2013 | 2012-04-18 | 6.5433 | 0.075641 | 6.5433 | 0.075641
2012/2013 | 2012-04-19 | 0.24754 | 0.000732 | 0.24754 | 0.000732
2012/2013 | 2012-04-20 | 0.67507 | 0.0099227 | 0.67507 | 0.0099227
2012/2013 | 2012-04-22 | 0.00289 | 4.0667e-05 | 0.00289 | 4.0667e-05
2012/2013 | 2012-04-23 | 0.14087 | 0.002318 | 0.14087 | 0.002318
2012/2013 | 2012-04-24 | 0.09593 | 0.00065067 | 0.09593 | 0.00065067
2012/2013 | 2012-04-25 | 0.02778 | 0.000488 | 0.02778 | 0.000488
2012/2013 | 2012-04-26 | 0.24811 | 0.00097601 | 0.24811 | 0.00097601
2012/2013 | 2012-04-27 | 0.05014 | 0.000366 | 0.05014 | 0.000366
2012/2013 | 2012-04-28 | 0.04835 | 0.000488 | 0.04835 | 0.000488
2012/2013 | 2012-04-29 | 0.02192 | 0.00032534 | 0.02192 | 0.00032534
2012/2013 | 2012-04-30 | 0.07295 | 0.00044734 | 0.07295 | 0.00044734
2012/2013 | 2012-05-01 | 1.0986 | 0.0068265 | 1.0986 | 0.0068265
2012/2013 | 2012-05-02 | 0.10642 | 0.015563 | 0.10642 | 0.015563
2012/2013 | 2012-05-03 | 0.10967 | 0.025396 | 0.10967 | 0.025396
2012/2013 | 2012-05-04 | 0.88968 | 0.0070297 | 0.88968 | 0.0070297
2012/2013 | 2012-05-05 | 0.13612 | 0.00073141 | 0.13612 | 0.00073141
2012/2013 | 2012-05-06 | 0.02308 | 0.0003657 | 0.02308 | 0.0003657
2012/2013 | 2012-05-07 | 0.01967 | 8.1268e-05 | 0.01967 | 8.1268e-05
2012/2013 | 2012-05-08 | 0.47542 | 0.0055262 | 0.47542 | 0.0055262
2012/2013 | 2012-05-09 | 1.2794 | 0.0061357 | 1.2794 | 0.0061357
2012/2013 | 2012-05-10 | 1.6864 | 0.12345 | 1.6864 | 0.12345
2012/2013 | 2012-05-11 | 0.47082 | 0.0032507 | 0.47082 | 0.0032507
2012/2013 | 2012-05-12 | 0.00731 | 4.0634e-05 | 0.00731 | 4.0634e-05
2012/2013 | 2012-05-13 | 3.9544 | 0.055709 | 3.9544 | 0.055709
2012/2013 | 2012-05-14 | 3.7881 | 0.027225 | 3.7881 | 0.027225
2012/2013 | 2012-05-15 | 0.57955 | 0.004998 | 0.57955 | 0.004998
2012/2013 | 2012-05-16 | 0.638 | 0.0035351 | 0.638 | 0.0035351
2012/2013 | 2012-05-17 | 3.2058 | 0.010037 | 3.2058 | 0.010037
2012/2013 | 2012-05-18 | 0.67412 | 0.012231 | 0.67412 | 0.012231
2012/2013 | 2012-05-19 | 0.05067 | 0.00093458 | 0.05067 | 0.00093458
2012/2013 | 2012-05-20 | 0.81873 | 0.023974 | 0.81873 | 0.023974
2012/2013 | 2012-05-21 | 0.15015 | 0.0019911 | 0.15015 | 0.0019911
2012/2013 | 2012-05-22 | 0.00252 | 8.1268e-05 | 0.00252 | 8.1268e-05
2012/2013 | 2012-05-23 | 2.1976 | 0.016375 | 2.1976 | 0.016375
2012/2013 | 2012-05-24 | 0.04547 | 0.00028444 | 0.04547 | 0.00028444
2012/2013 | 2012-05-25 | 0.11584 | 0.00056887 | 0.11584 | 0.00056887
2012/2013 | 2012-05-27 | 0.1106 | 0.0013003 | 0.1106 | 0.0013003
2012/2013 | 2012-05-28 | 0.03312 | 0.00020317 | 0.03312 | 0.00020317
2012/2013 | 2012-05-29 | 0.25535 | 0.0043885 | 0.25535 | 0.0043885
2012/2013 | 2012-05-30 | 0.40496 | 0.0060544 | 0.40496 | 0.0060544
2012/2013 | 2012-05-31 | 0.03962 | 0.00020317 | 0.03962 | 0.00020317
2012/2013 | 2012-06-01 | 1.2338 | 0.020807 | 1.2338 | 0.020807
2012/2013 | 2012-06-02 | 0.60409 | 0.026223 | 0.60409 | 0.026223
2012/2013 | 2012-06-03 | 0.01906 | 0.00020359 | 0.01906 | 0.00020359
2012/2013 | 2012-06-05 | 1.6251 | 0.0036646 | 1.6251 | 0.0036646
2012/2013 | 2012-06-06 | 1.0125 | 0.0030539 | 1.0125 | 0.0030539
2012/2013 | 2012-06-07 | 0.1292 | 0.00048862 | 0.1292 | 0.00048862
2012/2013 | 2012-06-08 | 0.2382 | 0.05782 | 0.2382 | 0.05782
2012/2013 | 2012-06-11 | 0.07358 | 0.00048862 | 0.07358 | 0.00048862
2012/2013 | 2012-06-12 | 0.23661 | 0.00081437 | 0.23661 | 0.00081437
2012/2013 | 2012-06-13 | 0.16141 | 0.00048862 | 0.16141 | 0.00048862
2012/2013 | 2012-06-14 | 0.12191 | 0.00040718 | 0.12191 | 0.00040718
2012/2013 | 2012-06-15 | 0.5872 | 0.0022395 | 0.5872 | 0.0022395
2012/2013 | 2012-06-18 | 0.66908 | 0.020726 | 0.66908 | 0.020726
2012/2013 | 2012-06-19 | 0.62982 | 0.0036239 | 0.62982 | 0.0036239
2012/2013 | 2012-06-20 | 0.42372 | 0.0014251 | 0.42372 | 0.0014251
2012/2013 | 2012-06-21 | 0.08518 | 0.00020359 | 0.08518 | 0.00020359
2012/2013 | 2012-06-22 | 0.26495 | 0.001303 | 0.26495 | 0.001303
2012/2013 | 2012-06-24 | 0.08835 | 0.001303 | 0.08835 | 0.001303
2012/2013 | 2012-06-25 | 0.02427 | 0.00024431 | 0.02427 | 0.00024431
2012/2013 | 2012-06-26 | 0.66566 | 0.001873 | 0.66566 | 0.001873
2012/2013 | 2012-06-27 | 0.94792 | 0.0022395 | 0.94792 | 0.0022395
2012/2013 | 2012-06-28 | 2.5957 | 0.012826 | 2.5957 | 0.012826
2012/2013 | 2012-06-29 | 0.07448 | 0.00057006 | 0.07448 | 0.00057006
2012/2013 | 2012-07-02 | 0.37282 | 0.0051195 | 0.37282 | 0.0051195
2012/2013 | 2012-07-03 | 0.09999 | 0.001097 | 0.09999 | 0.001097
2012/2013 | 2012-07-04 | 1.5137 | 0.018731 | 1.5137 | 0.018731
2012/2013 | 2012-07-05 | 0.07122 | 0.0047944 | 0.07122 | 0.0047944
2012/2013 | 2012-07-06 | 0.35345 | 0.0030473 | 0.35345 | 0.0030473
2012/2013 | 2012-07-08 | 0.01243 | 8.1261e-05 | 0.01243 | 8.1261e-05
2012/2013 | 2012-07-09 | 1.0563 | 0.018771 | 1.0563 | 0.018771
2012/2013 | 2012-07-10 | 0.36888 | 0.0023566 | 0.36888 | 0.0023566
2012/2013 | 2012-07-11 | 0.17081 | 0.0031286 | 0.17081 | 0.0031286
2012/2013 | 2012-07-12 | 0.2144 | 0.0009345 | 0.2144 | 0.0009345
2012/2013 | 2012-07-13 | 0.01751 | 0.00040631 | 0.01751 | 0.00040631
2012/2013 | 2012-07-15 | 0.40045 | 0.00065009 | 0.40045 | 0.00065009
2012/2013 | 2012-07-16 | 0.13051 | 0.00069072 | 0.13051 | 0.00069072
2012/2013 | 2012-07-17 | 1.2787 | 0.0047131 | 1.2787 | 0.0047131
2012/2013 | 2012-07-18 | 0.55883 | 0.014099 | 0.55883 | 0.014099
2012/2013 | 2012-07-19 | 1.2232 | 0.012555 | 1.2232 | 0.012555
2012/2013 | 2012-07-20 | 0.36441 | 0.0023972 | 0.36441 | 0.0023972
2012/2013 | 2012-07-21 | 0.02003 | 0.00020315 | 0.02003 | 0.00020315
2012/2013 | 2012-07-22 | 0.18877 | 0.0015846 | 0.18877 | 0.0015846
2012/2013 | 2012-07-23 | 3.0912 | 0.011661 | 3.0912 | 0.011661
2012/2013 | 2012-07-24 | 0.02316 | 8.1261e-05 | 0.02316 | 8.1261e-05
2012/2013 | 2012-07-25 | 0.59776 | 0.0039005 | 0.59776 | 0.0039005
2012/2013 | 2012-07-26 | 0.01121 | 0.00016252 | 0.01121 | 0.00016252
2012/2013 | 2012-07-27 | 0.00028 | 4.0631e-05 | 0.00028 | 4.0631e-05
2012/2013 | 2012-07-28 | 0.05148 | 0.00077198 | 0.05148 | 0.00077198
2012/2013 | 2012-07-29 | 1.7094 | 0.0056477 | 1.7094 | 0.0056477
2012/2013 | 2012-07-30 | 0.09114 | 0.0028441 | 0.09114 | 0.0028441
2012/2013 | 2012-07-31 | 0.37688 | 0.0030879 | 0.37688 | 0.0030879
2012/2013 | 2012-08-01 | 0.00692 | 8.1453e-05 | 0.00692 | 8.1453e-05
2012/2013 | 2012-08-02 | 0.03421 | 0.00016291 | 0.03421 | 0.00016291
2012/2013 | 2012-08-03 | 0.71333 | 0.0023214 | 0.71333 | 0.0023214
2012/2013 | 2012-08-04 | 0.18824 | 0.00044799 | 0.18824 | 0.00044799
2012/2013 | 2012-08-06 | 0.0079 | 4.0727e-05 | 0.0079 | 4.0727e-05
2012/2013 | 2012-08-07 | 0.23397 | 0.0035025 | 0.23397 | 0.0035025
2012/2013 | 2012-08-09 | 0.02277 | 0.00012218 | 0.02277 | 0.00012218
2012/2013 | 2012-08-12 | 0.16291 | 0.0021178 | 0.16291 | 0.0021178
2012/2013 | 2012-08-13 | 0.22835 | 0.0016291 | 0.22835 | 0.0016291
2012/2013 | 2012-08-14 | 0.03262 | 0.00012218 | 0.03262 | 0.00012218
2012/2013 | 2012-08-15 | 2.1131 | 0.0082268 | 2.1131 | 0.0082268
2012/2013 | 2012-08-16 | 0.04512 | 0.00057017 | 0.04512 | 0.00057017
2012/2013 | 2012-08-17 | 0.46624 | 0.0023621 | 0.46624 | 0.0023621
2012/2013 | 2012-08-19 | 0.19976 | 0.0011811 | 0.19976 | 0.0011811
2012/2013 | 2012-08-20 | 0.03771 | 0.017553 | 0.03771 | 0.017553
2012/2013 | 2012-08-21 | 0.04333 | 0.00073308 | 0.04333 | 0.00073308
2012/2013 | 2012-08-22 | 0.03731 | 0.0006109 | 0.03731 | 0.0006109
2012/2013 | 2012-08-23 | 0.88095 | 0.0029323 | 0.88095 | 0.0029323
2012/2013 | 2012-08-24 | 0.19193 | 0.0017105 | 0.19193 | 0.0017105
2012/2013 | 2012-08-25 | 0.01087 | 0.00012218 | 0.01087 | 0.00012218
2012/2013 | 2012-08-27 | 0.10499 | 0.00052945 | 0.10499 | 0.00052945
2012/2013 | 2012-08-29 | 0.28887 | 0.00089598 | 0.28887 | 0.00089598
2012/2013 | 2012-08-30 | 0.58879 | 0.0023214 | 0.58879 | 0.0023214
2012/2013 | 2012-08-31 | 0.02179 | 0.00020363 | 0.02179 | 0.00020363
2012/2013 | 2012-09-03 | 0.05943 | 0.001384 | 0.05943 | 0.001384
2012/2013 | 2012-09-04 | 0.71242 | 0.0052917 | 0.71242 | 0.0052917
2012/2013 | 2012-09-05 | 0.70741 | 0.004274 | 0.70741 | 0.004274
2012/2013 | 2012-09-06 | 0.39838 | 0.0013433 | 0.39838 | 0.0013433
2012/2013 | 2012-09-07 | 7.0543 | 0.016078 | 7.0543 | 0.016078
2012/2013 | 2012-09-08 | 0.19192 | 0.0030122 | 0.19192 | 0.0030122
2012/2013 | 2012-09-09 | 0.05792 | 0.00020353 | 0.05792 | 0.00020353
2012/2013 | 2012-09-10 | 1.0235 | 0.14161 | 1.0235 | 0.14161
2012/2013 | 2012-09-11 | 1.1204 | 0.0070827 | 1.1204 | 0.0070827
2012/2013 | 2012-09-12 | 0.85692 | 0.0022795 | 0.85692 | 0.0022795
2012/2013 | 2012-09-13 | 0.01926 | 0.00020353 | 0.01926 | 0.00020353
2012/2013 | 2012-09-14 | 0.00749 | 4.0705e-05 | 0.00749 | 4.0705e-05
2012/2013 | 2012-09-15 | 0.00281 | 4.0705e-05 | 0.00281 | 4.0705e-05
2012/2013 | 2012-09-16 | 0.0022 | 4.0705e-05 | 0.0022 | 4.0705e-05
2012/2013 | 2012-09-17 | 0.07107 | 0.013473 | 0.07107 | 0.013473
2012/2013 | 2012-09-18 | 0.48248 | 0.0061872 | 0.48248 | 0.0061872
2012/2013 | 2012-09-19 | 0.38478 | 0.0010583 | 0.38478 | 0.0010583
2012/2013 | 2012-09-20 | 0.72556 | 0.0060243 | 0.72556 | 0.0060243
2012/2013 | 2012-09-21 | 0.29584 | 0.0018317 | 0.29584 | 0.0018317
2012/2013 | 2012-09-22 | 0.02035 | 0.00016282 | 0.02035 | 0.00016282
2012/2013 | 2012-09-23 | 0.03212 | 0.00036635 | 0.03212 | 0.00036635
2012/2013 | 2012-09-24 | 0.3383 | 0.001384 | 0.3383 | 0.001384
2012/2013 | 2012-09-25 | 0.3705 | 0.0033378 | 0.3705 | 0.0033378
2012/2013 | 2012-09-26 | 0.8025 | 0.014043 | 0.8025 | 0.014043
2012/2013 | 2012-09-27 | 0.39407 | 0.0024016 | 0.39407 | 0.0024016
2012/2013 | 2012-09-28 | 0.17597 | 0.0010583 | 0.17597 | 0.0010583
2012/2013 | 2012-09-30 | 0.07176 | 0.0016689 | 0.07176 | 0.0016689
2012/2013 | 2012-10-01 | 0.00699 | 4.0657e-05 | 0.00699 | 4.0657e-05
2012/2013 | 2012-10-02 | 0.34827 | 0.0024801 | 0.34827 | 0.0024801
2012/2013 | 2012-10-03 | 0.10758 | 0.0028053 | 0.10758 | 0.0028053
2012/2013 | 2012-10-04 | 0.7117 | 0.0041877 | 0.7117 | 0.0041877
2012/2013 | 2012-10-05 | 0.34335 | 0.00093511 | 0.34335 | 0.00093511
2012/2013 | 2012-10-06 | 0.04691 | 0.00060986 | 0.04691 | 0.00060986
2012/2013 | 2012-10-08 | 0.17921 | 0.0055294 | 0.17921 | 0.0055294
2012/2013 | 2012-10-09 | 3.9386 | 0.054968 | 3.9386 | 0.054968
2012/2013 | 2012-10-11 | 0.26521 | 0.0010977 | 0.26521 | 0.0010977
2012/2013 | 2012-10-12 | 0.37571 | 0.001423 | 0.37571 | 0.001423
2012/2013 | 2012-10-13 | 17.5769 | 0.080582 | 17.5769 | 0.080582
2012/2013 | 2012-10-14 | 0.68413 | 0.0071963 | 0.68413 | 0.0071963
2012/2013 | 2012-10-15 | 0.1205 | 0.00052854 | 0.1205 | 0.00052854
2012/2013 | 2012-10-16 | 0.53797 | 0.0058953 | 0.53797 | 0.0058953
2012/2013 | 2012-10-17 | 0.38189 | 0.0033339 | 0.38189 | 0.0033339
2012/2013 | 2012-10-18 | 0.57733 | 0.0064238 | 0.57733 | 0.0064238
2012/2013 | 2012-10-19 | 0.12725 | 0.00097577 | 0.12725 | 0.00097577
2012/2013 | 2012-10-20 | 0.01594 | 0.00016263 | 0.01594 | 0.00016263
2012/2013 | 2012-10-21 | 0.62909 | 0.00081314 | 0.62909 | 0.00081314
2012/2013 | 2012-10-23 | 0.19759 | 0.0015856 | 0.19759 | 0.0015856
2012/2013 | 2012-10-24 | 0.07546 | 0.0017889 | 0.07546 | 0.0017889
2012/2013 | 2012-10-26 | 0.00525 | 0.00012197 | 0.00525 | 0.00012197
2012/2013 | 2012-10-27 | 0.24231 | 0.0045536 | 0.24231 | 0.0045536
2012/2013 | 2012-10-30 | 0.50451 | 0.0014637 | 0.50451 | 0.0014637
2012/2013 | 2012-10-31 | 0.76077 | 0.0034558 | 0.76077 | 0.0034558
2012/2013 | 2012-11-01 | 0.57078 | 0.0021957 | 0.57078 | 0.0021957
2012/2013 | 2012-11-02 | 0.1766 | 0.0011385 | 0.1766 | 0.0011385
2012/2013 | 2012-11-03 | 0.05676 | 0.018217 | 0.05676 | 0.018217
2012/2013 | 2012-11-04 | 0.18952 | 0.00024397 | 0.18952 | 0.00024397
2012/2013 | 2012-11-05 | 0.24213 | 0.0015452 | 0.24213 | 0.0015452
2012/2013 | 2012-11-06 | 0.25243 | 0.0021551 | 0.25243 | 0.0021551
2012/2013 | 2012-11-07 | 0.13195 | 0.00040662 | 0.13195 | 0.00040662
2012/2013 | 2012-11-08 | 1.1495 | 0.0074818 | 1.1495 | 0.0074818
2012/2013 | 2012-11-09 | 0.40747 | 0.0034563 | 0.40747 | 0.0034563
2012/2013 | 2012-11-10 | 0.00346 | 4.0662e-05 | 0.00346 | 4.0662e-05
2012/2013 | 2012-11-11 | 3.2565 | 0.019477 | 3.2565 | 0.019477
2012/2013 | 2012-11-12 | 0.33781 | 0.0012605 | 0.33781 | 0.0012605
2012/2013 | 2012-11-13 | 1.7363 | 0.0063026 | 1.7363 | 0.0063026
2012/2013 | 2012-11-14 | 0.45216 | 0.0043102 | 0.45216 | 0.0043102
2012/2013 | 2012-11-15 | 0.58387 | 0.0019111 | 0.58387 | 0.0019111
2012/2013 | 2012-11-16 | 1.5298 | 0.005652 | 1.5298 | 0.005652
2012/2013 | 2012-11-17 | 0.04944 | 0.00073192 | 0.04944 | 0.00073192
2012/2013 | 2012-11-18 | 0.00366 | 4.0662e-05 | 0.00366 | 4.0662e-05
2012/2013 | 2012-11-19 | 0.11422 | 0.0008539 | 0.11422 | 0.0008539
2012/2013 | 2012-11-20 | 0.6016 | 0.0019518 | 0.6016 | 0.0019518
2012/2013 | 2012-11-21 | 0.74847 | 0.0066279 | 0.74847 | 0.0066279
2012/2013 | 2012-11-22 | 0.32323 | 0.00089456 | 0.32323 | 0.00089456
2012/2013 | 2012-11-23 | 0.6536 | 0.0046355 | 0.6536 | 0.0046355
2012/2013 | 2012-11-24 | 0.04286 | 8.1324e-05 | 0.04286 | 8.1324e-05
2012/2013 | 2012-11-25 | 0.21282 | 0.079738 | 0.21282 | 0.079738
2012/2013 | 2012-11-26 | 1.4596 | 0.0037002 | 1.4596 | 0.0037002
2012/2013 | 2012-11-27 | 1.0337 | 0.0039035 | 1.0337 | 0.0039035
2012/2013 | 2012-11-28 | 0.18241 | 0.0036189 | 0.18241 | 0.0036189
2012/2013 | 2012-11-29 | 0.7111 | 0.020778 | 0.7111 | 0.020778
2012/2013 | 2012-11-30 | 0.36973 | 0.0010165 | 0.36973 | 0.0010165
2012/2013 | 2012-12-02 | 0.54953 | 0.014842 | 0.54953 | 0.014842
2012/2013 | 2012-12-03 | 0.3682 | 0.0070755 | 0.3682 | 0.0070755
2012/2013 | 2012-12-04 | 1.7351 | 0.004595 | 1.7351 | 0.004595
2012/2013 | 2012-12-05 | 0.58136 | 0.0065062 | 0.58136 | 0.0065062
2012/2013 | 2012-12-06 | 0.24617 | 0.009068 | 0.24617 | 0.009068
2012/2013 | 2012-12-07 | 2.9603 | 0.023341 | 2.9603 | 0.023341
2012/2013 | 2012-12-08 | 0.06258 | 0.00040664 | 0.06258 | 0.00040664
2012/2013 | 2012-12-10 | 0.34686 | 0.0037411 | 0.34686 | 0.0037411
2012/2013 | 2012-12-11 | 1.3679 | 0.0030091 | 1.3679 | 0.0030091
2012/2013 | 2012-12-12 | 0.99073 | 0.0057336 | 0.99073 | 0.0057336
2012/2013 | 2012-12-13 | 0.32818 | 0.080107 | 0.32818 | 0.080107
2012/2013 | 2012-12-14 | 0.42131 | 0.0067502 | 0.42131 | 0.0067502
2012/2013 | 2012-12-15 | 0.00724 | 8.1327e-05 | 0.00724 | 8.1327e-05
2012/2013 | 2012-12-17 | 0.02204 | 0.00032531 | 0.02204 | 0.00032531
2012/2013 | 2012-12-18 | 0.40688 | 0.0021552 | 0.40688 | 0.0021552
2012/2013 | 2012-12-19 | 0.33125 | 0.0034564 | 0.33125 | 0.0034564
2012/2013 | 2012-12-20 | 0.19413 | 0.0008946 | 0.19413 | 0.0008946
2012/2013 | 2012-12-21 | 0.00813 | 0.00020332 | 0.00813 | 0.00020332
2012/2013 | 2012-12-22 | 0.83361 | 0.0043917 | 0.83361 | 0.0043917
2012/2013 | 2012-12-24 | 0.00976 | 0.00016265 | 0.00976 | 0.00016265
2012/2013 | 2012-12-26 | 0.02338 | 0.00036597 | 0.02338 | 0.00036597
2012/2013 | 2012-12-27 | 0.00947 | 4.0664e-05 | 0.00947 | 4.0664e-05
2012/2013 | 2012-12-28 | 1.8114 | 0.015981 | 1.8114 | 0.015981
2012/2013 | 2012-12-29 | 0.56071 | 0.0055709 | 0.56071 | 0.0055709
2012/2013 | 2012-12-31 | 0.94994 | 0.086085 | 0.94994 | 0.086085
2012/2013 | 2013-01-01 | 0.41927 | 0.0073634 | 0.41927 | 0.0073634
2012/2013 | 2013-01-02 | 0.00757 | 0.00012205 | 0.00757 | 0.00012205
2012/2013 | 2013-01-03 | 0.08689 | 0.0036207 | 0.08689 | 0.0036207
2012/2013 | 2013-01-04 | 0.15036 | 0.0017086 | 0.15036 | 0.0017086
2012/2013 | 2013-01-06 | 0.07713 | 0.00024409 | 0.07713 | 0.00024409
2012/2013 | 2013-01-07 | 4.1292 | 0.057402 | 4.1292 | 0.057402
2012/2013 | 2013-01-08 | 2.6721 | 0.044628 | 2.6721 | 0.044628
2012/2013 | 2013-01-09 | 0.14931 | 0.0060616 | 0.14931 | 0.0060616
2012/2013 | 2013-01-10 | 0.02596 | 0.00024409 | 0.02596 | 0.00024409
2012/2013 | 2013-01-11 | 1.1774 | 0.035353 | 1.1774 | 0.035353
2012/2013 | 2013-01-13 | 0.49282 | 0.0019934 | 0.49282 | 0.0019934
2012/2013 | 2013-01-14 | 0.31138 | 0.00077295 | 0.31138 | 0.00077295
2012/2013 | 2013-01-15 | 0.16179 | 0.00040682 | 0.16179 | 0.00040682
2012/2013 | 2013-01-16 | 0.32477 | 0.0025223 | 0.32477 | 0.0025223
2012/2013 | 2013-01-17 | 1.1077 | 0.0056141 | 1.1077 | 0.0056141
2012/2013 | 2013-01-18 | 0.06704 | 0.00016273 | 0.06704 | 0.00016273
2012/2013 | 2013-01-19 | 0.00561 | 4.0682e-05 | 0.00561 | 4.0682e-05
2012/2013 | 2013-01-20 | 0.3569 | 0.004353 | 0.3569 | 0.004353
2012/2013 | 2013-01-21 | 0.02185 | 0.00012205 | 0.02185 | 0.00012205
2012/2013 | 2013-01-22 | 0.3063 | 0.0030918 | 0.3063 | 0.0030918
2012/2013 | 2013-01-23 | 0.08441 | 0.00032545 | 0.08441 | 0.00032545
2012/2013 | 2013-01-24 | 3.4655 | 0.0065498 | 3.4655 | 0.0065498
2012/2013 | 2013-01-26 | 0.82824 | 0.0041089 | 0.82824 | 0.0041089
2012/2013 | 2013-01-27 | 0.01892 | 0.00016273 | 0.01892 | 0.00016273
2012/2013 | 2013-01-29 | 0.01274 | 0.00016273 | 0.01274 | 0.00016273
2012/2013 | 2013-01-30 | 0.11456 | 0.00052886 | 0.11456 | 0.00052886
2012/2013 | 2013-01-31 | 3.1629 | 0.0060616 | 3.1629 | 0.0060616
2012/2013 | 2013-02-01 | 0.24736 | 0.0016273 | 0.24736 | 0.0016273
2012/2013 | 2013-02-02 | 0.15321 | 0.0014239 | 0.15321 | 0.0014239
2012/2013 | 2013-02-03 | 0.00297 | 4.0683e-05 | 0.00297 | 4.0683e-05
2012/2013 | 2013-02-04 | 0.51298 | 0.0059805 | 0.51298 | 0.0059805
2012/2013 | 2013-02-05 | 6.003 | 0.014402 | 6.003 | 0.014402
2012/2013 | 2013-02-06 | 0.06066 | 0.00085435 | 0.06066 | 0.00085435
2012/2013 | 2013-02-07 | 0.65658 | 0.0044752 | 0.65658 | 0.0044752
2012/2013 | 2013-02-08 | 1.0187 | 0.0045972 | 1.0187 | 0.0045972
2012/2013 | 2013-02-10 | 0.06583 | 0.00085435 | 0.06583 | 0.00085435
2012/2013 | 2013-02-11 | 0.04577 | 0.00061025 | 0.04577 | 0.00061025
2012/2013 | 2013-02-12 | 0.43731 | 0.0082994 | 0.43731 | 0.0082994
2012/2013 | 2013-02-13 | 0.03051 | 0.00061025 | 0.03051 | 0.00061025
2012/2013 | 2013-02-14 | 2.1236 | 0.049471 | 2.1236 | 0.049471
2012/2013 | 2013-02-15 | 0.02299 | 0.00020342 | 0.02299 | 0.00020342
2012/2013 | 2013-02-16 | 0.06758 | 0.00044752 | 0.06758 | 0.00044752
2012/2013 | 2013-02-17 | 0.04252 | 0.00016273 | 0.04252 | 0.00016273
2012/2013 | 2013-02-18 | 0.01627 | 0.00020342 | 0.01627 | 0.00020342
2012/2013 | 2013-02-19 | 0.21933 | 0.0019121 | 0.21933 | 0.0019121
2012/2013 | 2013-02-20 | 0.09358 | 0.00093572 | 0.09358 | 0.00093572
2012/2013 | 2013-02-21 | 0.22689 | 0.00052889 | 0.22689 | 0.00052889
2012/2013 | 2013-02-22 | 0.88096 | 0.0051261 | 0.88096 | 0.0051261
2012/2013 | 2013-02-24 | 0.67774 | 0.00065094 | 0.67774 | 0.00065094
2012/2013 | 2013-02-25 | 0.11435 | 0.00044752 | 0.11435 | 0.00044752
2012/2013 | 2013-02-26 | 0.01224 | 0.00032547 | 0.01224 | 0.00032547
2012/2013 | 2013-02-27 | 0.1151 | 0.01725 | 0.1151 | 0.01725
2012/2013 | 2013-02-28 | 0.08052 | 0.00040683 | 0.08052 | 0.00040683
2012/2013 | 2013-03-01 | 0.1218 | 0.00073248 | 0.1218 | 0.00073248
2012/2013 | 2013-03-02 | 0.01428 | 8.1387e-05 | 0.01428 | 8.1387e-05
2012/2013 | 2013-03-03 | 0.22593 | 0.0018312 | 0.22593 | 0.0018312
2012/2013 | 2013-03-04 | 1.2841 | 0.06458 | 1.2841 | 0.06458
2012/2013 | 2013-03-05 | 0.64549 | 0.0018719 | 0.64549 | 0.0018719
2012/2013 | 2013-03-07 | 1.3547 | 0.0044356 | 1.3547 | 0.0044356
2012/2013 | 2013-03-08 | 0.03984 | 0.00012208 | 0.03984 | 0.00012208
2012/2013 | 2013-03-09 | 0.03988 | 0.00040693 | 0.03988 | 0.00040693
2012/2013 | 2013-03-10 | 0.00525 | 0.00012208 | 0.00525 | 0.00012208
2012/2013 | 2013-03-11 | 0.13836 | 0.0020347 | 0.13836 | 0.0020347
2012/2013 | 2013-03-12 | 5.7516 | 0.036258 | 5.7516 | 0.036258
2012/2013 | 2013-03-13 | 0.13966 | 0.015708 | 0.13966 | 0.015708
2012/2013 | 2013-03-14 | 0.7999 | 0.0021568 | 0.7999 | 0.0021568
2012/2013 | 2013-03-15 | 1.356 | 0.012005 | 1.356 | 0.012005
2012/2013 | 2013-03-16 | 0.01909 | 0.00028485 | 0.01909 | 0.00028485
2012/2013 | 2013-03-17 | 0.80582 | 0.0028078 | 0.80582 | 0.0028078
2012/2013 | 2013-03-18 | 1.0537 | 0.086392 | 1.0537 | 0.086392
2012/2013 | 2013-03-19 | 0.01135 | 0.00028485 | 0.01135 | 0.00028485
2012/2013 | 2013-03-20 | 0.08368 | 0.00032555 | 0.08368 | 0.00032555
2012/2013 | 2013-03-21 | 1.0171 | 0.0041507 | 1.0171 | 0.0041507
2012/2013 | 2013-03-22 | 0.83527 | 0.010824 | 0.83527 | 0.010824
2012/2013 | 2013-03-23 | 0.01445 | 0.0024009 | 0.01445 | 0.0024009
2012/2013 | 2013-03-24 | 0.04217 | 0.00044763 | 0.04217 | 0.00044763
2012/2013 | 2013-03-25 | 0.13857 | 0.00073248 | 0.13857 | 0.00073248
2012/2013 | 2013-03-26 | 0.26796 | 0.0017905 | 0.26796 | 0.0017905
2012/2013 | 2013-03-27 | 0.55351 | 0.0022381 | 0.55351 | 0.0022381
2012/2013 | 2013-03-28 | 0.26344 | 0.001994 | 0.26344 | 0.001994
2012/2013 | 2013-03-30 | 0.07935 | 0.001587 | 0.07935 | 0.001587
2012/2013 | 2013-03-31 | 0.63628 | 0.0034996 | 0.63628 | 0.0034996
2013/2014 | 2013-04-01 | 0.00256 | 4.0713e-05 | 0.00256 | 4.0713e-05
2013/2014 | 2013-04-02 | 0.00721 | 0.00016285 | 0.00721 | 0.00016285
2013/2014 | 2013-04-03 | 0.33735 | 0.0011807 | 0.33735 | 0.0011807
2013/2014 | 2013-04-04 | 0.54917 | 0.0048042 | 0.54917 | 0.0048042
2013/2014 | 2013-04-05 | 0.48913 | 0.0020357 | 0.48913 | 0.0020357
2013/2014 | 2013-04-06 | 3.0595 | 0.099463 | 3.0595 | 0.099463
2013/2014 | 2013-04-07 | 0.01653 | 0.00016285 | 0.01653 | 0.00016285
2013/2014 | 2013-04-08 | 0.11367 | 0.00020357 | 0.11367 | 0.00020357
2013/2014 | 2013-04-09 | 0.01099 | 0.00012214 | 0.01099 | 0.00012214
2013/2014 | 2013-04-10 | 0.41327 | 0.0046006 | 0.41327 | 0.0046006
2013/2014 | 2013-04-11 | 0.07028 | 0.00048856 | 0.07028 | 0.00048856
2013/2014 | 2013-04-12 | 0.41442 | 0.015919 | 0.41442 | 0.015919
2013/2014 | 2013-04-13 | 0.29619 | 0.0010178 | 0.29619 | 0.0010178
2013/2014 | 2013-04-14 | 0.01848 | 0.00020357 | 0.01848 | 0.00020357
2013/2014 | 2013-04-15 | 0.65655 | 0.0086312 | 0.65655 | 0.0086312
2013/2014 | 2013-04-16 | 4.4833 | 0.024998 | 4.4833 | 0.024998
2013/2014 | 2013-04-17 | 0.35283 | 0.0021578 | 0.35283 | 0.0021578
2013/2014 | 2013-04-18 | 0.00847 | 8.1427e-05 | 0.00847 | 8.1427e-05
2013/2014 | 2013-04-19 | 0.08497 | 0.00065141 | 0.08497 | 0.00065141
2013/2014 | 2013-04-20 | 0.0491 | 8.1427e-05 | 0.0491 | 8.1427e-05
2013/2014 | 2013-04-21 | 0.30547 | 0.083992 | 0.30547 | 0.083992
2013/2014 | 2013-04-22 | 0.10463 | 0.00081427 | 0.10463 | 0.00081427
2013/2014 | 2013-04-23 | 1.753 | 0.022799 | 1.753 | 0.022799
2013/2014 | 2013-04-24 | 0.47444 | 0.0024021 | 0.47444 | 0.0024021
2013/2014 | 2013-04-25 | 0.0116 | 0.00020357 | 0.0116 | 0.00020357
2013/2014 | 2013-04-26 | 0.04881 | 0.00044785 | 0.04881 | 0.00044785
2013/2014 | 2013-04-27 | 0.02203 | 0.00028499 | 0.02203 | 0.00028499
2013/2014 | 2013-04-28 | 0.53351 | 0.0022799 | 0.53351 | 0.0022799
2013/2014 | 2013-04-29 | 1.6528 | 0.005252 | 1.6528 | 0.005252
2013/2014 | 2013-04-30 | 0.81655 | 0.0071248 | 0.81655 | 0.0071248
2013/2014 | 2013-05-01 | 0.41278 | 0.0067267 | 0.41278 | 0.0067267
2013/2014 | 2013-05-02 | 0.57757 | 0.0027722 | 0.57757 | 0.0027722
2013/2014 | 2013-05-03 | 0.05418 | 0.00024461 | 0.05418 | 0.00024461
2013/2014 | 2013-05-04 | 1.0354 | 0.021689 | 1.0354 | 0.021689
2013/2014 | 2013-05-05 | 0.52041 | 0.0051368 | 0.52041 | 0.0051368
2013/2014 | 2013-05-06 | 1.3766 | 0.030984 | 1.3766 | 0.030984
2013/2014 | 2013-05-07 | 0.28452 | 0.0033837 | 0.28452 | 0.0033837
2013/2014 | 2013-05-08 | 3.2433 | 0.071181 | 3.2433 | 0.071181
2013/2014 | 2013-05-09 | 0.18469 | 0.0017938 | 0.18469 | 0.0017938
2013/2014 | 2013-05-10 | 1.3698 | 0.0028538 | 1.3698 | 0.0028538
2013/2014 | 2013-05-11 | 0.01892 | 0.00073383 | 0.01892 | 0.00073383
2013/2014 | 2013-05-12 | 0.00962 | 0.0001223 | 0.00962 | 0.0001223
2013/2014 | 2013-05-13 | 1.1748 | 0.0064414 | 1.1748 | 0.0064414
2013/2014 | 2013-05-14 | 0.63602 | 0.0017123 | 0.63602 | 0.0017123
2013/2014 | 2013-05-15 | 2.0922 | 0.0067675 | 2.0922 | 0.0067675
2013/2014 | 2013-05-16 | 0.0243 | 0.00020384 | 0.0243 | 0.00020384
2013/2014 | 2013-05-18 | 0.11142 | 0.0008969 | 0.11142 | 0.0008969
2013/2014 | 2013-05-19 | 0.11272 | 0.0018346 | 0.11272 | 0.0018346
2013/2014 | 2013-05-20 | 2.8089 | 0.01696 | 2.8089 | 0.01696
2013/2014 | 2013-05-21 | 1.0329 | 0.0040768 | 1.0329 | 0.0040768
2013/2014 | 2013-05-22 | 2.4002 | 0.0074606 | 2.4002 | 0.0074606
2013/2014 | 2013-05-23 | 0.02434 | 0.001753 | 0.02434 | 0.001753
2013/2014 | 2013-05-24 | 0.23397 | 0.001223 | 0.23397 | 0.001223
2013/2014 | 2013-05-26 | 0.95084 | 0.0092544 | 0.95084 | 0.0092544
2013/2014 | 2013-05-27 | 0.33111 | 0.0011415 | 0.33111 | 0.0011415
2013/2014 | 2013-05-28 | 0.01529 | 0.0001223 | 0.01529 | 0.0001223
2013/2014 | 2013-05-29 | 1.8021 | 0.094704 | 1.8021 | 0.094704
2013/2014 | 2013-05-30 | 4.0138 | 0.0069713 | 4.0138 | 0.0069713
2013/2014 | 2013-05-31 | 2.166 | 0.013127 | 2.166 | 0.013127
2013/2014 | 2013-06-01 | 0.00436 | 4.0735e-05 | 0.00436 | 4.0735e-05
2013/2014 | 2013-06-04 | 0.20751 | 0.0031773 | 0.20751 | 0.0031773
2013/2014 | 2013-06-05 | 0.42951 | 0.0016294 | 0.42951 | 0.0016294
2013/2014 | 2013-06-06 | 0.01238 | 0.00016294 | 0.01238 | 0.00016294
2013/2014 | 2013-06-07 | 3.8593 | 0.086928 | 3.8593 | 0.086928
2013/2014 | 2013-06-08 | 0.00807 | 4.0735e-05 | 0.00807 | 4.0735e-05
2013/2014 | 2013-06-09 | 0.27754 | 0.0023626 | 0.27754 | 0.0023626
2013/2014 | 2013-06-10 | 0.22041 | 0.0010184 | 0.22041 | 0.0010184
2013/2014 | 2013-06-11 | 0.83262 | 0.004766 | 0.83262 | 0.004766
2013/2014 | 2013-06-12 | 1.4814 | 0.0060695 | 1.4814 | 0.0060695
2013/2014 | 2013-06-15 | 0.1143 | 0.0024848 | 0.1143 | 0.0024848
2013/2014 | 2013-06-16 | 0.087 | 0.0013443 | 0.087 | 0.0013443
2013/2014 | 2013-06-17 | 0.05337 | 0.00020367 | 0.05337 | 0.00020367
2013/2014 | 2013-06-18 | 1.033 | 0.023667 | 1.033 | 0.023667
2013/2014 | 2013-06-19 | 0.03422 | 0.00028514 | 0.03422 | 0.00028514
2013/2014 | 2013-06-20 | 0.39762 | 0.014257 | 0.39762 | 0.014257
2013/2014 | 2013-06-21 | 4.3884 | 0.032995 | 4.3884 | 0.032995
2013/2014 | 2013-06-22 | 2.5887 | 0.026355 | 2.5887 | 0.026355
2013/2014 | 2013-06-23 | 0.01735 | 0.00024441 | 0.01735 | 0.00024441
2013/2014 | 2013-06-24 | 0.20543 | 0.0014257 | 0.20543 | 0.0014257
2013/2014 | 2013-06-25 | 2.9657 | 0.009369 | 2.9657 | 0.009369
2013/2014 | 2013-06-26 | 0.56906 | 0.006151 | 0.56906 | 0.006151
2013/2014 | 2013-06-27 | 0.12523 | 0.0037883 | 0.12523 | 0.0037883
2013/2014 | 2013-06-28 | 0.02982 | 0.00016294 | 0.02982 | 0.00016294
2013/2014 | 2013-06-29 | 0.41468 | 0.10367 | 0.41468 | 0.10367
2013/2014 | 2013-06-30 | 0.01597 | 0.003992 | 0.01597 | 0.003992
2013/2014 | 2013-07-01 | 0.21641 | 0.0029735 | 0.21641 | 0.0029735
2013/2014 | 2013-07-02 | 0.74257 | 0.0017923 | 0.74257 | 0.0017923
2013/2014 | 2013-07-03 | 0.15026 | 0.0011405 | 0.15026 | 0.0011405
2013/2014 | 2013-07-04 | 1.3937 | 0.039552 | 1.3937 | 0.039552
2013/2014 | 2013-07-05 | 0.0191 | 0.0002444 | 0.0191 | 0.0002444
2013/2014 | 2013-07-06 | 0.08253 | 0.00016293 | 0.08253 | 0.00016293
2013/2014 | 2013-07-07 | 0.01043 | 8.1466e-05 | 0.01043 | 8.1466e-05
2013/2014 | 2013-07-08 | 0.34048 | 0.00081466 | 0.34048 | 0.00081466
2013/2014 | 2013-07-09 | 0.26989 | 0.0010998 | 0.26989 | 0.0010998
2013/2014 | 2013-07-10 | 0.22497 | 0.0014257 | 0.22497 | 0.0014257
2013/2014 | 2013-07-11 | 0.4499 | 0.001833 | 0.4499 | 0.001833
2013/2014 | 2013-07-12 | 0.13613 | 0.0007332 | 0.13613 | 0.0007332
2013/2014 | 2013-07-13 | 0.36074 | 0.0017108 | 0.36074 | 0.0017108
2013/2014 | 2013-07-14 | 1.4765 | 0.0059063 | 1.4765 | 0.0059063
2013/2014 | 2013-07-15 | 0.9356 | 0.0078208 | 0.9356 | 0.0078208
2013/2014 | 2013-07-16 | 0.28982 | 0.0015886 | 0.28982 | 0.0015886
2013/2014 | 2013-07-17 | 0.45401 | 0.0024033 | 0.45401 | 0.0024033
2013/2014 | 2013-07-18 | 0.74025 | 0.0044807 | 0.74025 | 0.0044807
2013/2014 | 2013-07-19 | 0.0791 | 0.0010183 | 0.0791 | 0.0010183
2013/2014 | 2013-07-20 | 0.0435 | 0.0001222 | 0.0435 | 0.0001222
2013/2014 | 2013-07-21 | 0.00464 | 8.1466e-05 | 0.00464 | 8.1466e-05
2013/2014 | 2013-07-22 | 0.44623 | 0.0016701 | 0.44623 | 0.0016701
2013/2014 | 2013-07-23 | 0.86668 | 0.0027699 | 0.86668 | 0.0027699
2013/2014 | 2013-07-24 | 3.478 | 0.072831 | 3.478 | 0.072831
2013/2014 | 2013-07-25 | 0.08306 | 0.0040733 | 0.08306 | 0.0040733
2013/2014 | 2013-07-26 | 0.71438 | 0.0068839 | 0.71438 | 0.0068839
2013/2014 | 2013-07-29 | 1.7738 | 0.0058248 | 1.7738 | 0.0058248
2013/2014 | 2013-07-30 | 1.1068 | 0.0094094 | 1.1068 | 0.0094094
2013/2014 | 2013-07-31 | 1.0101 | 0.010794 | 1.0101 | 0.010794
2013/2014 | 2013-08-01 | 0.3586 | 0.17812 | 0.3586 | 0.17812
2013/2014 | 2013-08-02 | 0.68136 | 0.0019551 | 0.68136 | 0.0019551
2013/2014 | 2013-08-04 | 0.01083 | 8.1463e-05 | 0.01083 | 8.1463e-05
2013/2014 | 2013-08-05 | 0.37832 | 0.0036658 | 0.37832 | 0.0036658
2013/2014 | 2013-08-06 | 1.3738 | 0.003788 | 1.3738 | 0.003788
2013/2014 | 2013-08-07 | 0.03401 | 0.00036658 | 0.03401 | 0.00036658
2013/2014 | 2013-08-08 | 1.6947 | 0.0075353 | 1.6947 | 0.0075353
2013/2014 | 2013-08-09 | 0.25254 | 0.0021588 | 0.25254 | 0.0021588
2013/2014 | 2013-08-10 | 0.04391 | 0.00057024 | 0.04391 | 0.00057024
2013/2014 | 2013-08-12 | 0.32121 | 0.019347 | 0.32121 | 0.019347
2013/2014 | 2013-08-13 | 0.01026 | 0.00016293 | 0.01026 | 0.00016293
2013/2014 | 2013-08-14 | 0.00941 | 0.00012219 | 0.00941 | 0.00012219
2013/2014 | 2013-08-15 | 0.41729 | 0.0015885 | 0.41729 | 0.0015885
2013/2014 | 2013-08-16 | 2.3562 | 0.011608 | 2.3562 | 0.011608
2013/2014 | 2013-08-17 | 0.2316 | 0.0024032 | 0.2316 | 0.0024032
2013/2014 | 2013-08-20 | 2.138 | 0.020488 | 2.138 | 0.020488
2013/2014 | 2013-08-21 | 1.4947 | 0.0038695 | 1.4947 | 0.0038695
2013/2014 | 2013-08-22 | 0.00379 | 4.0732e-05 | 0.00379 | 4.0732e-05
2013/2014 | 2013-08-26 | 0.1059 | 0.0010183 | 0.1059 | 0.0010183
2013/2014 | 2013-08-27 | 0.25278 | 0.00089609 | 0.25278 | 0.00089609
2013/2014 | 2013-08-28 | 0.56873 | 0.0054988 | 0.56873 | 0.0054988
2013/2014 | 2013-08-29 | 0.05938 | 0.00040732 | 0.05938 | 0.00040732
2013/2014 | 2013-08-30 | 0.26524 | 0.0014256 | 0.26524 | 0.0014256
2013/2014 | 2013-08-31 | 1.1858 | 0.0017107 | 1.1858 | 0.0017107
2013/2014 | 2013-09-01 | 0.12291 | 0.018234 | 0.12291 | 0.018234
2013/2014 | 2013-09-02 | 0.13682 | 0.001387 | 0.13682 | 0.001387
2013/2014 | 2013-09-03 | 0.16778 | 0.0018357 | 0.16778 | 0.0018357
2013/2014 | 2013-09-04 | 0.3044 | 0.0048952 | 0.3044 | 0.0048952
2013/2014 | 2013-09-05 | 1.8629 | 0.0077507 | 1.8629 | 0.0077507
2013/2014 | 2013-09-06 | 0.33361 | 0.0013462 | 0.33361 | 0.0013462
2013/2014 | 2013-09-09 | 0.42021 | 0.0014278 | 0.42021 | 0.0014278
2013/2014 | 2013-09-10 | 11.0802 | 0.53104 | 11.0802 | 0.53104
2013/2014 | 2013-09-11 | 1.5455 | 0.0031819 | 1.5455 | 0.0031819
2013/2014 | 2013-09-12 | 0.00934 | 8.1586e-05 | 0.00934 | 8.1586e-05
2013/2014 | 2013-09-13 | 0.01632 | 0.00012238 | 0.01632 | 0.00012238
2013/2014 | 2013-09-15 | 0.01591 | 8.1586e-05 | 0.01591 | 8.1586e-05
2013/2014 | 2013-09-16 | 2.9685 | 0.015093 | 2.9685 | 0.015093
2013/2014 | 2013-09-17 | 0.7238 | 0.0028555 | 0.7238 | 0.0028555
2013/2014 | 2013-09-18 | 0.09072 | 0.00024476 | 0.09072 | 0.00024476
2013/2014 | 2013-09-19 | 0.16435 | 0.0012238 | 0.16435 | 0.0012238
2013/2014 | 2013-09-20 | 0.3232 | 0.0016725 | 0.3232 | 0.0016725
2013/2014 | 2013-09-21 | 0.18974 | 0.0017541 | 0.18974 | 0.0017541
2013/2014 | 2013-09-22 | 1.7885 | 0.0062005 | 1.7885 | 0.0062005
2013/2014 | 2013-09-23 | 0.50678 | 0.0053031 | 0.50678 | 0.0053031
2013/2014 | 2013-09-24 | 3.6332 | 0.041976 | 3.6332 | 0.041976
2013/2014 | 2013-09-25 | 4.3152 | 0.016399 | 4.3152 | 0.016399
2013/2014 | 2013-09-26 | 0.36833 | 0.0028147 | 0.36833 | 0.0028147
2013/2014 | 2013-09-27 | 0.18875 | 0.0012646 | 0.18875 | 0.0012646
2013/2014 | 2013-09-28 | 0.29138 | 0.0011014 | 0.29138 | 0.0011014
2013/2014 | 2013-09-29 | 0.0503 | 0.00016317 | 0.0503 | 0.00016317
2013/2014 | 2013-09-30 | 0.47707 | 0.0082402 | 0.47707 | 0.0082402
2013/2014 | 2013-10-01 | 0.86259 | 0.054329 | 0.86259 | 0.054329
2013/2014 | 2013-10-02 | 0.32401 | 0.0025715 | 0.32401 | 0.0025715
2013/2014 | 2013-10-03 | 0.82048 | 0.0027348 | 0.82048 | 0.0027348
2013/2014 | 2013-10-04 | 0.66947 | 0.0020001 | 0.66947 | 0.0020001
2013/2014 | 2013-10-05 | 0.50288 | 0.002245 | 0.50288 | 0.002245
2013/2014 | 2013-10-06 | 0.00343 | 4.0818e-05 | 0.00343 | 4.0818e-05
2013/2014 | 2013-10-07 | 1.1448 | 0.0047349 | 1.1448 | 0.0047349
2013/2014 | 2013-10-08 | 4.8878 | 0.061594 | 4.8878 | 0.061594
2013/2014 | 2013-10-09 | 2.8268 | 0.020817 | 2.8268 | 0.020817
2013/2014 | 2013-10-10 | 1.654 | 0.0086942 | 1.654 | 0.0086942
2013/2014 | 2013-10-11 | 1.8183 | 0.012164 | 1.8183 | 0.012164
2013/2014 | 2013-10-12 | 1.0798 | 0.0074289 | 1.0798 | 0.0074289
2013/2014 | 2013-10-13 | 0.26021 | 0.00069391 | 0.26021 | 0.00069391
2013/2014 | 2013-10-14 | 1.2821 | 0.015715 | 1.2821 | 0.015715
2013/2014 | 2013-10-15 | 16.5116 | 0.42353 | 16.5116 | 0.42353
2013/2014 | 2013-10-16 | 0.17983 | 0.010409 | 0.17983 | 0.010409
2013/2014 | 2013-10-17 | 3.8046 | 0.018899 | 3.8046 | 0.018899
2013/2014 | 2013-10-18 | 0.31227 | 0.0050206 | 0.31227 | 0.0050206
2013/2014 | 2013-10-19 | 0.01763 | 0.00016327 | 0.01763 | 0.00016327
2013/2014 | 2013-10-20 | 0.28703 | 0.080248 | 0.28703 | 0.080248
2013/2014 | 2013-10-21 | 0.26575 | 0.0010204 | 0.26575 | 0.0010204
2013/2014 | 2013-10-22 | 1.8174 | 0.009184 | 1.8174 | 0.009184
2013/2014 | 2013-10-23 | 0.21107 | 0.00053063 | 0.21107 | 0.00053063
2013/2014 | 2013-10-24 | 0.01922 | 0.00024491 | 0.01922 | 0.00024491
2013/2014 | 2013-10-25 | 0.05098 | 0.00081636 | 0.05098 | 0.00081636
2013/2014 | 2013-10-26 | 3.8998 | 0.13776 | 3.8998 | 0.13776
2013/2014 | 2013-10-27 | 0.16421 | 0.0014286 | 0.16421 | 0.0014286
2013/2014 | 2013-10-28 | 0.18698 | 0.0018776 | 0.18698 | 0.0018776
2013/2014 | 2013-10-29 | 0.1558 | 0.000898 | 0.1558 | 0.000898
2013/2014 | 2013-10-30 | 0.90652 | 0.0083269 | 0.90652 | 0.0083269
2013/2014 | 2013-10-31 | 2.4961 | 0.0082044 | 2.4961 | 0.0082044
2013/2014 | 2013-11-01 | 0.52973 | 0.0024845 | 0.52973 | 0.0024845
2013/2014 | 2013-11-02 | 0.05214 | 0.00048876 | 0.05214 | 0.00048876
2013/2014 | 2013-11-03 | 0.01365 | 0.00020365 | 0.01365 | 0.00020365
2013/2014 | 2013-11-04 | 0.11718 | 0.00020365 | 0.11718 | 0.00020365
2013/2014 | 2013-11-05 | 0.0903 | 0.00073314 | 0.0903 | 0.00073314
2013/2014 | 2013-11-06 | 0.58113 | 0.0032991 | 0.58113 | 0.0032991
2013/2014 | 2013-11-07 | 0.11161 | 0.0008146 | 0.11161 | 0.0008146
2013/2014 | 2013-11-08 | 1.0542 | 0.0051727 | 1.0542 | 0.0051727
2013/2014 | 2013-11-09 | 2.0864 | 0.0080645 | 2.0864 | 0.0080645
2013/2014 | 2013-11-10 | 1.155 | 0.014663 | 1.155 | 0.014663
2013/2014 | 2013-11-11 | 0.32714 | 0.0011812 | 0.32714 | 0.0011812
2013/2014 | 2013-11-12 | 0.04716 | 0.00028511 | 0.04716 | 0.00028511
2013/2014 | 2013-11-13 | 1.8777 | 0.018451 | 1.8777 | 0.018451
2013/2014 | 2013-11-14 | 0.35007 | 0.0013034 | 0.35007 | 0.0013034
2013/2014 | 2013-11-15 | 0.98917 | 0.0035435 | 0.98917 | 0.0035435
2013/2014 | 2013-11-16 | 0.13111 | 0.0011812 | 0.13111 | 0.0011812
2013/2014 | 2013-11-18 | 0.01454 | 0.00048876 | 0.01454 | 0.00048876
2013/2014 | 2013-11-19 | 0.59074 | 0.0048469 | 0.59074 | 0.0048469
2013/2014 | 2013-11-20 | 2.8271 | 0.0080645 | 2.8271 | 0.0080645
2013/2014 | 2013-11-21 | 2.8072 | 0.0070055 | 2.8072 | 0.0070055
2013/2014 | 2013-11-22 | 1.4335 | 0.0064761 | 1.4335 | 0.0064761
2013/2014 | 2013-11-23 | 0.19383 | 0.001507 | 0.19383 | 0.001507
2013/2014 | 2013-11-24 | 0.45784 | 0.0068019 | 0.45784 | 0.0068019
2013/2014 | 2013-11-25 | 0.03103 | 0.00032584 | 0.03103 | 0.00032584
2013/2014 | 2013-11-26 | 1.4753 | 0.0065168 | 1.4753 | 0.0065168
2013/2014 | 2013-11-27 | 1.5714 | 0.0086347 | 1.5714 | 0.0086347
2013/2014 | 2013-11-28 | 2.7792 | 0.015233 | 2.7792 | 0.015233
2013/2014 | 2013-11-29 | 1.0244 | 0.0043581 | 1.0244 | 0.0043581
2013/2014 | 2013-11-30 | 2.3422 | 0.027615 | 2.3422 | 0.027615
2013/2014 | 2013-12-01 | 0.00823 | 8.144e-05 | 0.00823 | 8.144e-05
2013/2014 | 2013-12-02 | 0.05432 | 0.0013438 | 0.05432 | 0.0013438
2013/2014 | 2013-12-03 | 1.6208 | 0.026631 | 1.6208 | 0.026631
2013/2014 | 2013-12-04 | 0.03307 | 0.0004072 | 0.03307 | 0.0004072
2013/2014 | 2013-12-05 | 2.3786 | 0.016369 | 2.3786 | 0.016369
2013/2014 | 2013-12-06 | 0.91758 | 0.0089991 | 0.91758 | 0.0089991
2013/2014 | 2013-12-07 | 0.03054 | 0.0018324 | 0.03054 | 0.0018324
2013/2014 | 2013-12-08 | 0.01099 | 0.00012216 | 0.01099 | 0.00012216
2013/2014 | 2013-12-09 | 0.21985 | 0.0063116 | 0.21985 | 0.0063116
2013/2014 | 2013-12-10 | 0.78736 | 0.0020767 | 0.78736 | 0.0020767
2013/2014 | 2013-12-11 | 0.06499 | 0.00024432 | 0.06499 | 0.00024432
2013/2014 | 2013-12-12 | 0.83126 | 0.0059858 | 0.83126 | 0.0059858
2013/2014 | 2013-12-13 | 0.8111 | 0.0030133 | 0.8111 | 0.0030133
2013/2014 | 2013-12-14 | 0.32861 | 0.0024839 | 0.32861 | 0.0024839
2013/2014 | 2013-12-15 | 0.16964 | 0.046991 | 0.16964 | 0.046991
2013/2014 | 2013-12-16 | 0.11349 | 0.00057008 | 0.11349 | 0.00057008
2013/2014 | 2013-12-18 | 0.61402 | 0.0078182 | 0.61402 | 0.0078182
2013/2014 | 2013-12-19 | 0.85234 | 0.013723 | 0.85234 | 0.013723
2013/2014 | 2013-12-20 | 0.16003 | 0.00065152 | 0.16003 | 0.00065152
2013/2014 | 2013-12-21 | 0.37491 | 0.0025654 | 0.37491 | 0.0025654
2013/2014 | 2013-12-22 | 0.04414 | 4.072e-05 | 0.04414 | 4.072e-05
2013/2014 | 2013-12-23 | 2.1533 | 0.010506 | 2.1533 | 0.010506
2013/2014 | 2013-12-24 | 0.0092 | 8.144e-05 | 0.0092 | 8.144e-05
2013/2014 | 2013-12-25 | 0.09439 | 0.0019953 | 0.09439 | 0.0019953
2013/2014 | 2013-12-26 | 0.09354 | 0.001018 | 0.09354 | 0.001018
2013/2014 | 2013-12-27 | 0.55448 | 0.0021174 | 0.55448 | 0.0021174
2013/2014 | 2013-12-29 | 1.7307 | 0.026957 | 1.7307 | 0.026957
2013/2014 | 2013-12-30 | 1.7243 | 0.0069224 | 1.7243 | 0.0069224
2013/2014 | 2013-12-31 | 0.06755 | 0.0096506 | 0.06755 | 0.0096506
2013/2014 | 2014-01-01 | 0.13764 | 0.00048864 | 0.13764 | 0.00048864
2013/2014 | 2014-01-02 | 0.04541 | 0.00044792 | 0.04541 | 0.00044792
2013/2014 | 2014-01-03 | 0.64448 | 0.0039906 | 0.64448 | 0.0039906
2013/2014 | 2014-01-04 | 0.32454 | 0.0038684 | 0.32454 | 0.0038684
2013/2014 | 2014-01-06 | 0.24574 | 0.015026 | 0.24574 | 0.015026
2013/2014 | 2014-01-07 | 0.38973 | 0.0019546 | 0.38973 | 0.0019546
2013/2014 | 2014-01-08 | 0.89902 | 0.0074517 | 0.89902 | 0.0074517
2013/2014 | 2014-01-09 | 1.0578 | 0.07016 | 1.0578 | 0.07016
2013/2014 | 2014-01-10 | 1.9116 | 0.013275 | 1.9116 | 0.013275
2013/2014 | 2014-01-11 | 0.15038 | 0.0018731 | 0.15038 | 0.0018731
2013/2014 | 2014-01-12 | 0.13022 | 0.00069224 | 0.13022 | 0.00069224
2013/2014 | 2014-01-13 | 0.2069 | 0.0020767 | 0.2069 | 0.0020767
2013/2014 | 2014-01-14 | 0.42728 | 0.0020767 | 0.42728 | 0.0020767
2013/2014 | 2014-01-15 | 0.47419 | 0.0024839 | 0.47419 | 0.0024839
2013/2014 | 2014-01-16 | 0.38008 | 0.0010587 | 0.38008 | 0.0010587
2013/2014 | 2014-01-17 | 0.25275 | 0.0021989 | 0.25275 | 0.0021989
2013/2014 | 2014-01-19 | 0.17382 | 0.0022396 | 0.17382 | 0.0022396
2013/2014 | 2014-01-20 | 0.24879 | 0.0021582 | 0.24879 | 0.0021582
2013/2014 | 2014-01-21 | 0.10526 | 0.0006108 | 0.10526 | 0.0006108
2013/2014 | 2014-01-22 | 0.14244 | 0.00044792 | 0.14244 | 0.00044792
2013/2014 | 2014-01-23 | 0.95597 | 0.0037462 | 0.95597 | 0.0037462
2013/2014 | 2014-01-24 | 0.21565 | 0.0015474 | 0.21565 | 0.0015474
2013/2014 | 2014-01-25 | 0.01596 | 0.00028504 | 0.01596 | 0.00028504
2013/2014 | 2014-01-26 | 0.64936 | 0.0083883 | 0.64936 | 0.0083883
2013/2014 | 2014-01-27 | 0.00358 | 8.144e-05 | 0.00358 | 8.144e-05
2013/2014 | 2014-01-28 | 0.13469 | 0.0011809 | 0.13469 | 0.0011809
2013/2014 | 2014-01-29 | 0.12029 | 0.010628 | 0.12029 | 0.010628
2013/2014 | 2014-01-30 | 0.51772 | 0.05827 | 0.51772 | 0.05827
2013/2014 | 2014-01-31 | 0.56051 | 0.086286 | 0.56051 | 0.086286
2013/2014 | 2014-02-01 | 0.00851 | 8.1446e-05 | 0.00851 | 8.1446e-05
2013/2014 | 2014-02-02 | 0.62005 | 0.062632 | 0.62005 | 0.062632
2013/2014 | 2014-02-03 | 0.10078 | 0.00061085 | 0.10078 | 0.00061085
2013/2014 | 2014-02-05 | 0.14758 | 0.00032579 | 0.14758 | 0.00032579
2013/2014 | 2014-02-07 | 0.00554 | 4.0723e-05 | 0.00554 | 4.0723e-05
2013/2014 | 2014-02-08 | 0.22303 | 0.0013031 | 0.22303 | 0.0013031
2013/2014 | 2014-02-09 | 0.0147 | 0.00057013 | 0.0147 | 0.00057013
2013/2014 | 2014-02-10 | 0.69881 | 0.0042759 | 0.69881 | 0.0042759
2013/2014 | 2014-02-11 | 0.38993 | 0.001181 | 0.38993 | 0.001181
2013/2014 | 2014-02-12 | 0.4967 | 0.0075745 | 0.4967 | 0.0075745
2013/2014 | 2014-02-14 | 11.2962 | 0.046465 | 11.2962 | 0.046465
2013/2014 | 2014-02-15 | 0.01254 | 0.00016289 | 0.01254 | 0.00016289
2013/2014 | 2014-02-16 | 0.00766 | 8.1446e-05 | 0.00766 | 8.1446e-05
2013/2014 | 2014-02-17 | 0.55013 | 0.0015475 | 0.55013 | 0.0015475
2013/2014 | 2014-02-18 | 0.48469 | 0.0015475 | 0.48469 | 0.0015475
2013/2014 | 2014-02-19 | 0.21257 | 0.0005294 | 0.21257 | 0.0005294
2013/2014 | 2014-02-20 | 0.24927 | 0.0017511 | 0.24927 | 0.0017511
2013/2014 | 2014-02-21 | 0.28074 | 0.027 | 0.28074 | 0.027
2013/2014 | 2014-02-22 | 0.11138 | 0.00093663 | 0.11138 | 0.00093663
2013/2014 | 2014-02-23 | 0.02981 | 0.00040723 | 0.02981 | 0.00040723
2013/2014 | 2014-02-24 | 0.10808 | 0.0032986 | 0.10808 | 0.0032986
2013/2014 | 2014-02-25 | 2.0555 | 0.080795 | 2.0555 | 0.080795
2013/2014 | 2014-02-26 | 0.00143 | 4.0723e-05 | 0.00143 | 4.0723e-05
2013/2014 | 2014-02-28 | 0.18492 | 0.0013031 | 0.18492 | 0.0013031
2013/2014 | 2014-03-01 | 0.21889 | 0.0016287 | 0.21889 | 0.0016287
2013/2014 | 2014-03-02 | 0.23339 | 0.027036 | 0.23339 | 0.027036
2013/2014 | 2014-03-03 | 0.06922 | 0.0015879 | 0.06922 | 0.0015879
2013/2014 | 2014-03-04 | 1.3206 | 0.076547 | 1.3206 | 0.076547
2013/2014 | 2014-03-05 | 0.17182 | 0.0011808 | 0.17182 | 0.0011808
2013/2014 | 2014-03-06 | 0.01303 | 0.0002443 | 0.01303 | 0.0002443
2013/2014 | 2014-03-07 | 0.00387 | 4.0717e-05 | 0.00387 | 4.0717e-05
2013/2014 | 2014-03-10 | 0.16388 | 0.0014251 | 0.16388 | 0.0014251
2013/2014 | 2014-03-11 | 0.15757 | 0.0017101 | 0.15757 | 0.0017101
2013/2014 | 2014-03-12 | 0.66266 | 0.0020765 | 0.66266 | 0.0020765
2013/2014 | 2014-03-13 | 0.2059 | 0.00052932 | 0.2059 | 0.00052932
2013/2014 | 2014-03-14 | 0.55399 | 0.0024023 | 0.55399 | 0.0024023
2013/2014 | 2014-03-15 | 4.688 | 0.044585 | 4.688 | 0.044585
2013/2014 | 2014-03-16 | 0.64609 | 0.022313 | 0.64609 | 0.022313
2013/2014 | 2014-03-17 | 0.24425 | 0.0021987 | 0.24425 | 0.0021987
2013/2014 | 2014-03-18 | 0.64079 | 0.0041938 | 0.64079 | 0.0041938
2013/2014 | 2014-03-19 | 0.07317 | 0.00052932 | 0.07317 | 0.00052932
2013/2014 | 2014-03-20 | 0.002 | 0.00028502 | 0.002 | 0.00028502
2013/2014 | 2014-03-21 | 0.73888 | 0.0058632 | 0.73888 | 0.0058632
2013/2014 | 2014-03-22 | 0.01445 | 0.00020358 | 0.01445 | 0.00020358
2013/2014 | 2014-03-23 | 1.0528 | 0.0029316 | 1.0528 | 0.0029316
2013/2014 | 2014-03-24 | 0.00314 | 4.0717e-05 | 0.00314 | 4.0717e-05
2013/2014 | 2014-03-25 | 1.7908 | 0.0040717 | 1.7908 | 0.0040717
2013/2014 | 2014-03-26 | 0.97855 | 0.0026466 | 0.97855 | 0.0026466
2013/2014 | 2014-03-27 | 0.30088 | 0.0013844 | 0.30088 | 0.0013844
2013/2014 | 2014-03-28 | 0.00835 | 0.00020358 | 0.00835 | 0.00020358
2013/2014 | 2014-03-29 | 0.4482 | 0.0020358 | 0.4482 | 0.0020358
2013/2014 | 2014-03-30 | 0.16502 | 0.0056189 | 0.16502 | 0.0056189
2013/2014 | 2014-03-31 | 0.94173 | 0.004601 | 0.94173 | 0.004601

## (2c)_2010-14_SummaryNorm
2010-2014 Summary Sheet with Normalised
SAIDI (Interruption Duration)
| Disclosed Actuals by Class |  |  |  | TLC 2010-2014 Dataset Actuals by Class |  |  |  | Variance in Actuals by Class |  |  | SAIDI Normalised
| Class B | Class C | Total |  | Class B | Class C | Total SAIDI Actual |  | Class B | Class C | Total | TLC 2010-14 Dataset | Disclosed | Variance to Disclosed
2010 | 91.92 | 205.69 | 297.61 |  | 83.032 | 205.7432 | 288.7752 |  | 8.888 | -0.05322 | 8.8348 | 262.8817
2011 | 63.58 | 228.85 | 292.43 |  | 68.1888 | 228.8597 | 297.0485 |  | -4.6088 | -0.00972 | -4.6185 | 264.9671 | 260.35 | -4.6171
2012 | 71.698 | 252.827 | 324.524 |  | 71.6975 | 252.8272 | 324.5247 |  | 0.00046 | -0.00016 | -0.0007 | 311.8828 | 311.8821 | -0.00070854
2013 | 83.013 | 116.553 | 199.565 |  | 83.0125 | 116.5528 | 199.5653 |  | 0.0005 | 0.00025 | -0.00025 | 199.5653 | 199.57 | 0.00475
2014 | 83.6106 | 186.845 | 270.4555 |  | 83.6106 | 186.8449 | 270.4555 |  | -3e-05 | 6e-05 | 3e-05 | 270.4555 | 270.4555 | 3e-05
SAIFI (Interruption Frequency)
| Disclosed Actuals by Class |  |  |  | TLC 2010-14 Dataset Actuals by Class |  |  |  | Variances in Actuals by Class |  |  | SAIFI Normalised
Year | Class B | Class C | Total |  | Planned : Class B | Unplanned : Class C | Total of SAIFI Actual |  | Class B | Class C | Total | TLC 2010-14 Dataset | Disclosed | Variance to Disclosed
2010 | 0.55 | 2.11 | 2.66 |  | 0.55478 | 2.1107 | 2.6655 |  | -0.0047784 | -0.00073976 | -0.0055182 | 2.6655
2011 | 0.48 | 2.99 | 3.47 |  | 0.47817 | 3.1878 | 3.6659 |  | 0.001826 | -0.19775 | -0.19593 | 3.6659 | 3.474 | -0.19193
2012 | 0.506 | 3.48 | 3.986 |  | 0.50658 | 3.5075 | 4.014 |  | -0.00058425 | -0.027465 | -0.028049 | 4.014 | 3.987 | -0.027049
2013 | 0.54 | 1.78 | 2.32 |  | 0.5412 | 1.7764 | 2.3176 |  | -0.001197 | 0.0036246 | 0.0024276 | 2.3176 | 2.32 | 0.0024276
2014 | 0.46378 | 3.6668 | 4.1306 |  | 0.46379 | 3.6668 | 4.1306 |  | -6.9076e-06 | -3.6965e-06 | -1.0604e-05 | 4.1306 | 4.1306 | -1e-05
Source = "(2a)_2010-14_incidents" | [6 empty] | Source = "(2b)_2010-14_dailyAggregates"
| SAIDI Actual | SAIDI Actual | SAIDI Actual | SAIFI Actual | SAIFI Actual | SAIFI Actual
Year | Planned : Class B | Unplanned : Class C | Total of SAIDI Actual | Planned : Class B | Unplanned : Class C | Total of SAIFI Actual | SAIDI Normalised | SAIFI Normalised | chk_SAIDI Actual | chk_SAIFI Actual
2009/2010 | 83.032 | 205.7432 | 288.7752 | 0.55478 | 2.1107 | 2.6655 | 262.8817 | 2.6655 | 288.7752 | 2.6655
2010/2011 | 68.1888 | 228.8597 | 297.0485 | 0.47817 | 3.1878 | 3.6659 | 264.9671 | 3.6659 | 297.0485 | 3.6659
2011/2012 | 71.6975 | 252.8272 | 324.5247 | 0.50658 | 3.5075 | 4.014 | 311.8828 | 4.014 | 324.5247 | 4.014
2012/2013 | 83.0125 | 116.5528 | 199.5653 | 0.5412 | 1.7764 | 2.3176 | 199.5653 | 2.3176 | 199.5653 | 2.3176
2013/2014 | 83.6106 | 186.8449 | 270.4555 | 0.46379 | 3.6668 | 4.1306 | 270.4555 | 4.1306 | 270.4555 | 4.1306

## (2d)_2010-10_Customers
Average customers per annum
| Year | TLC Average Total Customers | Registry Customer Count
| 2010 | 24276 | 24396
| 2011 | 24485 | 24423
| 2012 | 24458 | 24337
| 2013 | 24584 | 24316
| 2014 | 24545 | 24368
Notes
> | Since August 2008, outage calculations in Basix have been done on the Total Customers each month rather than on an annual average. (The closing total for the prior month is used as the base figure for the current month calculations.)
> | The figures provided shown above for the years 2009 to 2014 (inclusive) are the average of the monthly divisors
> | Recent changes in the Registry database mean we are unable to recover figures for 2005-2007
> | The discrepancy between TLC and Registry counts is two-fold:
i) The TLC figures are the average of the monthly divisor
ii) The TLC figures include some customers where a Total Dismantle has taken place.
> | The discrepancy with Total Dismantle records has only recently been discovered and steps are underway to correct the process for future calculations. The impact is not believed to be material – the increased count may well be offset by the increased customers during an outage.