## CoverSheet
Electricity Distribution Business
Price-Quality Regulation 1 April 2025 DPP Reset
Reliability standards and incentives model
Draft determination
Published 29 May 2024

## Table of Contents
Table of Contents
| Sheet Name | Link
| Inputs from R | Inputs from R (statistical lsoftware)
Unplanned disruption standards - DPP4
Planned disruption standards - DPP4
| Other Inputs | Other Inputs
Inputs that are the same for all distributors
Inputs that are specific to individual distributors
| Calculations | Calculations for the selected EDB
Inputs
Calculations
Outputs
| Calculations-Chartbook | Calculations Chartbook
Frequency of major events
| Output | Outputs
| Chart book | Outputs Chart book
Tables for Draft Reasons paper
Tables for Draft Determination

## Description
Description
This Excel workbook is one of a suite of models for modelling for the EDB DPP4 draft decision.
General description
1 | This model calculates quality standards which must be met by price-quality regulated EDBs during the DPP4 regulatory period. It also provides quality incentive scheme parameters, including incentive rates.
Inputs
1 | All data used by the model is entered in the two 'Input' sheets for the EDB selected in cell C5 of the 'Output' sheet:
2 | The 'Inputs from R' sheet uses the raw output from the R model. The R code (Stata for DPP3) normalises unplanned raw interruption data provided by the EDBs and calculates historical averages, boundary values, standard deviation, etc.
3 | All other inputs are in the 'Other inputs' sheet.
Calculations
1 | Quality standards and incentives are calculated, consistent with our draft decisions, in the "Calculations" sheet
2 | "The Calculations Chartbook" contains further analysis of smaller EDBs that are expected to have a lower frequency of major events.
Outputs
1 | The "Output" sheet uses Excel's data table facility to display the calculated results for all EDBs.
2 | The "Chart book" sheet contains tables used in our DPP4 draft reasons paper or determination.
Notes
1 | Annual quantities relate to years ending on 31 March.
2 | A lighter font is used for cells containing a formula linking to another sheet. A red font is applied to input cells.
3 | Wherever two horizontally adjacent cells contain numerical formulas which differ, a red border has been placed between the cells to indicate that the cell formulas are different.
4 | This model should only be used for its intended purpose.
Model suite
1 | Follow the link 'Model map – EDB DPP draft determination – 29 May 2024' on the Commission's EDB 2025-2030 default price-quality path determination web page
for a graphical depiction of interconnections between the models and data sources.

## Inputs from R
Inputs from R model
All input data is entered into this sheet.
Unplanned quality parameters - based on 10 year historical reference dataset (DYE 2014-2023)
This is raw output from R models. File dpp4_draft_decision_unplanned_parameters_normalised_unadjusted_for_caps.csv
R output name: | saidi_bound | saidi_target | saidi_collar | saidi_cap | saidi_sd | saifi_bound | saifi_target | saifi_collar | saifi_cap | saifi_sd
EDB | SAIDI boundary value | SAIDI average | SAIDI collar | SAIDI cap pre-adjustment | SAIDI standard deviation | SAIFI boundary value | SAIFI average | SAIFI collar | SAIFI cap pre-adjustment | SAIFI standard deviation
Alpine Energy | 8.77 | 90.1443 | 0 | 121.6919 | 15.7738 | 0.060423 | 0.76659 | 0 | 1.0193 | 0.12633
Aurora Energy | 6.5603 | 97.9808 | 0 | 122.0546 | 12.0369 | 0.084872 | 1.5453 | 0 | 1.873 | 0.16388
EA Networks | 5.7224 | 71.2988 | 0 | 90.842 | 9.7716 | 0.072888 | 1.0316 | 0 | 1.311 | 0.13966
Firstlight Network | 17.6725 | 188.3376 | 0 | 237.4661 | 24.5643 | 0.18016 | 2.5397 | 0 | 3.2346 | 0.34744
Electricity Invercargill | 4.865 | 17.0985 | 0 | 29.1534 | 6.0274 | 0.09811 | 0.42009 | 0 | 0.70601 | 0.14296
Horizon Energy | 12.9913 | 138.4455 | 0 | 183.0146 | 22.2846 | 0.092 | 1.5568 | 0 | 2.0216 | 0.23237
Nelson Electricity | 6.7935 | 5.8406 | 0 | 14.9044 | 4.5319 | 0.14078 | 0.11065 | 0 | 0.30368 | 0.096516
Network Tasman | 6.0837 | 72.2088 | 0 | 97.7256 | 12.7584 | 0.065437 | 0.77533 | 0 | 1.0349 | 0.12977
Orion NZ | 4.4076 | 48.704 | 0 | 59.8403 | 5.5681 | 0.036799 | 0.6344 | 0 | 0.76038 | 0.062993
OtagoNet | 11.8174 | 132.6225 | 0 | 173.7824 | 20.58 | 0.16449 | 1.8942 | 0 | 2.4935 | 0.29967
Powerco | 9.7826 | 166.1718 | 0 | 195.7168 | 14.7725 | 0.053381 | 1.8684 | 0 | 2.1191 | 0.12535
The Lines Company | 13.8486 | 179.8106 | 0 | 227.2591 | 23.7242 | 0.14683 | 2.7175 | 0 | 3.4333 | 0.35789
Top Energy | 29.0906 | 320.6453 | 0 | 404.8391 | 42.0969 | 0.19457 | 3.6781 | 0 | 4.5155 | 0.41869
Unison Networks | 4.5468 | 71.097 | 0 | 86.811 | 7.857 | 0.069154 | 1.5766 | 0 | 1.8737 | 0.14855
Vector Lines | 6.1083 | 120.3608 | 0 | 139.47 | 9.5546 | 0.045657 | 1.3436 | 0 | 1.527 | 0.091733
Wellington Electricity | 1.8068 | 29.9571 | 0 | 37.8414 | 3.9421 | 0.029188 | 0.44907 | 0 | 0.56482 | 0.057875
Planned quality parameters - based on 7 year historical reference dataset (DYE 2017-2023)
This is raw output from R models, File: dpp4_draft_decision_planned_parameters_unadjusted_for_caps.csv
R output name: | saidi_collar | saidi_target | saidi_cap | saidi_limit | saifi_collar | saifi_target | saifi_cap | saifi_limit
EDB | SAIDI collar | SAIDI average | SAIDI cap | SAIDI standard | SAIFI collar | SAIFI average | SAIFI cap | SAIFI standard
Alpine Energy | 0 | 72.5008 | 145.0015 | 725.0075 | 0 | 0.23951 | 0.47903 | 2.3951
Aurora Energy | 0 | 160.378 | 320.7559 | 1603.7796 | 0 | 0.78669 | 1.5734 | 7.8669
EA Networks | 0 | 117.8216 | 235.6433 | 1178.2163 | 0 | 0.39823 | 0.79647 | 3.9823
Firstlight Network | 0 | 90.8895 | 181.779 | 908.8952 | 0 | 0.54292 | 1.0858 | 5.4292
Electricity Invercargill | 0 | 14.8697 | 29.7395 | 148.6975 | 0 | 0.063807 | 0.12761 | 0.63807
Horizon Energy | 0 | 109.4675 | 218.935 | 1094.6752 | 0 | 0.64817 | 1.2963 | 6.4817
Nelson Electricity | 0 | 16.5724 | 33.1448 | 165.7239 | 0 | 0.06201 | 0.12402 | 0.6201
Network Tasman | 0 | 101.9646 | 203.9292 | 1019.6462 | 0 | 0.35051 | 0.70102 | 3.5051
Orion NZ | 0 | 21.5411 | 43.0823 | 215.4114 | 0 | 0.068659 | 0.13732 | 0.68659
OtagoNet | 0 | 194.5745 | 389.1491 | 1945.7454 | 0 | 0.87119 | 1.7424 | 8.7119
Powerco | 0 | 78.1166 | 156.2333 | 781.1663 | 0 | 0.34964 | 0.69928 | 3.4964
The Lines Company | 0 | 124.5949 | 249.1898 | 1245.9488 | 0 | 0.64145 | 1.2829 | 6.4145
Top Energy | 0 | 125.1839 | 250.3677 | 1251.8386 | 0 | 0.74615 | 1.4923 | 7.4615
Unison Networks | 0 | 78.5926 | 157.1853 | 785.9263 | 0 | 0.55476 | 1.1095 | 5.5476
Vector Lines | 0 | 82.5326 | 165.0653 | 825.3265 | 0 | 0.37109 | 0.74219 | 3.7109
Wellington Electricity | 0 | 9.535 | 19.0699 | 95.3496 | 0 | 0.069399 | 0.1388 | 0.69399

## Other Inputs
Inputs
All other input data (apart from the EDB at C5 in the "Output" sheet is entered into this sheet.
Inputs that are the same for all distributors
Constants
Minutes per hour |  | 60
Hours per day |  | 24
Days per year |  | 365
Commission-defined constants
Value of lost load |  | 35374
IRIS retention rate |  | 33.18%
SAIDI weighting to reflect quality standard incentives |  | 90%
SAIFI weighting to reflect quality standard incentives |  | 0%
Planned incentive rate - % of unplanned |  | 65%
Notified interruptions incentive rate - % of unplanned |  | 25%
Revenue at risk constraint |  | 2%
Extreme event standard―SAIDI |  | 120
Extreme event standard―customer minutes |  | 6000000
Unplanned standard deviation multiplier |  | 2
Years in regulatory period |  | 5
Unplanned SAIDI % increase/decrease cap (for target and limit) |  | 5%
Unplanned SAIFI % increase/decrease cap (for target and limit) |  | 5%
Planned buffer added to SAIDI average |  | 100%
Planned buffer added to SAIFI average |  | 100%
Planned SAIDI % increase/decrease cap (limit) |  | 10%
Planned SAIFI % increase/decrease cap (limit) |  | 10%
Inputs that are specific to individual distributors
Energy delivered (GWh)
This data is the total 'energy delivered to ICPs in the disclosure year' for all customers, from schedule 8(i) in ID Years end on 31 March
EDBs |  | Value | 2021 | 2022 | 2023
Alpine Energy |  |  | 800.5455 | 772.4013 | 812.1628
Aurora Energy |  |  | 1305.3753 | 1307.0362 | 1355.3381
EA Networks |  |  | 627.0342 | 554.2844 | 564.283
Firstlight Network |  |  | 284.2698 | 287.7109 | 286.3531
Electricity Invercargill |  |  | 250.2509 | 252.3435 | 249.8186
Horizon Energy |  |  | 544.6027 | 555.7719 | 536.6239
Nelson Electricity |  |  | 135.9097 | 137.655 | 135.4555
Network Tasman |  |  | 628.5261 | 652.002 | 653.664
Orion NZ |  |  | 3249.4936 | 3280.5187 | 3377.4135
OtagoNet |  |  | 443.7489 | 450.3409 | 462.5099
Powerco |  |  | 4879.8594 | 4994.4297 | 4960.4517
The Lines Company |  |  | 366.4014 | 368.2871 | 365.3802
Top Energy |  |  | 317.9501 | 329.8296 | 332.4412
Unison Networks |  |  | 1633.2226 | 1647.301 | 1678.9686
Vector Lines |  |  | 8209.931 | 8374.678 | 8462.235
Wellington Electricity |  |  | 2263.9819 | 2266.9787 | 2286.9192
ICPs
This data is the 'average no. of ICPs in the disclosure year' for all customers, from schedule 8(i) in ID Years end on 31 March
EDBs |  | Value | 2021 | 2022 | 2023
Alpine Energy |  |  | 33699.5 | 33269 | 33539
Aurora Energy |  |  | 92095.658 | 93287.4411 | 94323.3637
EA Networks |  |  | 20001.0833 | 20246.8301 | 20538
Firstlight Network |  |  | 25783 | 25775.0833 | 25871.75
Electricity Invercargill |  |  | 17419 | 17491 | 17562
Horizon Energy |  |  | 25416.3333 | 25080.709 | 25179.3333
Nelson Electricity |  |  | 9271 | 9285 | 9297
Network Tasman |  |  | 40596.5 | 41622 | 42224
Orion NZ |  |  | 209584 | 213669 | 218227
OtagoNet |  |  | 17842 | 18567 | 19361
Powerco |  |  | 348191 | 352563 | 356643
The Lines Company |  |  | 23841.4228 | 23999.0767 | 24015.6055
Top Energy |  |  | 32876.9167 | 33262.6923 | 33740
Unison Networks |  |  | 115724 | 116892.75 | 118448
Vector Lines |  |  | 583483 | 593440 | 603707
Wellington Electricity |  |  | 170188.25 | 171955 | 173512.25
Maximum allowable revenue for DPP4 period ($000 nominal)
This is the 'MAR (applicable X factor)' series from the outputs of Financial model – EDB DPP4 draft determination – 29 May 2024
|  | Value | 2026 | 2027 | 2028 | 2029 | 2030
Alpine Energy |  |  | 70249.4819 | 73445.8333 | 76787.6188 | 80281.4554 | 83934.2616
Aurora Energy |  |  | 154992.7389 | 158092.5937 | 161254.4455 | 164479.5344 | 167769.1251
EA Networks |  |  | 45800.9433 | 52089.4128 | 59241.2891 | 67375.1181 | 76625.7219
Electricity Invercargill |  |  | 16983.8007 | 19038.5009 | 21341.7787 | 23923.7071 | 26817.9972
Firstlight Network |  |  | 35732.4483 | 40310.4896 | 45475.0695 | 51301.3354 | 57874.0625
Horizon Energy |  |  | 34062.7858 | 36029.571 | 38109.9184 | 40310.3851 | 42637.9068
Nelson Electricity |  |  | 7045.0153 | 7703.3015 | 8423.098 | 9210.1523 | 10070.7489
Network Tasman |  |  | 36952.3547 | 41272.085 | 46096.7917 | 51485.5067 | 57504.1624
Orion NZ |  |  | 219480.2594 | 252972.947 | 291576.6187 | 336071.2108 | 387355.6775
OtagoNet |  |  | 33640.2245 | 39940.3657 | 47420.3974 | 56301.2895 | 66845.3949
Powerco |  |  | 486106.0212 | 495828.1416 | 505744.7045 | 515859.5986 | 526176.7905
The Lines Company |  |  | 48360.3271 | 52681.8059 | 57389.4521 | 62517.7736 | 68104.3618
Top Energy |  |  | 52961.703 | 61313.7635 | 70982.944 | 82176.9543 | 95136.26
Unison Networks |  |  | 136086.1561 | 157408.135 | 182070.8416 | 210597.701 | 243594.1488
Vector Lines |  |  | 579966.0311 | 641848.4066 | 710333.6316 | 786126.2301 | 870005.8989
Wellington Electricity |  |  | 118755.8974 | 134092.034 | 151408.6792 | 170961.5961 | 193039.5766
Maximum allowable revenue for Aurora - Indicative ($000 nominal)
This is the MAR from Aurora's CPP, Schedule 1.3 for 2026, and indicative MAR values for 2027-2030 from the outputs of Financial model – EDB DPP4 draft determination – 29 May 2024
|  |  | 2026 | 2027 | 2028 | 2029 | 2030
Aurora Energy |  |  | 90867 | 158092.5937 | 161254.4455 | 164479.5344 | 167769.1251
Circuit Length
This is from 2023 Information Disclosures, Section 9 (c) Total circuit length (for supply)
2023 Circuit length (km)
Electricity Invercargill | 665
Nelson Electricity | 296
DPP3 unplanned
EDB DPP determination 2020 (27 November 2019), Schedule 3.2, Table 3.2.1 (boundary values); Schedule 4, Table 4.1 (collar, target, cap)
Aurora CPP (31 March 2021), Schedule 3.2, table 3.2.1 (limit, boundary), Schedule 4m Table 4.1 and 4.2 (Collar, target, cap)
Also Final DPP3 model, Inouts from Stata model, Outputs or Chart book for all but Aurora (this will download)
EDB | SAIDI boundary value (Stata) | SAIDI target (DPP/CPP) | SAIDI Limit (DPP/CPP) | SAIFI boundary value (Stata) | SAIFI target (CPP/DPP) | SAIFI Limit (DPP/CPP)
Alpine Energy | 9.1745 | 91.8836 | 124.7078 | 0.067084 | 0.90693 | 1.197
Aurora Energy | 5.69 | 88.08 | 124.94 | 0.0737 | 1.57 | 2.071
EA Networks | 6.2509 | 71.6543 | 91.9755 | 0.072886 | 1.0065 | 1.2826
Firstlight Network | 13.0984 | 173.848 | 219.4603 | 0.1765 | 2.47 | 3.1525
Electricity Invercargill | 4.1289 | 15.3923 | 25.8552 | 0.080374 | 0.42733 | 0.69559
Horizon Energy | 14.6859 | 144.3524 | 194.5268 | 0.11697 | 1.8375 | 2.3904
Nelson Electricity | 8.6827 | 9.5334 | 19.5969 | 0.14298 | 0.19879 | 0.42773
Network Tasman | 7.2246 | 74.4923 | 101.0324 | 0.068837 | 0.90416 | 1.1956
Orion NZ | 7.5972 | 66.4659 | 84.7104 | 0.066785 | 0.83711 | 1.0336
OtagoNet | 11.8082 | 120.0213 | 160.3547 | 0.17759 | 1.794 | 2.4172
Powerco | 9.8185 | 151.9589 | 180.2532 | 0.062755 | 1.9991 | 2.2684
The Lines Company | 11.1731 | 143.0358 | 181.4778 | 0.15962 | 2.5578 | 3.2715
Top Energy | 27.923 | 302.1594 | 380.238 | 0.22836 | 4.1328 | 5.0732
Unison Networks | 4.4828 | 67.8146 | 82.3444 | 0.073527 | 1.5201 | 1.8152
Vector Lines | 4.825 | 89.2779 | 104.8298 | 0.037054 | 1.1803 | 1.3366
Wellington Electricity | 2.1567 | 31.2018 | 39.8079 | 0.031269 | 0.48396 | 0.61354
DPP3 planned
EDB DPP determination 2020 (27 November 2019), Schedule 3.1, Table 3.1.1 (limits); Table 4.2 (target, cap)
Aurora CPP (31 March 2021), Schedule 3.2, table 3.2.1 (limit, boundary), Schedule 4m Table 4.1 and 4.2 (Collar, target, cap)
Also Final DPP3 model, Inputs from Stata model, Outputs or Chart book for all but Aurora (this will download)
EDB | SAIDI target (DPP/CPP) | SAIDI cap (derived) | SAIDI Limit (DPP/CPP) | SAIFI target (CPP/DPP) | SAIFI cap (derived) | SAIFI Limit (DPP/CPP)
Alpine Energy | 54.9912 | 164.9737 | 824.8685 | 0.23287 | 0.6986 | 3.493
Aurora Energy | 72.16 | 195.9592 | 979.796 | 0.36923 | 1.1077 | 5.5385
EA Networks | 91.7388 | 275.2164 | 1376.082 | 0.32626 | 0.97878 | 4.8939
Firstlight Network | 86.0452 | 258.1355 | 1290.6775 | 0.4983 | 1.4949 | 7.4745
Electricity Invercargill | 7.6329 | 22.8987 | 114.4936 | 0.034556 | 0.10367 | 0.51834
Horizon Energy | 57.2422 | 171.7265 | 858.6325 | 0.36276 | 1.0883 | 5.4414
Nelson Electricity | 12.0074 | 36.0222 | 180.111 | 0.15775 | 0.47326 | 2.3663
Network Tasman | 75.2757 | 225.8271 | 1129.1355 | 0.32681 | 0.98043 | 4.9021
Orion NZ | 13.2269 | 39.6806 | 198.403 | 0.049871 | 0.14961 | 0.74806
OtagoNet | 140.9622 | 422.8866 | 2114.433 | 0.64141 | 1.9242 | 9.6212
Powerco | 51.4997 | 154.4991 | 772.4955 | 0.23409 | 0.70227 | 3.5113
The Lines Company | 88.7783 | 266.335 | 1331.675 | 0.58351 | 1.7505 | 8.7527
Top Energy | 127.0242 | 381.0726 | 1905.363 | 0.51684 | 1.5505 | 7.7526
Unison Networks | 41.7196 | 125.1589 | 625.7945 | 0.29766 | 0.89298 | 4.4649
Vector Lines | 39.0254 | 117.0761 | 585.3805 | 0.19189 | 0.57566 | 2.8783
Wellington Electricity | 4.6463 | 13.939 | 69.6951 | 0.036905 | 0.11072 | 0.55358
SAIDI incentives rates for DPP3 ($/SAIDI)
Planned incentive rate - % of unplanned |  |  | 50%
Notified incentive rate - % of Unplanned |  |  |  | 25%
Table 4.3 Incentive rates for the DPP regulatory period, in the DPP3 Determination
Schedule 4(5), Incentive rates for Aurora CPP
Determination
|  | Unplanned | Planned | Notified
Alpine Energy |  | 7879 | 3939.5 | 1969.75
Aurora Energy |  | 14279 | 7139.5 | 3569.75
EA Networks |  | 5394 | 2697 | 1348.5
Firstlight Network |  | 2797 | 1398.5 | 699.25
Electricity Invercargill |  | 2544 | 1272 | 636
Horizon Energy |  | 5397 | 2698.5 | 1349.25
Nelson Electricity |  | 1417 | 708.5 | 354.25
Network Tasman |  | 6260 | 3130 | 1565
Orion NZ |  | 31686 | 15843 | 7921.5
OtagoNet |  | 4339 | 2169.5 | 1084.75
Powerco |  | 47908 | 23954 | 11977
The Lines Company |  | 3827 | 1913.5 | 956.75
Top Energy |  | 3283 | 1641.5 | 820.75
Unison Networks |  | 16185 | 8092.5 | 4046.25
Vector Lines |  | 84519 | 42259.5 | 21129.75
Wellington Electricity |  | 23215 | 11607.5 | 5803.75

## Calculations
Calculations for the selected EDB | [7 empty] | Alpine Energy
This sheet calculates the quality standards that will apply for the DPP3 period
The calculations are for the distributor selected in the 'Output' sheet.
Inputs | [8 empty] | Notes
|  | Source | Value
Constants
Minutes per hour |  | Other inputs | 60
Hours per day |  | Other inputs | 24
Days per year |  | Other inputs | 365
Commission-defined constants
Value of lost load |  | Other inputs | 35374
IRIS retention rate |  | Other inputs | 33.18%
SAIDI weighting to reflect quality standard incentives |  | Other inputs | 90%
SAIFI weighting to reflect quality standard incentives |  | Other inputs | 0%
Planned incentive rate - % of unplanned |  | Other inputs | 65%
Notified interruptions incentive rate - % of unplanned |  | Other inputs | 25%
Revenue at risk constraint |  | Other inputs | 2%
Extreme event standard―SAIDI |  | Other inputs | 120
Extreme event standard―customer minutes |  | Other inputs | 6000000
Unplanned standard deviation multiplier |  | Other inputs | 2
Years in regulatory period |  | Other inputs | 5
Unplanned SAIDI % increase/decrease cap (for target and limit) |  | Other inputs | 5%
Unplanned SAIFI % increase/decrease cap (for target and limit) |  | Other inputs | 5%
Planned buffer added to SAIDI average |  | Other inputs | 100%
Planned buffer added to SAIFI average |  | Other inputs | 100%
Planned SAIDI % increase/decrease cap (limit) |  | Other inputs | 10%
Planned SAIFI % increase/decrease cap (limit) |  | Other inputs | 10%
EDB-specific inputs
|  |  |  | 2021 | 2022 | 2023
Energy delivered (GWh) |  | Other inputs |  | 800.5455 | 772.4013 | 812.1628 |  |  | GWh disclosures are used to estimate the amount of SAIDI incentives paid per MWh of electricity foregone
ICPs |  | Other inputs |  | 33699.5 | 33269 | 33539 |  |  | This is used to estimate a SAIDI incentive rate per customer
|  |  |  | 2026 | 2027 | 2028 | 2029 | 2030
MAR or net allowable revenue |  | Other inputs |  | 70249.4819 | 73445.8333 | 76787.6188 | 80281.4554 | 83934.2616
MAR or net allowable revenue |  | Other inputs |  | 70249.4819 | 73445.8333 | 76787.6188 | 80281.4554 | 83934.2616
MAR or net allowable revenue |  | Other inputs |  | 90867 | 158092.5937 | 161254.4455 | 164479.5344 | 167769.1251
Unplanned SAIDI incentives rates for DPP3 ($/SAIDI) |  | Other inputs | 7879
Planned SAIDI incentives rates for DPP3 ($/SAIDI) |  | Other inputs | 3939.5
Notified SAIDI incentives rates for DPP3 ($/SAIDI) |  | Other inputs | 1969.75
Unplanned reliability standards | [8 empty] | R inputs are unadjusted for caps, etc - which will be done in this Excel model below
Draft decision | SAIDI boundary value | Inputs from R | 8.77
Draft decision | SAIDI average | Inputs from R | 90.1443
Draft decision | SAIDI collar | Inputs from R | 0
Draft decision | SAIDI standard deviation | Inputs from R | 15.7738
Draft decision | SAIFI boundary value | Inputs from R | 0.060423
Draft decision | SAIFI average | Inputs from R | 0.76659
Draft decision | SAIFI collar | Inputs from R | 0
Draft decision | SAIFI standard deviation | Inputs from R | 0.12633
DPP3 unplanned | SAIDI target (DPP/CPP) | Other inputs | 91.8836
DPP3 unplanned | SAIFI target (CPP/DPP) | Other inputs | 0.90693
DPP3 unplanned | SAIDI Limit (DPP/CPP) | Other inputs | 124.7078
DPP3 unplanned | SAIFI Limit (DPP/CPP) | Other inputs | 1.197
Planned reliability standards | [8 empty] | R inputs are unadjusted for caps, etc - which will be done in this Excel model below
Draft decision | SAIDI collar | Inputs from R | 0
Draft decision | SAIDI average | Inputs from R | 72.5008
Draft decision | SAIDI cap | Inputs from R | 145.0015 | [5 empty] | Note, this is not used in the model. Does the calculation below.
Draft decision | SAIFI average | Inputs from R | 0.23951
Draft decision | SAIFI cap | Inputs from R | 0.47903 | [5 empty] | Note, this is not used in the model. Does the calculation below.
DPP3 planned | SAIDI target (DPP/CPP) | Other inputs | 54.9912
DPP3 planned | SAIFI target (CPP/DPP) | Other inputs | 0.23287
DPP3 planned | SAIDI cap (derived) | Other inputs | 164.9737
DPP3 planned | SAIFI cap (derived) | Other inputs | 0.6986
Calculations |  | Units | Result
Number of minutes in a year |  | minutes | 525600
Unplanned reliability standards | [8 empty] | Calculates the unplanned reliability standard:
SAIDI average |  | minutes | 90.1443 | [5 empty] | Normalised historical average calculated in R
SAIDI buffer |  | minutes | 31.5476 | [5 empty] | plus a buffer of 2x the standard deviation
SAIDI unadjusted cap |  | minutes | 121.6919 | [5 empty] | equals SAIDI unadjusted cap
Unplanned SAIDI percent increase in DPP4 vs DPP3 |  | percent | -2.418% | [5 empty] | Calculate percentage increase between regulatory periods
Unplanned SAIDI scaling adjustment |  | percent | 0% | [5 empty] | make scaling adjustment of +/- 5% cap on interperiod movement
Unplanned Adjusted SAIDI cap |  | minutes | 121.6919 | [5 empty] | This adjusts the SAIDI unadjusted cap of the +/- 5% is reached
Calculates the unplanned reliability standard:
SAIFI average |  | frequency | 0.76659 | [5 empty] | Normalised historical average calculated in R
SAIFI buffer |  | frequency | 0.25267 | [5 empty] | plus a buffer of 2x the standard deviation
SAIFI unadjusted cap |  | frequency | 1.0193 | [5 empty] | equals SAIFI unadjusted cap
Unplanned SAIFI percent increase in DPP4 vs DPP3 |  | percent | -14.85% | [5 empty] | Calculate percentage increase between regulatory periods
Unplanned SAIFI scaling adjustment |  | percent | 11.57% | [5 empty] | make scaling adjustment to +/- 5% cap on interperiod movement
Unplanned Adjusted SAIFI cap |  | frequency | 1.1372 | [5 empty] | This adjusts the SAIFI unadjusted cap if the +/- 5% is reached
Planned reliability standards | [8 empty] | Calculates the planned reliability standard for SAIDI:
SAIDI average |  | minutes | 72.5008 | [5 empty] | Historical average calculated in R
SAIDI buffer |  | minutes | 72.5008 | [5 empty] | Planned buffer added to SAIDI average set at 100%
SAIDI unadjusted cap |  | minutes | 145.0015 | [5 empty] | Calculates the unadjusted cap for a year
Planned SAIDI percent increase in DPP4 vs DPP3 |  | percent | -12.11% | [5 empty] | Calculate percentage increase between regulatory periods
Planned SAIDI scaling adjustment |  | percent | 2.396% | [5 empty] | Make scaling adjustment necessary to reflect the +/-10% cap on movement from current standard
Planned Adjusted SAIDI cap |  | minutes | 148.4763 | [5 empty] | This adjusts the SAIDI unadjusted cap if the +/- 10% is reached
Planned reliability standard―SAIDI (5-year regulatory period limit) |  | minutes | 742.3817 | [5 empty] | Planned SAIDI standards are set for the five-year regulatory period
Calculates the planned reliability standard for SAIFI:
SAIFI average |  | frequency | 0.23951 | [5 empty] | Historical average calculated in R
SAIFI buffer |  | frequency | 0.23951 | [5 empty] | Planned buffer added to SAIDI average set at 100%
SAIFI unadjusted cap |  | frequency | 0.47903 | [5 empty] | Calculates the unadjusted cap for a year
Planned SAIFI percent increase in DPP4 vs DPP3 |  | percent | -31.43% | [5 empty] | Calculate percentage increase between regulatory periods
Planned SAIFI scaling adjustment |  | percent | 31.25% | [5 empty] | Make scaling adjustment necessary to reflect the +/-10% cap on movement from the current standard
Planned Adjusted SAIFI cap |  | frequency | 0.62874 | [5 empty] | This adjusts the SAIFI unadjusted cap if the +/- 10% is reached
Planned reliability standard―SAIFI (5-year regulatory period limit) |  | frequency | 3.1437 | [5 empty] | Planned SAIFI standards are set for the five-year regulatory period
Extreme event standards
Extreme event standard |  | SAIDI minutes | 120 | [5 empty] | The extreme event standard is set at 120 SAIDI minutes or 6,000,000 customer minutes (whichever is lower)
Extreme event standard―approx SAIDI equivalent |  | SAIDI minutes | 120 | [5 empty] | If 6,000,000/ICPs at end <120 mins, then take 120mins, or else use 6,000,000/ICPs
SAIDI Incentive Rate – DPP3
Average ICPs 2021-2023 |  | ICPs | 33502.5 | [5 empty] | This is the three-year average of ICPs to calculate the incentive rate per customer
Average GWh 2021-2023 |  | GWh / year | 795.0366 | [5 empty] | This is the three-year average of electricity volumes to calculate the implied VoLL
Unplanned Incentive Rate |  | $ / minute | 7879 | [5 empty] | The SAIDI incentive rate set for DPP3
Incentive Rate per customer |  | $ / minute / ICP | 0.23518 | [5 empty] | SAIDI incentive rate per customer in DPP3
Implied VoLL |  | $ / MWh | 5208.8201 | [5 empty] | The estimated amount of SAIDI incentives paid per MWh of electricity foregone
Planned incentive rate |  | $ / minute | 3939.5 | [5 empty] | The SAIDI incentive rate set for DPP3 for planned, weighted as 50% of unplanned
Notified incentive rate |  | $ / minute | 1969.75 | [5 empty] | The SAIDI incentive rate set for DPP3 for notified, weighted as 25% of unplanned
SAIDI Incentive Rate – DPP4
Multiplier |  | 1000 * years / minute | 0.0019026 | [5 empty] | This multiplier is used to calculate the incentive rate
Average ICPs 2021-2023 |  | ICPs | 33502.5 | [5 empty] | This is the three-year average of ICPs to calculate the incentive rate per customer
Average GWh 2021-2023 |  | GWh / year | 795.0366 | [5 empty] | The incentive rate is calculated using the three-year average of energy delivered by the network
Unplanned incentive rate |  | $ / minute | 15978.4558 | [5 empty] | The SAIDI incentive rate is a function of VoLL, and measures the value of losses from each SAIDI minute
Unplanned incentive rate per customer |  | $ / minute / ICP | 0.47693 | [5 empty] | SAIDI incentive rate per customer for DPP4
Planned incentive rate |  | $ / minute | 10385.9963 | [5 empty] | The incentive rate for planned interruptions in DPP4 is set at 65% of unplanned interruptions
Notified incentive rate |  | $ / minute | 3994.614 | [5 empty] | The incentive rate for planned interruptions in DPP4 is set at 25% of unplanned interruptions
Interruption penalties and rewards
Planned
Planned SAIDI percent increase in DPP4 vs DPP3 |  | percent | 31.84% | [5 empty] | This calculates the difference in reliability targets (average reliability) between reference periods, after normalisation
Planned SAIDI scaling adjustment |  | percent | [6 empty] | There is no cap on planned targets - this is a placeholder only
Planned SAIDI target |  | minutes | 72.5008 | [5 empty] | This calculates the SAIDI target which equals the average
Planned SAIDI collar |  | minutes | 0 | [5 empty] | This picks up the SAIDI collar which is set at 0
Planned Adjusted SAIDI cap |  | minutes | 148.4763 | [5 empty] | This picks up the adjusted SAIDI cap calculated above
Unplanned
Unplanned SAIDI percent increase in DPP4 vs DPP3 |  | percent | -1.893% | [5 empty] | This calculates the difference in reliability targets (average reliability) between reference periods, after normalisation
Unplanned SAIDI scaling adjustment |  | percent | 0% | [5 empty] | This calculates the adjustment necessary to reflect the 5% cap on increases we'll allow in SAIDI
Unplanned SAIDI target |  | minutes | 90.1443 | [5 empty] | This adjusts the SAIDI target if the +/- 5% cap is reached
Unplanned SAIDI collar |  | minutes | 0 | [5 empty] | This adjusts the SAIDI collar if the +/- 5% cap is reached
Unplanned SAIDI cap |  | minutes | 121.6919 | [5 empty] | This adjusts the SAIDI cap if the +/- 5% cap is reached. Calculated above.
Unplanned SAIFI percent increase in DPP4 vs DPP3 |  | percent | -15.48% | [5 empty] | These calculations repeat those from above for SAIFI. Not used since SAIFI is not part of QIS
Unplanned SAIFI scaling adjustment |  | percent | 12.39% | [5 empty] | These calculations repeat those from above for SAIFI
Unplanned SAIFI target |  | minutes | 0.86159 | [5 empty] | These calculations repeat those from above for SAIFI
Unplanned SAIFI collar |  | minutes | 0 | [5 empty] | These calculations repeat those from above for SAIFI
Unplanned SAIFI cap |  | minutes | 1.1372 | [5 empty] | These calculations repeat those from above for SAIFI
Revenue loss/gain
Average MAR or net allowable revenue |  | $ nominal | 76939730.2107 | [5 empty] | This calculates the average annual MAR over the DPP3 period
Unplanned: Maximum revenue loss |  | percent of MAR | 0.6552% | [5 empty] | This calculates the maximum loss for unplanned disruptions as a proportion of the MAR
Unplanned: Maximum revenue gain |  | percent of MAR | 1.872% | [5 empty] | This calculates the maximum gain for unplanned disruptions as a proportion of the MAR
Planned: Maximum revenue loss |  | percent of MAR | 1.026% | [5 empty] | This calculates the maximum loss for planned disruptions as a proportion of the MAR
Planned: Maximum revenue gain |  | percent of MAR | 0.9787% | [5 empty] | This calculates the maximum gain for planned disruptions as a proportion of the MAR
Total: Maximum revenue loss |  | percent of MAR | 1.681% | [5 empty] | This calculates the maximum loss for all disruptions as a proportion of the MAR (with cap applied)
Total: Maximum revenue gain |  | percent of MAR | 2% | [5 empty] | This calculates the maximum gain for all disruptions as a proportion of the MAR (with cap applied)
Implied value of lost load |  | $/MWh | 10563.3839 | [5 empty] | The estimated amount of SAIDI incentives paid per MWh of electricity foregone
Outputs |  | Output | Value | [5 empty] | These summaried outputs from the calculations appear in the Data Table in the "Output" tab
Planned reliability standards
Planned SAIDI target |  | minutes | 72.5008
Planned SAIDI collar |  | minutes | 0
Planned Adjusted SAIDI cap |  | minutes | 148.4763
Planned reliability standard―SAIDI (5-year regulatory period limit) - minutes |  |  | 742.3817
SAIFI average |  | frequency | 0.23951
Planned Adjusted SAIFI cap |  | frequency | 0.62874
Planned reliability standard―SAIFI (5-year regulatory period limit) - frequency |  | frequency | 3.1437
Planned SAIDI percent increase in DPP4 vs DPP3 |  |  | -12.11%
Planned SAIDI scaling adjustment |  |  | 2.396%
Planned SAIFI percent increase in DPP4 vs DPP3 |  |  | -31.43%
Planned SAIFI scaling adjustment |  |  | 31.25%
Extreme event standard
Extreme event standard - SAIDI minutes |  |  | 120
Extreme event standard―approx SAIDI equivalent - SAIDI minutes |  |  | 120
Unplanned reliability standards
SAIDI target - minutes |  |  | 90.1443
SAIDI collar - minutes |  |  | 0
SAIDI cap - minutes |  |  | 121.6919
SAIFI target - minutes |  |  | 0.86159
SAIFI collar - minutes |  |  | 0
SAIFI cap - minutes |  |  | 1.1372
Unplanned SAIDI percent increase in DPP4 vs DPP3 |  |  | -1.893%
Unplanned SAIDI scaling adjustment |  |  | 0%
Unplanned SAIFI percent increase in DPP4 vs DPP3 |  |  | -15.48%
Unplanned SAIFI scaling adjustment |  |  | 12.39%
Quality incentives
Unplanned Incentive Rate - $ / minute |  | DPP3 | 7879
Planned incentive rate - $ / minute |  | DPP3 | 3939.5
Notified incentive rate - $ / minute |  | DPP3 | 1969.75
Incentive Rate per customer - $ / minute / ICP |  | DPP3 | 0.23518
Implied VoLL - $ / MWh |  | DPP3 | 5208.8201
Unplanned incentive rate - $ / minute |  | DPP4 | 15978.4558
Planned incentive rate - $ / minute |  | DPP4 | 10385.9963
Notified incentive rate - $ / minute |  | DPP4 | 3994.614
Unplanned incentive rate per customer - $ / minute / ICP |  | DPP4 | 0.47693
Implied value of lost load |  | DPP4 | 10563.3839
Unplanned: Maximum revenue loss |  | DPP4 | 0.6552%
Unplanned: Maximum revenue gain |  | DPP4 | 1.872%
Planned: Maximum revenue loss |  | DPP4 | 1.026%
Planned: Maximum revenue gain |  | DPP4 | 0.9787%
Total: Maximum revenue loss |  | DPP4 | 1.681%
Total: Maximum revenue gain |  | DPP4 | 2%

## Calculations-Chartbook
Calculations Chartbook - frequency of major events
Inputs
Circuit Length
| Distributor | 2023 Circuit length (km)
| Electricity Invercargill | 665
| Nelson Electricity | 296
Calculations
Reduced frequency of major events
| Distributor | 2023 Circuit length (km) | Major events (compared to 23) | ‘Major half hours’ (compared to 1104)
| Electricity Invercargill | 665 | 15.295 | 734.16
| Nelson Electricity | 296 | 6.808 | 326.784

## Output
Outputs
This sheet uses Excel's data table facility to display the quality standards for each EDB.
EDB |  | Scenario
Active EDB |  | Alpine Energy
| Active EDB outputs | Alpine Energy | Aurora Energy | EA Networks | Firstlight Network | Electricity Invercargill | Horizon Energy | Nelson Electricity | Network Tasman | Orion NZ | OtagoNet | Powerco | The Lines Company | Top Energy | Unison Networks | Vector Lines | Wellington Electricity
Planned reliability standards
Planned SAIDI target | 72.5008 | 72.5008 | 160.378 | 117.8216 | 90.8895 | 14.8697 | 109.4675 | 16.5724 | 101.9646 | 21.5411 | 194.5745 | 78.1166 | 124.5949 | 125.1839 | 78.5926 | 82.5326 | 9.535
Planned SAIDI collar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Adjusted SAIDI cap | 148.4763 | 148.4763 | 215.5551 | 247.6948 | 232.3219 | 25.1886 | 188.8991 | 33.1448 | 203.9292 | 43.0823 | 389.1491 | 156.2333 | 249.1898 | 342.9653 | 137.6748 | 128.7837 | 15.3329
Planned reliability standard―SAIDI (5-year regulatory period limit) - minutes | 742.3817 | 742.3817 | 1077.7756 | 1238.4738 | 1161.6097 | 125.943 | 944.4957 | 165.7239 | 1019.6462 | 215.4114 | 1945.7454 | 781.1663 | 1245.9488 | 1714.8267 | 688.374 | 643.9186 | 76.6647
SAIFI average | 0.23951 | 0.23951 | 0.78669 | 0.39823 | 0.54292 | 0.063807 | 0.64817 | 0.06201 | 0.35051 | 0.068659 | 0.87119 | 0.34964 | 0.64145 | 0.74615 | 0.55476 | 0.37109 | 0.069399
Planned Adjusted SAIFI cap | 0.62874 | 0.62874 | 1.2185 | 0.8809 | 1.3454 | 0.11403 | 1.1971 | 0.42593 | 0.88239 | 0.13732 | 1.7424 | 0.69928 | 1.5755 | 1.4923 | 0.98227 | 0.63323 | 0.12179
Planned reliability standard―SAIFI (5-year regulatory period limit) - frequency | 3.1437 | 3.1437 | 6.0923 | 4.4045 | 6.7271 | 0.57017 | 5.9856 | 2.1297 | 4.4119 | 0.68659 | 8.7119 | 3.4964 | 7.8774 | 7.4615 | 4.9114 | 3.1661 | 0.60894
Planned SAIDI percent increase in DPP4 vs DPP3 | -12.11% | -12.11% | 63.69% | -14.38% | -29.58% | 29.87% | 27.49% | -7.988% | -9.697% | 8.573% | -7.978% | 1.122% | -6.437% | -34.3% | 25.59% | 40.99% | 36.81%
Planned SAIDI scaling adjustment | 2.396% | 2.396% | -32.8% | 5.114% | 27.8% | -15.3% | -13.72% | 0% | 0% | 0% | 0% | 0% | 0% | 36.98% | -12.41% | -21.98% | -19.6%
Planned SAIFI percent increase in DPP4 vs DPP3 | -31.43% | -31.43% | 42.04% | -18.63% | -27.36% | 23.1% | 19.12% | -73.79% | -28.5% | -8.217% | -9.451% | -0.4258% | -26.71% | -3.755% | 24.25% | 28.93% | 25.36%
Planned SAIFI scaling adjustment | 31.25% | 31.25% | -22.56% | 10.6% | 23.9% | -10.64% | -7.653% | 243.4% | 25.87% | 0% | 0% | 0% | 22.81% | 0% | -11.47% | -14.68% | -12.26%
Unplanned reliability standards
SAIDI target - minutes | 90.1443 | 90.1443 | 92.484 | 71.2988 | 182.5404 | 16.1619 | 138.4455 | 9.0567 | 72.2088 | 63.1426 | 126.0223 | 159.5568 | 150.1876 | 317.2673 | 71.097 | 93.7418 | 29.9571
SAIDI collar - minutes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SAIDI cap - minutes | 121.6919 | 121.6919 | 122.0546 | 90.842 | 230.4333 | 27.1479 | 184.8005 | 18.6171 | 97.7256 | 80.4749 | 168.3724 | 189.2659 | 190.5517 | 399.2499 | 86.4616 | 110.0713 | 37.8414
SAIFI target - minutes | 0.86159 | 0.86159 | 1.5453 | 1.0316 | 2.5397 | 0.42009 | 1.7456 | 0.18885 | 0.85895 | 0.79526 | 1.8837 | 1.8991 | 2.6857 | 3.9262 | 1.5766 | 1.2393 | 0.45976
SAIFI collar - minutes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SAIFI cap - minutes | 1.1372 | 1.1372 | 1.9675 | 1.311 | 3.2346 | 0.70601 | 2.2709 | 0.40635 | 1.1358 | 0.98188 | 2.4935 | 2.155 | 3.4333 | 4.8196 | 1.8737 | 1.4034 | 0.58286
Unplanned SAIDI percent increase in DPP4 vs DPP3 | -1.893% | -1.893% | 11.24% | -0.4962% | 8.335% | 11.08% | -4.092% | -38.73% | -3.065% | -26.72% | 10.5% | 9.353% | 25.71% | 6.118% | 4.84% | 34.82% | -3.989%
Unplanned SAIDI scaling adjustment | 0% | 0% | -5.61% | 0% | -3.078% | -5.478% | 0% | 55.06% | 0% | 29.65% | -4.977% | -3.981% | -16.47% | -1.053% | 0% | -22.12% | 0%
Unplanned SAIFI percent increase in DPP4 vs DPP3 | -15.48% | -15.48% | -1.575% | 2.494% | 2.819% | -1.694% | -15.28% | -44.34% | -14.25% | -24.22% | 5.583% | -6.536% | 6.243% | -11% | 3.716% | 13.84% | -7.21%
Unplanned SAIFI scaling adjustment | 12.39% | 12.39% | 0% | 0% | 0% | 0% | 12.13% | 70.68% | 10.79% | 25.36% | -0.5518% | 1.643% | -1.17% | 6.745% | 0% | -7.762% | 2.381%
Extreme event standard
Extreme event standard―approx SAIDI equivalent - SAIDI minutes | 120 | 120 | 63.611 | 120 | 120 | 120 | 120 | 120 | 120 | 27.4943 | 120 | 16.8235 | 120 | 120 | 50.6551 | 9.9386 | 34.5797
SAIDI Incentive Rate – DPP3
Unplanned Incentive Rate - $ / minute | 7879 | 7879 | 14279 | 5394 | 2797 | 2544 | 5397 | 1417 | 6260 | 31686 | 4339 | 47908 | 3827 | 3283 | 16185 | 84519 | 23215
Planned incentive rate - $ / minute | 3939.5 | 3939.5 | 7139.5 | 2697 | 1398.5 | 1272 | 2698.5 | 708.5 | 3130 | 15843 | 2169.5 | 23954 | 1913.5 | 1641.5 | 8092.5 | 42259.5 | 11607.5
Notified Incentive rate - $ / minute | 1969.75 | 1969.75 | 3569.75 | 1348.5 | 699.25 | 636 | 1349.25 | 354.25 | 1565 | 7921.5 | 1084.75 | 11977 | 956.75 | 820.75 | 4046.25 | 21129.75 | 5803.75
Incentive Rate per customer - $ / minute / ICP | 0.23518 | 0.23518 | 0.15315 | 0.26621 | 0.10837 | 0.14545 | 0.21395 | 0.15262 | 0.15091 | 0.14819 | 0.23341 | 0.13592 | 0.15978 | 0.098609 | 0.13831 | 0.1424 | 0.13506
Implied VoLL - $ / MWh | 5208.8201 | 5208.8201 | 5674.5334 | 4872.3943 | 5138.2217 | 5331.3527 | 5198.5325 | 5462.6293 | 5103.3028 | 5042.933 | 5043.2971 | 5092.1911 | 5485.4881 | 5281.0897 | 5145.7905 | 5320.8124 | 5369.0316
SAIDI Incentive Rate – DPP4
Unplanned incentive rate - $ / minute | 15978.4558 | 15978.4558 | 26580.9622 | 11694.2287 | 5750.1966 | 5040.606 | 10966.6686 | 2740.1301 | 12957.6444 | 66372.363 | 9088.206 | 99381.6981 | 7369.6396 | 6566.7487 | 33224.8988 | 167795.1726 | 45674.7091
Planned incentive rate - $ / minute | 10385.9963 | 10385.9963 | 17277.6254 | 7601.2486 | 3737.6278 | 3276.3939 | 7128.3346 | 1781.0846 | 8422.4688 | 43142.036 | 5907.3339 | 64598.1038 | 4790.2657 | 4268.3867 | 21596.1842 | 109066.8622 | 29688.5609
Notified Incentive rate - $ / minute | 3994.614 | 3994.614 | 6645.2405 | 2923.5572 | 1437.5491 | 1260.1515 | 2741.6671 | 685.0325 | 3239.4111 | 16593.0908 | 2272.0515 | 24845.4245 | 1842.4099 | 1641.6872 | 8306.2247 | 41948.7931 | 11418.6773
Unplanned incentive rate per customer - $ / minute / ICP | 0.47693 | 0.47693 | 0.28509 | 0.57715 | 0.22279 | 0.28819 | 0.43475 | 0.29513 | 0.31238 | 0.3104 | 0.48888 | 0.28196 | 0.30768 | 0.19724 | 0.28392 | 0.2827 | 0.26573
Implied value of lost load | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839 | 10563.3839
Interruption penalties and rewards
Unplanned: Maximum revenue loss | 0.6552% | 0.6552% | 0.5293% | 0.3795% | 0.5969% | 0.2561% | 1.33% | 0.3085% | 0.7086% | 0.3867% | 0.7882% | 0.5836% | 0.5146% | 0.7424% | 0.2745% | 0.3818% | 0.2344%
Unplanned: Maximum revenue gain | 1.872% | 1.872% | 1.656% | 1.384% | 2.275% | 0.3768% | 3.971% | 0.2923% | 2.005% | 1.409% | 2.346% | 3.134% | 1.915% | 2.873% | 1.27% | 2.192% | 0.8905%
Planned: Maximum revenue loss | 1.026% | 1.026% | 0.642% | 1.639% | 1.146% | 0.1564% | 1.481% | 0.3476% | 1.84% | 0.3124% | 2.354% | 0.9974% | 1.032% | 1.282% | 0.6862% | 0.7029% | 0.112%
Planned: Maximum revenue gain | 0.9787% | 0.9787% | 1.866% | 1.487% | 0.7363% | 0.2253% | 2.041% | 0.3476% | 1.84% | 0.3124% | 2.354% | 0.9974% | 1.032% | 0.7369% | 0.9128% | 1.254% | 0.1842%
Total: Maximum revenue loss | 1.681% | 1.681% | 1.171% | 2% | 1.743% | 0.4125% | 2% | 0.6562% | 2% | 0.6991% | 2% | 1.581% | 1.547% | 2% | 0.9607% | 1.085% | 0.3464%
Total: Maximum revenue gain | 2% | 2% | 2% | 2% | 2% | 0.6021% | 2% | 0.6399% | 2% | 1.721% | 2% | 2% | 2% | 2% | 2% | 2% | 1.075%
Inputs from R model |  | Alpine Energy | Aurora Energy | EA Networks | Firstlight Network | Electricity Invercargill | Horizon Energy | Nelson Electricity | Network Tasman | Orion NZ | OtagoNet | Powerco | The Lines Company | Top Energy | Unison Networks | Vector Lines | Wellington Electricity
Unplanned quality parameters - based on 10 year historical reference dataset (DYE 2014-2023)
SAIDI boundary value |  | 8.77 | 6.5603 | 5.7224 | 17.6725 | 4.865 | 12.9913 | 6.7935 | 6.0837 | 4.4076 | 11.8174 | 9.7826 | 13.8486 | 29.0906 | 4.5468 | 6.1083 | 1.8068
SAIDI average |  | 90.1443 | 97.9808 | 71.2988 | 188.3376 | 17.0985 | 138.4455 | 5.8406 | 72.2088 | 48.704 | 132.6225 | 166.1718 | 179.8106 | 320.6453 | 71.097 | 120.3608 | 29.9571
SAIDI collar |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SAIDI cap pre-adjustment |  | 121.6919 | 122.0546 | 90.842 | 237.4661 | 29.1534 | 183.0146 | 14.9044 | 97.7256 | 59.8403 | 173.7824 | 195.7168 | 227.2591 | 404.8391 | 86.811 | 139.47 | 37.8414
SAIDI standard deviation |  | 15.7738 | 12.0369 | 9.7716 | 24.5643 | 6.0274 | 22.2846 | 4.5319 | 12.7584 | 5.5681 | 20.58 | 14.7725 | 23.7242 | 42.0969 | 7.857 | 9.5546 | 3.9421
SAIFI boundary value |  | 0.060423 | 0.084872 | 0.072888 | 0.18016 | 0.09811 | 0.092 | 0.14078 | 0.065437 | 0.036799 | 0.16449 | 0.053381 | 0.14683 | 0.19457 | 0.069154 | 0.045657 | 0.029188
SAIFI average |  | 0.76659 | 1.5453 | 1.0316 | 2.5397 | 0.42009 | 1.5568 | 0.11065 | 0.77533 | 0.6344 | 1.8942 | 1.8684 | 2.7175 | 3.6781 | 1.5766 | 1.3436 | 0.44907
SAIFI collar |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SAIFI cap pre-adjustment |  | 1.0193 | 1.873 | 1.311 | 3.2346 | 0.70601 | 2.0216 | 0.30368 | 1.0349 | 0.76038 | 2.4935 | 2.1191 | 3.4333 | 4.5155 | 1.8737 | 1.527 | 0.56482
SAIFI standard deviation |  | 0.12633 | 0.16388 | 0.13966 | 0.34744 | 0.14296 | 0.23237 | 0.096516 | 0.12977 | 0.062993 | 0.29967 | 0.12535 | 0.35789 | 0.41869 | 0.14855 | 0.091733 | 0.057875
Planned quality parameters - based on 7 year historical reference dataset (DYE 2017-2023)
SAIDI collar |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SAIDI average |  | 72.5008 | 160.378 | 117.8216 | 90.8895 | 14.8697 | 109.4675 | 16.5724 | 101.9646 | 21.5411 | 194.5745 | 78.1166 | 124.5949 | 125.1839 | 78.5926 | 82.5326 | 9.535
SAIDI cap |  | 145.0015 | 320.7559 | 235.6433 | 181.779 | 29.7395 | 218.935 | 33.1448 | 203.9292 | 43.0823 | 389.1491 | 156.2333 | 249.1898 | 250.3677 | 157.1853 | 165.0653 | 19.0699
SAIDI standard |  | 725.0075 | 1603.7796 | 1178.2163 | 908.8952 | 148.6975 | 1094.6752 | 165.7239 | 1019.6462 | 215.4114 | 1945.7454 | 781.1663 | 1245.9488 | 1251.8386 | 785.9263 | 825.3265 | 95.3496
SAIFI collar |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SAIFI average |  | 0.23951 | 0.78669 | 0.39823 | 0.54292 | 0.063807 | 0.64817 | 0.06201 | 0.35051 | 0.068659 | 0.87119 | 0.34964 | 0.64145 | 0.74615 | 0.55476 | 0.37109 | 0.069399
SAIFI cap |  | 0.47903 | 1.5734 | 0.79647 | 1.0858 | 0.12761 | 1.2963 | 0.12402 | 0.70102 | 0.13732 | 1.7424 | 0.69928 | 1.2829 | 1.4923 | 1.1095 | 0.74219 | 0.1388
SAIFI standard |  | 2.3951 | 7.8669 | 3.9823 | 5.4292 | 0.63807 | 6.4817 | 0.6201 | 3.5051 | 0.68659 | 8.7119 | 3.4964 | 6.4145 | 7.4615 | 5.5476 | 3.7109 | 0.69399

## Chart book
Outputs Chart book
Tables for Draft Reasons paper
Chapter 3
Note informs Table 3.2 | Quality standards for DPP4 | [6 empty] | Tables 3.2 and E1 | Quality standards for DPP4
|  | Unplanned SAIDI | Unplanned SAIFI | Planned SAIDI | Planned SAIFI | Extreme outage SAIDI |  |  |  | Unplanned SAIDI | Unplanned SAIFI | Planned SAIDI | Planned SAIFI | Extreme outage
| Distributor | (1-year) | (1-year) | (5-year) | (5-year) |  |  |  | Distributor | (1-year) | (1-year) | (5-year) | (5-year) | (per event)
| Alpine Energy | 121.6919 | 1.1372 | 742.3817 | 3.1437 | 120 |  |  | Alpine Energy | 121.6919 | 1.1372 | 742.3817 | 3.1437 | 120 SAIDI
| Aurora Energy | 122.0546 | 1.9675 | 1077.7756 | 6.0923 | 63.611 |  |  | Aurora Energy | 122.0546 | 1.9675 | 1077.7756 | 6.0923 | 6m CIM
| EA Networks | 90.842 | 1.311 | 1238.4738 | 4.4045 | 120 |  |  | EA Networks | 90.842 | 1.311 | 1238.4738 | 4.4045 | 120 SAIDI
| Firstlight Network | 230.4333 | 3.2346 | 1161.6097 | 6.7271 | 120 |  |  | Firstlight Network | 230.4333 | 3.2346 | 1161.6097 | 6.7271 | 120 SAIDI
| Electricity Invercargill | 27.1479 | 0.70601 | 125.943 | 0.57017 | 120 |  |  | Electricity Invercargill | 27.1479 | 0.70601 | 125.943 | 0.57017 | 120 SAIDI
| Horizon Energy | 184.8005 | 2.2709 | 944.4957 | 5.9856 | 120 |  |  | Horizon Energy | 184.8005 | 2.2709 | 944.4957 | 5.9856 | 120 SAIDI
| Nelson Electricity | 18.6171 | 0.40635 | 165.7239 | 2.1297 | 120 |  |  | Nelson Electricity | 18.6171 | 0.40635 | 165.7239 | 2.1297 | 120 SAIDI
| Network Tasman | 97.7256 | 1.1358 | 1019.6462 | 4.4119 | 120 |  |  | Network Tasman | 97.7256 | 1.1358 | 1019.6462 | 4.4119 | 120 SAIDI
| Orion NZ | 80.4749 | 0.98188 | 215.4114 | 0.68659 | 27.4943 |  |  | Orion NZ | 80.4749 | 0.98188 | 215.4114 | 0.68659 | 6m CIM
| OtagoNet | 168.3724 | 2.4935 | 1945.7454 | 8.7119 | 120 |  |  | OtagoNet | 168.3724 | 2.4935 | 1945.7454 | 8.7119 | 120 SAIDI
| Powerco | 189.2659 | 2.155 | 781.1663 | 3.4964 | 16.8235 |  |  | Powerco | 189.2659 | 2.155 | 781.1663 | 3.4964 | 6m CIM
| The Lines Company | 190.5517 | 3.4333 | 1245.9488 | 7.8774 | 120 |  |  | The Lines Company | 190.5517 | 3.4333 | 1245.9488 | 7.8774 | 120 SAIDI
| Top Energy | 399.2499 | 4.8196 | 1714.8267 | 7.4615 | 120 |  |  | Top Energy | 399.2499 | 4.8196 | 1714.8267 | 7.4615 | 120 SAIDI
| Unison Networks | 86.4616 | 1.8737 | 688.374 | 4.9114 | 50.6551 |  |  | Unison Networks | 86.4616 | 1.8737 | 688.374 | 4.9114 | 6m CIM
| Vector Lines | 110.0713 | 1.4034 | 643.9186 | 3.1661 | 9.9386 |  |  | Vector Lines | 110.0713 | 1.4034 | 643.9186 | 3.1661 | 6m CIM
| Wellington Electricity | 37.8414 | 0.58286 | 76.6647 | 0.60894 | 34.5797 |  |  | Wellington Electricity | 37.8414 | 0.58286 | 76.6647 | 0.60894 | 6m CIM
Attachment E
Quality standards, QIS, normalisation and reference periods
Table E6 | Draft annual unplanned reliability standards
| EDB | Unplanned SAIDI | Unplanned SAIFI
| Alpine Energy | 121.6919 | 1.1372
| Aurora Energy | 122.0546 | 1.9675
| EA Networks | 90.842 | 1.311
| Firstlight Network | 230.4333 | 3.2346
| Electricity Invercargill | 27.1479 | 0.70601
| Horizon Energy | 184.8005 | 2.2709
| Nelson Electricity | 18.6171 | 0.40635
| Network Tasman | 97.7256 | 1.1358
| Orion NZ | 80.4749 | 0.98188
| OtagoNet | 168.3724 | 2.4935
| Powerco | 189.2659 | 2.155
| The Lines Company | 190.5517 | 3.4333
| Top Energy | 399.2499 | 4.8196
| Unison Networks | 86.4616 | 1.8737
| Vector Lines | 110.0713 | 1.4034
| Wellington Electricity | 37.8414 | 0.58286
Table E7 | Regulatory period draft planned reliability standards (5-year total)
| EDB | Planned SAIDI | Planned SAIFI
| Alpine Energy | 742.3817 | 3.1437
| Aurora Energy | 1077.7756 | 6.0923
| EA Networks | 1238.4738 | 4.4045
| Firstlight Network | 1161.6097 | 6.7271
| Electricity Invercargill | 125.943 | 0.57017
| Horizon Energy | 944.4957 | 5.9856
| Nelson Electricity | 165.7239 | 2.1297
| Network Tasman | 1019.6462 | 4.4119
| Orion NZ | 215.4114 | 0.68659
| OtagoNet | 1945.7454 | 8.7119
| Powerco | 781.1663 | 3.4964
| The Lines Company | 1245.9488 | 7.8774
| Top Energy | 1714.8267 | 7.4615
| Unison Networks | 688.374 | 4.9114
| Vector Lines | 643.9186 | 3.1661
| Wellington Electricity | 76.6647 | 0.60894
Table E18 | Draft incentive rates for DPP4 compared to DPP3
|  | DPP3 |  |  | DPP4
|  | Unplanned Incentive rate | Planned incentive rate | "Notified" Planned Incentive rate | Unplanned Incentive rate | Planned incentive rate | "Notified" Planned Incentive rate
|  |  | 50% | 25% |  | 65% | 25%
| Alpine Energy | 7879 | 3939.5 | 1969.75 | 15978.4558 | 10385.9963 | 3994.614
| Aurora Energy | 14279 | 7139.5 | 3569.75 | 26580.9622 | 17277.6254 | 6645.2405
| EA Networks | 5394 | 2697 | 1348.5 | 11694.2287 | 7601.2486 | 2923.5572
| Firstlight Network | 2797 | 1398.5 | 699.25 | 5750.1966 | 3737.6278 | 1437.5491
| Electricity Invercargill | 2544 | 1272 | 636 | 5040.606 | 3276.3939 | 1260.1515
| Horizon Energy | 5397 | 2698.5 | 1349.25 | 10966.6686 | 7128.3346 | 2741.6671
| Nelson Electricity | 1417 | 708.5 | 354.25 | 2740.1301 | 1781.0846 | 685.0325
| Network Tasman | 6260 | 3130 | 1565 | 12957.6444 | 8422.4688 | 3239.4111
| Orion NZ | 31686 | 15843 | 7921.5 | 66372.363 | 43142.036 | 16593.0908
| OtagoNet | 4339 | 2169.5 | 1084.75 | 9088.206 | 5907.3339 | 2272.0515
| Powerco | 47908 | 23954 | 11977 | 99381.6981 | 64598.1038 | 24845.4245
| The Lines Company | 3827 | 1913.5 | 956.75 | 7369.6396 | 4790.2657 | 1842.4099
| Top Energy | 3283 | 1641.5 | 820.75 | 6566.7487 | 4268.3867 | 1641.6872
| Unison Networks | 16185 | 8092.5 | 4046.25 | 33224.8988 | 21596.1842 | 8306.2247
| Vector Lines | 84519 | 42259.5 | 21129.75 | 167795.1726 | 109066.8622 | 41948.7931
| Wellington Electricity | 23215 | 11607.5 | 5803.75 | 45674.7091 | 29688.5609 | 11418.6773
Table E20 | DPP4 Implied maximum revenue at risk.
| EDB | Maximum loss |  |  | Maximum gain
|  | Unplanned | Planned | Total | Unplanned | Planned | Total
| Alpine Energy | 0.6552% | 1.026% | 1.681% | 1.872% | 0.9787% | 2%
Indicative only | Aurora Energy | 0.5293% | 0.642% | 1.171% | 1.656% | 1.866% | 2%
| EA Networks | 0.3795% | 1.639% | 2% | 1.384% | 1.487% | 2%
| Firstlight Network | 0.5969% | 1.146% | 1.743% | 2.275% | 0.7363% | 2%
| Electricity Invercargill | 0.2561% | 0.1564% | 0.4125% | 0.3768% | 0.2253% | 0.6021%
| Horizon Energy | 1.33% | 1.481% | 2% | 3.971% | 2.041% | 2%
| Nelson Electricity | 0.3085% | 0.3476% | 0.6562% | 0.2923% | 0.3476% | 0.6399%
| Network Tasman | 0.7086% | 1.84% | 2% | 2.005% | 1.84% | 2%
| Orion NZ | 0.3867% | 0.3124% | 0.6991% | 1.409% | 0.3124% | 1.721%
| OtagoNet | 0.7882% | 2.354% | 2% | 2.346% | 2.354% | 2%
| Powerco | 0.5836% | 0.9974% | 1.581% | 3.134% | 0.9974% | 2%
| The Lines Company | 0.5146% | 1.032% | 1.547% | 1.915% | 1.032% | 2%
| Top Energy | 0.7424% | 1.282% | 2% | 2.873% | 0.7369% | 2%
| Unison Networks | 0.2745% | 0.6862% | 0.9607% | 1.27% | 0.9128% | 2%
| Vector Lines | 0.3818% | 0.7029% | 1.085% | 2.192% | 1.254% | 2%
| Wellington Electricity | 0.2344% | 0.112% | 0.3464% | 0.8905% | 0.1842% | 1.075%
Note: Aurora is not included in Table E20 in the Reasons paper as it is on a CPP until 31 March 2026
Table E22 | Reduced frequency of major events
| Distributor | 2023 Circuit length (km) | Major events (compared to 23) | ‘Major half hours’ (compared to 1104)
| Electricity Invercargill | 665 | 15.295 | 734.16
| Nelson Electricity | 296 | 6.808 | 326.784
Tables for Draft Determination
Table 3.1.1 | Table 3.1.1: Accumulated SAIDI limits and accumulated SAIFI limits for planned interruptions for non-exempt EDBs for the
DPP regulatory period 1 April 2025 – 31 March 2030
| Non-exempt EDB | Planned accumulated SAIDI limit for the DPP regulatory period | Planned accumulated SAIFI limit for the DPP regulatory period
| Alpine Energy | 742.3817 | 3.1437
| Aurora Energy Limited | 1077.7756 | 6.0923
| Electricity Ashburton Limited | 1238.4738 | 4.4045
| Firstlight Network Limited | 1161.6097 | 6.7271
| Electricity Invercargill Limited | 125.943 | 0.57017
| Horizon Energy Distribution Limited | 944.4957 | 5.9856
| Nelson Electricity Limited | 165.7239 | 2.1297
| Network Tasman Limited | 1019.6462 | 4.4119
| Orion New Zealand Limited | 215.4114 | 0.68659
| OtagoNet Joint Venture | 1945.7454 | 8.7119
| Powerco Limited | 781.1663 | 3.4964
| The Lines Company Limited | 1245.9488 | 7.8774
| Top Energy Limited | 1714.8267 | 7.4615
| Unison Networks Limited | 688.374 | 4.9114
| Vector Limited | 643.9186 | 3.1661
| Wellington Electricity Lines Limited | 76.6647 | 0.60894
Table 3.2.1 | Table 3.2.1: Unplanned SAIDI limits, unplanned SAIFI limits, SAIDI unplanned boundary values and SAIFI unplanned boundary values
for non-exempt EDBs for the DPP regulatory period 1 April 2025 – 31 March 2030
| Non-exempt EDB | Unplanned SAIDI limit | Unplanned SAIFI limit | SAIDI unplanned boundary value | SAIFI unplanned boundary value
| Alpine Energy | 121.6919 | 1.1372 | 8.77 | 0.060423
| Aurora Energy Limited | 122.0546 | 1.9675 | 6.5603 | 0.084872
| Electricity Ashburton Limited | 90.842 | 1.311 | 5.7224 | 0.072888
| Firstlight Network Limited | 230.4333 | 3.2346 | 17.6725 | 0.18016
| Electricity Invercargill Limited | 27.1479 | 0.70601 | 4.865 | 0.09811
| Horizon Energy Distribution Limited | 184.8005 | 2.2709 | 12.9913 | 0.092
| Nelson Electricity Limited | 18.6171 | 0.40635 | 6.7935 | 0.14078
| Network Tasman Limited | 97.7256 | 1.1358 | 6.0837 | 0.065437
| Orion New Zealand Limited | 80.4749 | 0.98188 | 4.4076 | 0.036799
| OtagoNet Joint Venture | 168.3724 | 2.4935 | 11.8174 | 0.16449
| Powerco Limited | 189.2659 | 2.155 | 9.7826 | 0.053381
| The Lines Company Limited | 190.5517 | 3.4333 | 13.8486 | 0.14683
| Top Energy Limited | 399.2499 | 4.8196 | 29.0906 | 0.19457
| Unison Networks Limited | 86.4616 | 1.8737 | 4.5468 | 0.069154
| Vector Limited | 110.0713 | 1.4034 | 6.1083 | 0.045657
| Wellington Electricity Lines Limited | 37.8414 | 0.58286 | 1.8068 | 0.029188
Table 4.1 | Table 4.1: SAIDI unplanned interruption collars, SAIDI unplanned interruption targets and SAIDI unplanned interruption caps
for the DPP regulatory period 1 April 2025 – 31 March 2030
| Non-exempt EDB | SAIDI unplanned interruption collar | SAIDI unplanned interruption target | SAIDI unplanned interruption cap
| Alpine Energy | 0 | 90.1443 | 121.6919
| Aurora Energy Limited | 0 | 92.484 | 122.0546
| Electricity Ashburton Limited | 0 | 71.2988 | 90.842
| Firstlight Network Limited | 0 | 182.5404 | 230.4333
| Electricity Invercargill Limited | 0 | 16.1619 | 27.1479
| Horizon Energy Distribution Limited | 0 | 138.4455 | 184.8005
| Nelson Electricity Limited | 0 | 9.0567 | 18.6171
| Network Tasman Limited | 0 | 72.2088 | 97.7256
| Orion New Zealand Limited | 0 | 63.1426 | 80.4749
| OtagoNet Joint Venture | 0 | 126.0223 | 168.3724
| Powerco Limited | 0 | 159.5568 | 189.2659
| The Lines Company Limited | 0 | 150.1876 | 190.5517
| Top Energy Limited | 0 | 317.2673 | 399.2499
| Unison Networks Limited | 0 | 71.097 | 86.4616
| Vector Limited | 0 | 93.7418 | 110.0713
| Wellington Electricity Lines Limited | 0 | 29.9571 | 37.8414
Table 4.2 | Table 4.2: SAIDI planned interruption collars, SAIDI planned interruption targets, and SAIDI planned interruption caps
for the DPP regulatory period 1 April 2020 – 31 March 2025
| Non-exempt EDB | SAIDI planned interruption collar | SAIDI planned interruption Target | SAIDI planned interruption cap
| Alpine Energy | 0 | 72.5008 | 148.4763
| Aurora Energy Limited | 0 | 160.378 | 215.5551
| Electricity Ashburton Limited | 0 | 117.8216 | 247.6948
| Firstlight Network Limited | 0 | 90.8895 | 232.3219
| Electricity Invercargill Limited | 0 | 14.8697 | 25.1886
| Horizon Energy Distribution Limited | 0 | 109.4675 | 188.8991
| Nelson Electricity Limited | 0 | 16.5724 | 33.1448
| Network Tasman Limited | 0 | 101.9646 | 203.9292
| Orion New Zealand Limited | 0 | 21.5411 | 43.0823
| OtagoNet Joint Venture | 0 | 194.5745 | 389.1491
| Powerco Limited | 0 | 78.1166 | 156.2333
| The Lines Company Limited | 0 | 124.5949 | 249.1898
| Top Energy Limited | 0 | 125.1839 | 342.9653
| Unison Networks Limited | 0 | 78.5926 | 137.6748
| Vector Limited | 0 | 82.5326 | 128.7837
| Wellington Electricity Lines Limited | 0 | 9.535 | 15.3329
Table 4.3 | Table 4.3: Incentive rates for the
DPP regulatory period 1 April 2025 – 31 March 2030
| Non-exempt EDB | Incentive rate
| Alpine Energy | 15978.4558
| Aurora Energy Limited | 26580.9622
| Electricity Ashburton Limited | 11694.2287
| Firstlight Network Limited | 5750.1966
| Electricity Invercargill Limited | 5040.606
| Horizon Energy Distribution Limited | 10966.6686
| Nelson Electricity Limited | 2740.1301
| Network Tasman Limited | 12957.6444
| Orion New Zealand Limited | 66372.363
| OtagoNet Joint Venture | 9088.206
| Powerco Limited | 99381.6981
| The Lines Company Limited | 7369.6396
| Top Energy Limited | 6566.7487
| Unison Networks Limited | 33224.8988
| Vector Limited | 167795.1726
| Wellington Electricity Lines Limited | 45674.7091