## Tables from Document
Otahuhu Substation Diversity Project: Application for Increase in Major Capex Allowance
Table 3.1: PAD budget as compared with actual expenditure (NZ $m)
|  | Overspend Category/ Adjustment to PAD Estimate | PAD Budget 2006 $ | Actual | Overspend relative to PAD | PAD Budget in Commissioning Year 2009 $ | Overspend relative to adjusted PAD |  | PAD record:
[9 empty] | Prepared By: | Transpower - John Heaney
| A | Enabling Works Civil General | 3.5281 | 11.0009 | 7.4728 | 3.8139 | 7.187 |  | Checked / reviewed by: | Transpower - Daniel Crawshay
|  | Stormwater Drainage | 0.069712 | 3.064 | 2.9943 | 0.075359 | 2.9886 |  | Date of Estimate: | 2007-09-18
|  | Wastewater | 0.27883 | 1.7894 | 1.5106 | 0.30141 | 1.488 |  | Estimate revision: | 3
|  | Underground Services Relocation | 0.17427 | 1.7622 | 1.5879 | 0.18838 | 1.5738 |  | Pricebook Version: | B08
|  | Warehouse Building Relocation | 1.1946 | 1.5199 | 0.32532 | 1.2914 | 0.22856 |  | Pricebook Date: | 2006-06-12
|  | Earthworks and General | 1.8107 | 2.8653 | 1.0546 | 1.9574 | 0.90795
| B | Transmission Line Deviations | 2.3522 | 4.1932 | 1.8411 | 2.5427 | 1.6505
|  | 220 kV tower piled foundations | 0.066 | 2.4316 | 2.3656 | 0.071346 | 2.3603
|  | Other work | 2.2862 | 1.7616 | -0.5246 | 2.4714 | -0.70978
| C | Enabling Works Secondary Equipment Design & Install | 2.8074 | 7.6699 | 4.8625 | 3.0348 | 4.6351
| D | EW Transition Station & Cable Termination Design & Install | 3.1701 | 7.068 | 3.8979 | 3.4269 | 3.6412
|  | Cable terminations | 1.2479 | 2.147 | 0.89915 | 1.3489 | 0.79807
|  | Transition Stations | 1.6293 | 3.9358 | 2.3065 | 1.7613 | 2.1745
|  | AIS switchyard works | 0.29288 | 0.98521 | 0.69232 | 0.31661 | 0.6686
| E | Enabling Works Procurement | 3.386 | 3.9042 | 0.51814 | 3.6603 | 0.24387
|  | Protection equipment | 0.5604 | 0.97122 | 0.41082 | 0.60579 | 0.36543
|  | Other procurement | 2.8256 | 2.933 | 0.10732 | 3.0545 | -0.12156
| F | Design Build GIS/AIS & EHV Cable | 58.1639 | 64.1987 | 6.0347 | 62.8752 | 1.3234
| G | Land Easement | 0 | 1.2 | 1.2 | 0 | 1.2
| H | Interest During Construction | 3.2033 | 6.9143 | 3.711 | 3.4627 | 3.4515
|  | TOTAL | 76.6111 | 106.1492 | 29.5381 | 82.8166 | 23.3326
|  | CHECKS | 0 | 0 | 0 | 0 | 0 | 0
Inflation from pricebook date to midpoint of project spend
|  | Jun 2006 CPI | 1000
|  | Jun 2009 CPI | 1081
Table 5.2: Project cost history
|  | Description/Project Status | Amount | Variance to PAD[1]
Date
| 2006-12-01 | GUP P90 | $99m | -
| 2007-08-01 | PAD Budget | 76.6111
| 2007-12-01 | Enabling design and construction contracts awarded | 81.5581 | 4.947
| 2008-10-01 | All major contracts awarded. Project 21% complete. Re-estimate for Board submission for additional funding | 100.2733 | 23.6622
| 2012-05-01 | Final Cost | 106.1492 | 29.5381
Table 5.3: PAD budget vs. actual expenditure (NZ $m)
|  | Overspend Category/ | PAD Budget 2006 $ | Actual | Overspend relative to PAD | Adjusted PAD[1] 2009 $ | Overspend relative to adjusted PAD
Adjustment to PAD Estimate
| A | Enabling Works Civil General | 3.5281 | 11.0009 | 7.4728 | 3.8139 | 7.187
| B | Transmission Line Deviations | 2.3522 | 4.1932 | 1.8411 | 2.5427 | 1.6505
| C | Enabling Works Secondary Equipment Design & Install | 2.8074 | 7.6699 | 4.8625 | 3.0348 | 4.6351
| D | EW Transition Station & Cable Termination Design & Install | 3.1701 | 7.068 | 3.8979 | 3.4269 | 3.6412
| E | Enabling Works Procurement | 3.386 | 3.9042 | 0.51814 | 3.6603 | 0.24387
| F | Design Build GIS/AIS & EHV Cable | 58.1639 | 64.1987 | 6.0347 | 62.8752 | 1.3234
| G | Land Easement | 0 | 1.2 | 1.2 | 0 | 1.2
| H | Interest During Construction | 3.2033 | 6.9143 | 3.711 | 3.4627 | 3.4515
|  | TOTAL | 76.6111 | 106.1492 | 29.5381 | 82.8166 | 23.3326
Table 6.2: Enabling Works Civil General
| Date | Description | Amount | Variance to PAD
| 2007-08-01 | PAD Budget | 3.5281 | -
| 2007-12-01 | Main design and construction contracts for civil site works award | 4.9353 | 1.4071
| 2008-10-01 | Construction underway – re-estimate for Board submission for additional funding | 9.6585 | 6.1303
| 2012-05-01 | Final Cost | 11.0009 | 7.4728
Table 7: Subcategories of Enabling Works Civil General
|  | Description | PAD Budget | Actual | Variance
|  | Stormwater Drainage | 69.7122 | 3063.9877 | 2994.2755
|  | Underground Services Relocation | 174.2691 | 1762.2081 | 1587.939
|  | Wastewater | 278.826 | 1789.433 | 1510.607
|  | Warehouse Building Relocation | 1194.6118 | 1519.9361 | 325.3243
|  | Earthworks and General | 1810.7084 | 2865.3286 | 1054.6202
|  | Total | 3528.1275 | 11000.8935 | 7472.766
Table 6.3: Transmission Line Deviations
| Date | Description | Amount | Variance
| 2007-08-01 | PAD Budget | 2352.1767 | -
| 2007-12-01 | Enabling design and construction contracts for civil site works awarded | 3436.1053 | 1083.9286
| 2008-10-01 | Design contracts awarded – re-estimate for Board submission for additional funding | 4021.3664 | 1669.1897
| 2012-05-01 | Final Cost | 4193.2277 | 1841.0511
Table 6.4: Enabling works secondary systems – design and build
| Date | Description | Amount | Variance
| 2007-08-01 | PAD Budget | 2807.4272 | -
| 2007-12-01 | Construction contract awarded | 3177.8228 | 370.3956
| 2008-10-01 | Design contracts awarded – re-estimate for Board submission for additional funding | 5380.5492 | 2573.122
| 2012-05-01 | Final Cost | 7669.9265 | 4862.4993
Table 6.5: Enabling works station and cable termination
| Date | Description | Amount | Variance
| 2007-08-01 | PAD Budget | 3170.0936 | -
| 2007-12-01 | Construction contract awarded | 3758.5821 | 588.4885
| 2008-10-01 | Construction commenced – re-estimate for Board submission for additional funding | 4384.2359 | 1214.1423
| 2012-05-01 | Final Cost | 7068.0213 | 3897.9276
Table 6.6: Subcategories of the enabling works station and cable termination
|  | Description | PAD Budget | Actual | Variance
|  | Cable Terminations | 1247.8705 | 2147.0173 | 899.1467
|  | Transition Stations | 1629.3393 | 3935.7977 | 2306.4584
|  | AIS Switchyard Works | 292.8838 | 985.2063 | 692.3225
|  | Total | 3170.0936 | 7068.0213 | 3897.9276
Table 6.7: Cost history for Design/Build contract for GIS/AIS substation and 220 kV cabling
| Date | Description | Amount | Variance
| 2007-08-01 | PAD Budget | 58163.9448 | -
| 2008-10-01 | Re-estimate for Board submission for additional funding | 62080.0011 | $3.9m
| 2012-05-01 | Final Cost | 64198.6644 | 6034.7197

## Model Map
Otahuhu Substation Diversity Project: Application for Increase in Major Capex Allowance
The purpose of this model is to align the PAD budget and Actual spend to allow comparison and understand the drivers for overspend
This model supports the Otahuhu application for increase in major capex allowance
Summary worksheet
PAD Budget
Actual Spend
Cost Assignment worksheet
CA level worksheet
UR-Summary PAD worksheet
data transposed and formatted
2. Transmission Line Deviations worksheet
3. Enabling Wks - General Civil worksheet
Actual Breakdown worksheet
Matrix assigning costs from original PAD structure to categories used for Application

## Model explained
Note on C33: oakdeng: Tower installation item plus contingency at 10%
NOTES ON SUBCATEGORY COST BREAKDOWN General The "Summary" sheet aligns the overspend for the original PAD budget with the Actual spend, the alignment is by 'Subcategory' . The nature of the overspend did not align well with project Work Breakdown Structure (WBS) so 'Categories' and 'Subcategories' were specifically developed to support the explanation of the overspend. The Categories are defined by mapping WBS Work Packages as shown in sheet 'Cost Assignment' of this workbook, however, at the next level down Subcategory breakdown required identification of more specific detailed cost information from the various contract price schedules, FMIS and other sources then prorating the Category balance. Methodology for Subcategory breakdown varies by Category is as follows: A - Enabling Works General Civil & B - Transmission Line Deviations The original budget is a breakdown of the category total based on the total of relevant Items in sheet '2.Transmission Line Deviations' and sheet '3.Enabling Wks - General Civil' from the original PAD estimate work book . For Category A, this is adjusted prorata to balance category total as calclulated in sheet 'Overspend' (i.e. 4% different). Category B picks out the single relevant line item for Subcategory F including PAD budget contingency of 10% with subcategory O being the balance. Actuals are mapped for Enabling Works Installation contract costs against payment schedule item from workbook 'OTA Enabling Works Price Schedule September_10_Changes_2_Payment DFA Submission Com Com Appln. xls' sheet ‘Schedule’ (where approximately 900 payment schedule items are mapped to Category and Subcategory as identified in column A and B respectively. This identifies direct construction cost only. The Category balance comprising project management (TP and Contractor) and design costs as identified at Category level are then prorated by specifically identified direct Subcategory construction cost. D - EW Transition Station & cable Termination Design & Install Both PAD budget and actuals are mapped from Work Packages are as shown in sheet 'Cost Assignment' and adjusted prorata for project managment etc E - Enabling Works Procurement PAD budget and actuals for 'Protection Equipment' are from a single work package and 'Other Procurement' is the category balance. GJO 13/9/12

## Summary
Otahuhu Substation Diversity Project: Application for Increase in Major Capex Allowance
Comparison of PAD Budget and Actual Spend in aligned Categories and Subcategories
$,000
| Overspend Category/Subcategory | PAD Budget | Actual | CHECKS | CHECKS
A | Enabling Works Civil General | 3528.1275 | 11000.8935 | 0 | 0
| S - Stormwater Drainage | 69.7122 | 3063.9877
| W- Wastewater | 278.826 | 1789.433
| U - Underground Services Relocation | 174.2691 | 1762.2081
| W - Warehouse Building Relocation | 1194.6118 | 1519.9361
| E- Earthworks and General | 1810.7084 | 2865.3286
B | Transmission Line Deviations | 2352.1767 | 4193.2277 | 0 | 0
| F - 220 kV Tower Piled Foundations and Install | 66 | 2431.6486
| O - Line Deviation Other | 2286.1767 | 1761.5791
C | Enabling Works Secondary Equipment Design & Install | 2807.4272 | 7669.9265
D | EW Transition Station & Cable Termination Design & Install | 3170.0936 | 7068.0213 | 0 | 0
| C - Cable Terminations | 1247.8705 | 2147.0173
| T - Transition Stations | 1629.3393 | 3935.7977
| S - AIS Switchyard Works | 292.8838 | 985.2063
E | Enabling Works Procurement | 3386.0423 | 3904.181 | 0 | 0
| P - Protection Equipment | 560.4 | 971.2211
| O - Other Procurement | 2825.6423 | 2932.9599
F | Design Build GIS/AIS & EHV Cable | 58163.9448 | 64198.6644
G | Land Easement | 0 | 1200
H | Interest During Construction | 3203.27 | 6914.2827
| TOTAL | 76611.082 | 106149.1971 | 0 | 0
Note on C14: oakdeng: Tower installation item plus contingency at 10%

## Cost Assignment
Otahuhu Overspend - Matrix assigning costs from original PAD structure to categories used for Application
Tracked over time: forecasts and actuals versus PAD budget
|  | Summary Table for PAD versus Actual Spend by Categories used for Application | [46 empty] | Summary Table for PAD versus Forecast Spend Dec 2007 | [9 empty] | Summary Table for PAD versus Forecast Spend Oct 2008
|  | Category | Overspend Category | PAD Budget | Actual | Variance | Percent Change | [42 empty] | Overspend Category | PAD Budget | Forecast 12/07 | Variance | Percent Change |  |  |  |  | Category | Overspend Category | PAD Budget | Forecast 10/08 | Variance | Percent Change
|  | A | Enabling Works Civil General | 3528.1275 | 11000.8935 | 7472.766 | 211.8% | [41 empty] | A | Enabling Works Civil General | 3528.1275 | 4935.2653 | 1407.1378 | 39.88% |  |  |  |  | A | Enabling Works Civil General | 3528.1275 | 9658.4594 | 6130.3319 | 173.8%
|  | B | Transmission Line Deviations | 2352.1767 | 4193.2277 | 1841.0511 | 78.27% | [41 empty] | B | Transmission Line Deviations | 2352.1767 | 3436.1053 | 1083.9286 | 46.08% |  |  |  |  | B | Transmission Line Deviations | 2352.1767 | 4021.3664 | 1669.1897 | 70.96%
|  | C | Enabling Works Secondary Equipment Design & Install | 2807.4272 | 7669.9265 | 4862.4993 | 173.2% | [41 empty] | C | Enabling Works Secondary Equipment Design & Install | 2807.4272 | 3177.8228 | 370.3956 | 13.19% |  |  |  |  | C | Enabling Works Secondary Equipment Design & Install | 2807.4272 | 5380.5492 | 2573.122 | 91.65%
|  | D | EW Transition Station & Cable Termination Design & Install | 3170.0936 | 7068.0213 | 3897.9276 | 123% | [41 empty] | D | EW Transition Station & Cable Termination Design & Install | 3170.0936 | 3758.5821 | 588.4885 | 18.56% |  |  |  |  | D | EW Transition Station & Cable Termination Design & Install | 3170.0936 | 4384.2359 | 1214.1423 | 38.3%
|  | E | Enabling Works Procurement | 3386.0423 | 3904.181 | 518.1387 | 15.3% | [41 empty] | E | Enabling Works Procurement | 3386.0423 | 3373.7329 | -12.3093 | -0.3635% |  |  |  |  | E | Enabling Works Procurement | 3386.0423 | 3487.654 | 101.6117 | 3.001%
|  | F | Design Build GIS/AIS & EHV Cable | 58163.9448 | 64198.6644 | 6034.7197 | 10.38% | [41 empty] | F | Design Build GIS/AIS & EHV Cable | 58163.9448 | 54455.0505 | -3708.8942 | -6.377% |  |  |  |  | F | Design Build GIS/AIS & EHV Cable | 58163.9448 | 62080.0011 | 3916.0564 | 6.733%
|  | G | Land Easement | 0 | 1200 | 1200 | 'NA' | [41 empty] | G | Land Easement | 0 | 0 | 0 | 'NA' |  |  |  |  | G | Land Easement | 0 | 0 | 0 | 'NA'
|  | H | Interest During Construction | 3203.27 | 6914.2827 | 3711.0127 | 115.9% | [41 empty] | H | Interest During Construction | 3203.27 | 4939 | 1735.73 | 54.19% |  |  |  |  | H | Interest During Construction | 3203.27 | 7778 | 4574.73 | 142.8%
|  |  | TOTAL | 76611.082 | 106149.1971 | 29538.1151 | 38.56% | [42 empty] | TOTAL | 76611.082 | 78075.5589 | 1464.4769 | 1.912% |  |  |  |  | 0 | TOTAL | 76611.082 | 96790.266 | 20179.184 | 26.34%
[59 empty] | 0 | 0 | 0
|  |  | Enabling Works Design & Install Subtotal | 11857.8249 | 29932.069 | 18074.244 | 152.4% | [41 empty] | 0 | Enabling Works Design & Install Subtotal | 11857.8249 | 15307.7754 | 3449.9505 | 29.09% |  |  |  |  | 0 | Enabling Works Design & Install Subtotal | 11857.8249 | 23444.6109 | 11586.7859 | 97.71%
|  |  | EW Procure & DB Works Subtotal | 61549.987 | 68102.8454 | 6552.8584 | 10.65% | [41 empty] | 0 | EW Procure & DB Works Subtotal | 61549.987 | 57828.7835 | -3721.2036 | -6.046% |  |  |  |  | 0 | EW Procure & DB Works Subtotal | 61549.987 | 65567.6551 | 4017.6681 | 6.527%
[47 empty] | Total incl Land Easement and Investigations Project |  |  |  |  | 81558.0749 | [9 empty] | 100273.266 | 20.97% | Percent complete based on actual to date + investigations divided by total actual minus land easement cost
[11 empty] | MATRIX ASSIGNING COSTS from PAD to categories used for Application | [8 empty] | PAD Budget assigned to Categories used for Application | [6 empty] | MATRIX ASSIGNING COSTS to categories used for Application: with adjustments for Actual Spend distribution
Otahuhu Original breakdown per PAD | [8 empty] | Work Package to Overspend Category Map - PAD Budget | [9 empty] | Application of Work Package to Overspend Category Map - PAD Budget | [7 empty] | Adjusted PM Share for Actuals | [9 empty] | Actual Spend assigned to Categories used for Application | [10 empty] | Forecast as at December 2007 - Enabling Works Contracts Awarded | [10 empty] | Forecast as at October 2008 - Board Submission for Additioal Funding
This includes the complete Transpower work break down structure. | [8 empty] | A | B | C | D | E | F | G | H |  |  | A | B | C | D | E | F | G | H | A | B | C | D | E | F | G | H |  |  | A | B | C | D | E | F | G | H |  |  |  | A | B | C | D | E | F | G | H |  |  |  | A | B | C | D | E | F | G | H
| Workstream | WP | Description | PAD Budget | Actual | Variance | Percent Change | Cat | Enabling Works Civil General | Transmission Line Deviations | Enabling Works Secondary Equipment Design & Install | EW Transition Station & Cable Termination Design & Install | Enabling Works Procurement | Design Build GIS/AIS & EHV Cable | Land Easement | Interest During Construction | Zero Check |  | Enabling Works Civil General | Transmission Line Deviations | Enabling Works Secondary Equipment Design & Install | EW Transition Station & Cable Termination Design & Install | Enabling Works Procurement | Design Build GIS/AIS & EHV Cable | Land Easement | Interest During Construction | Enabling Works Civil General | Transmission Line Deviations | Enabling Works Secondary Equipment Design & Install | EW Transition Station & Cable Termination Design & Install | Enabling Works Procurement | Design Build GIS/AIS & EHV Cable | Land Easement | Interest During Construction | Zero Check |  | Enabling Works Civil General | Transmission Line Deviations | Enabling Works Secondary Equipment Design & Install | EW Transition Station & Cable Termination Design & Install | Enabling Works Procurement | Design Build GIS/AIS & EHV Cable | Land Easement | Interest During Construction |  | ID | Forecast 12/07 | Enabling Works Civil General | Transmission Line Deviations | Enabling Works Secondary Equipment Design & Install | EW Transition Station & Cable Termination Design & Install | Enabling Works Procurement | Design Build GIS/AIS & EHV Cable | Land Easement | Interest During Construction |  | ID | Forecast 10/08 | Enabling Works Civil General | Transmission Line Deviations | Enabling Works Secondary Equipment Design & Install | EW Transition Station & Cable Termination Design & Install | Enabling Works Procurement | Design Build GIS/AIS & EHV Cable | Land Easement | Interest During Construction
#REF! | Investigations Projects | 01 | OTA Diversity (CP_OTA_01) | 0 | 2282.516 | 2282.516 | 'NA' |  | 5% | 5% | 12% | 5% | 3% | 70% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 114.1258 | 114.1258 | 273.9019 | 114.1258 | 68.4755 | 1597.7612 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#REF! | Management/Support | 10_10 | Project Management | 3381.661 | 2251.8094 | -1129.8516 | -33.41% |  | 4.6% | 2.2% | 5.1% | 8.3% | 0.8% | 79% | 0% | 0% | 0 |  | 155.5564 | 74.3965 | 172.4647 | 280.6779 | 27.0533 | 2671.5122 | 0 | 0 | 12% | 5% | 15% | 14% | 1% | 53% | 0% | 0% | 0 |  | 270.2171 | 112.5905 | 337.7714 | 315.2533 | 22.5181 | 1193.459 | 0 | 0 |  | 10_10 | 1632 | 195.84 | 81.6 | 244.8 | 228.48 | 16.32 | 864.96 | 0 | 0 |  | 10_10 | 1709 | 205.08 | 85.45 | 256.35 | 239.26 | 17.09 | 905.77 | 0 | 0
|  | 10_20 | Transpower Technical Support | 354.8841 | 718.5089 | 363.6248 | 102.5% |  | 4.6% | 2.2% | 5.1% | 8.3% | 0.8% | 79% | 0% | 0% | 0 |  | 16.3247 | 7.8074 | 18.0991 | 29.4554 | 2.8391 | 280.3584 | 0 | 0 | 12% | 5% | 15% | 14% | 1% | 53% | 0% | 0% | 0 |  | 86.2211 | 35.9254 | 107.7763 | 100.5912 | 7.1851 | 380.8097 | 0 | 0 |  | 10_20 | 354.8841 | 42.5861 | 17.7442 | 53.2326 | 49.6838 | 3.5488 | 188.0886 | 0 | 0 |  | 10_20 | 442.272 | 53.0726 | 22.1136 | 66.3408 | 61.9181 | 4.4227 | 234.4042 | 0 | 0
|  | 10_30 | External Technical Support | 287.5545 | 1827 | 1539.4455 | 535.4% |  | 4.6% | 2.2% | 5.1% | 8.3% | 0.8% | 79% | 0% | 0% | 0 |  | 13.2275 | 6.3262 | 14.6653 | 23.867 | 2.3004 | 227.168 | 0 | 0 | 12% | 5% | 15% | 14% | 1% | 53% | 0% | 0% | 0 |  | 219.24 | 91.35 | 274.05 | 255.78 | 18.27 | 968.31 | 0 | 0 |  | 10_30 | 436.96 | 52.4352 | 21.848 | 65.544 | 61.1744 | 4.3696 | 231.5888 | 0 | 0 |  | 10_30 | 1010.327 | 121.2392 | 50.5164 | 151.549 | 141.4458 | 10.1033 | 535.4733 | 0 | 0
|  | 10_40 | Environmental | 32.972 | 137.5968 | 104.6248 | 317.3% |  | 4.6% | 2.2% | 5.1% | 8.3% | 0.8% | 79% | 0% | 0% | 0 |  | 1.5167 | 0.72538 | 1.6816 | 2.7367 | 0.26378 | 26.0479 | 0 | 0 | 12% | 5% | 15% | 14% | 0% | 54% | 0% | 0% | 0 |  | 16.5116 | 6.8798 | 20.6395 | 19.2636 | 0 | 74.3023 | 0 | 0 |  | 10_40 | 32.972 | 3.9566 | 1.6486 | 4.9458 | 4.6161 | 0 | 17.8049 | 0 | 0 |  | 10_40 | 107 | 12.84 | 5.35 | 16.05 | 14.98 | 0 | 57.78 | 0 | 0
|  | 10_50 | Property | 24.729 | 9.5237 | -15.2053 | -61.49% |  | 4.6% | 2.2% | 5.1% | 8.3% | 0.8% | 79% | 0% | 0% | 0 |  | 1.1375 | 0.54404 | 1.2612 | 2.0525 | 0.19783 | 19.5359 | 0 | 0 | 12% | 5% | 15% | 14% | 0% | 54% | 0% | 0% | 0 |  | 1.1428 | 0.47618 | 1.4285 | 1.3333 | 0 | 5.1428 | 0 | 0 |  | 10_50 | 24.729 | 2.9675 | 1.2365 | 3.7094 | 3.4621 | 0 | 13.3537 | 0 | 0 |  | 10_50 | 24.729 | 2.9675 | 1.2365 | 3.7094 | 3.4621 | 0 | 13.3537 | 0 | 0
|  | 10_60 | Switching & RTU/SCADA | 60.1 | 122 | 61.9 | 103% |  | 4.6% | 2.2% | 5.1% | 8.3% | 0.8% | 79% | 0% | 0% | 0 |  | 2.7646 | 1.3222 | 3.0651 | 4.9883 | 0.4808 | 47.479 | 0 | 0 | 12% | 5% | 15% | 14% | 0% | 54% | 0% | 0% | 0 |  | 14.64 | 6.1 | 18.3 | 17.08 | 0 | 65.88 | 0 | 0 |  | 10_60 | 60.1 | 7.212 | 3.005 | 9.015 | 8.414 | 0 | 32.454 | 0 | 0 |  | 10_60 | 450 | 54 | 22.5 | 67.5 | 63 | 0 | 243 | 0 | 0
|  | 10_70 | OTA Warehouse Changes | 0 | 149.853 | 149.853 | 'NA' |  | 4.6% | 2.2% | 5.1% | 8.3% | 0.8% | 79% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 149.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10_70 | 185 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 10_80 | Site Village & Security/Safety Services | 0 | 1347.3047 | 1347.3047 | 'NA' |  | 4.6% | 2.2% | 5.1% | 8.3% | 0.8% | 79% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12% | 5% | 15% | 14% | 0% | 54% | 0% | 0% | 0 |  | 161.6766 | 67.3652 | 202.0957 | 188.6227 | 0 | 727.5445 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 10_85 | SWN & OTA 'C' Cables & Post Commissioning | 0 | 1204 | 1204 | 'NA' |  | 4.6% | 2.2% | 5.1% | 8.3% | 0.8% | 79% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 31% | 0% | 54% | 0% | 0% | 0 |  | 60.2 | 60.2 | 60.2 | 373.24 | 0 | 650.16 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 10_90 | Contingency | 426.4248 | 2 | -424.4248 | -99.53% |  | 4.6% | 2.2% | 5.1% | 8.3% | 0.8% | 79% | 0% | 0% | 0 |  | 19.6155 | 9.3813 | 21.7477 | 35.3933 | 3.4114 | 336.8756 | 0 | 0 | 12% | 5% | 15% | 14% | 0% | 54% | 0% | 0% | 0 |  | 0.24 | 0.1 | 0.3 | 0.28 | 0 | 1.08 | 0 | 0 |  | 10_90 | 426.42 | 51.1704 | 21.321 | 63.963 | 59.6988 | 0 | 230.2668 | 0 | 0 |  | 10_90 | 228 | 27.36 | 11.4 | 34.2 | 31.92 | 0 | 123.12 | 0 | 0
#REF! | Enabling Works Design | 20_01 | 110 kV Tie Line Deviation | 104.96 | 106.289 | 1.329 | 1.266% | B | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 104.96 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 106.289 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_01 | 55 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_01 | 105 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_02 | OTA - PEN C Deviation | 94.9 | 184.5643 | 89.6643 | 94.48% | B | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 94.9 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 184.5643 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_02 | 93 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_02 | 133 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_03 | Warehouse Relocation/Alteration | 36.52 | 82.5352 | 46.0152 | 126% | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 36.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 82.5352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_03 | 140 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_03 | 73 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_04 | Manhole and Contact Sewer Relocation | 12.5 | 103.213 | 90.713 | 725.7% | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 103.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_04 | 69.9 | 69.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_04 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_05 | Site Platform Formation and Stormwater Relocation | 66.48 | 263.4265 | 196.9465 | 296.2% | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 66.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 263.4265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_05 | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_05 | 206 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_06 | 220 kV Switchyard Extensions | 101.31 | 167.8065 | 66.4965 | 65.64% | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 101.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 167.8065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_06 | 135.2 | 135.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_06 | 165 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_07 | 220 kV Bus Zone Protection Modifications | 157.3 | 105.4528 | -51.8472 | -32.96% | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 157.3 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 105.4528 | 0 | 0 | 0 | 0 | 0 |  | 20_07 | 157.3 | 0 | 0 | 157.3 | 0 | 0 | 0 | 0 | 0 |  | 20_07 | 41 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0
|  | 20_08 | 220 kV Protection System | 225 | 328.5088 | 103.5088 | 46% | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 328.5088 | 0 | 0 | 0 | 0 | 0 |  | 20_08 | 225 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 |  | 20_08 | 116 | 0 | 0 | 116 | 0 | 0 | 0 | 0 | 0
|  | 20_09 | Cable Transition Stations | 61.6 | 120.0085 | 58.4085 | 94.82% | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 61.6 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 120.0085 | 0 | 0 | 0 | 0 |  | 20_09 | 118.8 | 0 | 0 | 0 | 118.8 | 0 | 0 | 0 | 0 |  | 20_09 | 154 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0
|  | 20_10 | Communications | 0 | 105.358 | 105.358 | 'NA' | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 105.358 | 0 | 0 | 0 | 0 | 0 |  | 20_10 | 70 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 |  | 20_10 | 87 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0
|  | 20_11 | SCADA | 58.72 | 60.1965 | 1.4765 | 2.514% | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 58.72 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 60.1965 | 0 | 0 | 0 | 0 | 0 |  | 20_11 | 75 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 |  | 20_11 | 44 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0
|  | 20_12 | Local Service Power Supplies | 0 | 63.97 | 63.97 | 'NA' | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 63.97 | 0 | 0 | 0 | 0 | 0 |  | 20_12 | 13.3 | 0 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 |  | 20_12 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0
|  | 20_15 | Earthgrid Connections | 0.81 | 7.0004 | 6.1904 | 764.3% | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 7.0004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_15 | 7.4 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_15 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_16 | Sewerage Connection | 0 | 40.0061 | 40.0061 | 'NA' | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 40.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_16 | 64.9 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_16 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_17 | Water Supply | 5 | 2.0008 | -2.9992 | -59.98% | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 2.0008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_17 | 11.4 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_17 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_18 | Roading | 0 |  |  |  | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [19 empty] | 20_18 | 20.2 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_18 | 20.2 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_19 | Vector Cable Relocation | 0 |  |  |  | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [19 empty] | 20_19 | 18.8 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_19 | 18.8 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_20 | Miscellaneous Site Works | 0 | 101.6968 | 101.6968 | 'NA' | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 101.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_20 | 31.5 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_20 | 63 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_21 | Cable Route Security | 0 |  |  |  | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [19 empty] | 20_21 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_21 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_22 | Low Impedance BZ Prot Existing 220 kV AIS | 0 | 183.0582 | 183.0582 | 'NA' | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 183.0582 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_22 | 61 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0
|  | 20_23 | Prot Settings Existing BZ | 0 | 7 | 7 | 'NA' | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_23 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0
|  | 20_24 | Prot Settings Existing AIS | 0 | 30.5471 | 30.5471 | 'NA' | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 30.5471 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_24 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0
|  | 20_25 | Prot Settings GIS | 0 | 271.4987 | 271.4987 | 'NA' | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 271.4987 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_25 | 85 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0
|  | 20_26 | Prot Settings Low Impedance BZ Existing AIS | 0 | 9.9002 | 9.9002 | 'NA' | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 9.9002 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_26 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0
|  | 20_30 | Tie Line and Line Protection | 0 | 611.881 | 611.881 | 'NA' | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 611.881 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20_30 | 264 | 0 | 0 | 264 | 0 | 0 | 0 | 0 | 0
|  | 20_85 | SWN & OTA 'C' Cables & Post Commissioning | 0 | 349 | 349 | 'NA' |  | 15% | 0% | 5% | 80% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 52.35 | 0 | 17.45 | 279.2 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20_90 | Contingency | 94.8853 | 7 | -87.8853 | -92.62% |  | 35% | 20% | 20% | 20% | 5% | 0% | 0% | 0% | 0 |  | 33.2099 | 18.9771 | 18.9771 | 18.9771 | 4.7443 | 0 | 0 | 0 | [10 empty] | 2.45 | 1.4 | 1.4 | 1.4 | 0.35 | 0 | 0 | 0 |  | 20_90 | 94.89 | 33.2115 | 18.978 | 18.978 | 18.978 | 4.7445 | 0 | 0 | 0 |  | 20_90 | 64 | 22.4 | 12.8 | 12.8 | 12.8 | 3.2 | 0 | 0 | 0
#REF! | Procurement | 30_01 | Miscellaneous | 50 | 75.4267 | 25.4267 | 50.85% | E | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 75.4267 | 0 | 0 | 0 |  | 30_01 | 50 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 |  | 30_01 | 100 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0
|  | 30_02 | Primary Equipment | 1538.5 | 1711.1051 | 172.6051 | 11.22% | E | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 1538.5 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 1711.1051 | 0 | 0 | 0 |  | 30_02 | 1538.5 | 0 | 0 | 0 | 0 | 1538.5 | 0 | 0 | 0 |  | 30_02 | 1653.838 | 0 | 0 | 0 | 0 | 1653.838 | 0 | 0 | 0
|  | 30_03 | Protection | 560.4 | 971.2211 | 410.8211 | 73.31% | E | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 560.4 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 971.2211 | 0 | 0 | 0 |  | 30_03 | 560.4 | 0 | 0 | 0 | 0 | 560.4 | 0 | 0 | 0 |  | 30_03 | 600 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 0
|  | 30_05 | Secondary Equipment | 152.25 | 58.3219 | -93.9281 | -61.69% | E | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 152.25 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 58.3219 | 0 | 0 | 0 |  | 30_04 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 |  | 30_04 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0
|  | 30_06 | Communications | 150 | 101.9375 | -48.0625 | -32.04% | E | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 101.9375 | 0 | 0 | 0 |  | 30_05 | 152.25 | 0 | 0 | 0 | 0 | 152.25 | 0 | 0 | 0 |  | 30_05 | 200 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0
|  | 30_07 | Line Materials | 590 | 762.3701 | 172.3701 | 29.22% | E | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 590 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 762.3701 | 0 | 0 | 0 |  | 30_06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30_06 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0
|  | 30_85 | SWN & OTA 'C' Cables & Post Commissioning | 0 | 107 | 107 | 'NA' | E | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 0 |  | 30_07 | 590 | 0 | 0 | 0 | 0 | 590 | 0 | 0 | 0 |  | 30_07 | 590 | 0 | 0 | 0 | 0 | 590 | 0 | 0 | 0
|  | 30_90 | Contingency | 303.6014 | 0 | -303.6014 | -100% | E | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 303.6014 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30_90 | 303.6 | 0 | 0 | 0 | 0 | 303.6 | 0 | 0 | 0 |  | 30_90 | 139 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0
#REF! | Enabling Works Construction | 40_01 | 110 kV Tie Line Deviation | 961.8 | 556.7672 | -405.0327 | -42.11% | B | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 961.8 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 556.7672 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_01 | 315 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_01 | 551 | 0 | 551 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40_02 | OTA - PEN C Deviation | 735 | 2436.7132 | 1701.7132 | 231.5% | B | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 2436.7132 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_02 | 2130 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_02 | 2366 | 0 | 2366 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40_03 | 220 kV Bay Tie Line 4 | 280 | 1037.4265 | 757.4265 | 270.5% | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0% | 0% | 19% | 81% | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 197.111 | 840.3154 | 0 | 0 | 0 | 0 |  | 40_03 | 661 | 0 | 0 | 125.59 | 535.41 | 0 | 0 | 0 | 0 |  | 40_03 | 844 | 0 | 0 | 160.36 | 683.64 | 0 | 0 | 0 | 0
|  | 40_04 | Tie Line 5 Cable Termination | 18.15 | 207.5695 | 189.4195 | 1044% | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 18.15 | 0 | 0 | 0 | 0 | 0% | 0% | 19% | 81% | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 39.4382 | 168.1313 | 0 | 0 | 0 | 0 |  | 40_04 | 23 | 0 | 0 | 4.37 | 18.63 | 0 | 0 | 0 | 0 |  | 40_04 | 34 | 0 | 0 | 6.46 | 27.54 | 0 | 0 | 0 | 0
|  | 40_05 | Southdown Cable Termination | 301.7 | 0 | -301.7 | -100% | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 301.7 | 0 | 0 | 0 | 0 | 0% | 0% | 19% | 81% | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_05 | 97 | 0 | 0 | 18.43 | 78.57 | 0 | 0 | 0 | 0 |  | 40_05 | 125 | 0 | 0 | 23.75 | 101.25 | 0 | 0 | 0 | 0
|  | 40_06 | OTA 'C' Bus Tie Cable Termination | 301.7 | 0 | -301.7 | -100% | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 301.7 | 0 | 0 | 0 | 0 | 0% | 0% | 19% | 81% | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_06 | 99 | 0 | 0 | 18.81 | 80.19 | 0 | 0 | 0 | 0 |  | 40_06 | 125 | 0 | 0 | 23.75 | 101.25 | 0 | 0 | 0 | 0
|  | 40_07 | 220 kV Bus Sections 478 & 488 | 211.6 | 939.3274 | 727.7274 | 343.9% | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 211.6 | 0 | 0 | 0 | 0 | 0% | 0% | 51% | 49% | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 479.0569 | 460.2704 | 0 | 0 | 0 | 0 |  | 40_07 | 285 | 0 | 0 | 145.35 | 139.65 | 0 | 0 | 0 | 0 |  | 40_07 | 365 | 0 | 0 | 186.15 | 178.85 | 0 | 0 | 0 | 0
|  | 40_08 | Henderson Circuit Transition Station | 357.85 | 713.3856 | 355.5356 | 99.35% | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 357.85 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 713.3856 | 0 | 0 | 0 | 0 |  | 40_08 | 507 | 0 | 0 | 0 | 507 | 0 | 0 | 0 | 0 |  | 40_08 | 596 | 0 | 0 | 0 | 596 | 0 | 0 | 0 | 0
|  | 40_09 | Southdown Circuit Transition Station | 189.65 | 0 | -189.65 | -100% | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 189.65 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_09 | 348 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 |  | 40_09 | 390 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0
|  | 40_10 | Huntly Circuit 2 Transition Station | 208.55 | 311.676 | 103.126 | 49.45% | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 208.55 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 311.676 | 0 | 0 | 0 | 0 |  | 40_10 | 208 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 |  | 40_10 | 245 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0
|  | 40_11 | Ohinewai (WKM3) Circuit Transition Station | 208.55 | 356.3269 | 147.7769 | 70.86% | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 208.55 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 356.3269 | 0 | 0 | 0 | 0 |  | 40_11 | 208 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 |  | 40_11 | 245 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0
|  | 40_12 | OTA 'C' Bus Tie Transition Station | 212.55 | 0 | -212.55 | -100% | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 212.55 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_12 | 221 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 |  | 40_12 | 258 | 0 | 0 | 0 | 258 | 0 | 0 | 0 | 0
|  | 40_13 | Earthing Connections | 16.2 | 22.1021 | 5.9021 | 36.43% | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 22.1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_13 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_13 | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40_14 | General Civil Works | 2441.9 | 7348.5325 | 4906.6325 | 200.9% | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 2441.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 7348.5325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_14 | 2881 | 2881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_14 | 6753 | 6753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40_15 | Communications/Protection Signalling | 47.2 | 319.1568 | 271.9568 | 576.2% | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 47.2 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 319.1568 | 0 | 0 | 0 | 0 | 0 |  | 40_15 | 69 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 |  | 40_15 | 53 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0
|  | 40_16 | Protection Systems | 1016 | 2372.7505 | 1356.7505 | 133.5% | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 1016 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 2372.7505 | 0 | 0 | 0 | 0 | 0 |  | 40_16 | 790 | 0 | 0 | 790 | 0 | 0 | 0 | 0 | 0 |  | 40_16 | 2540 | 0 | 0 | 2540 | 0 | 0 | 0 | 0 | 0
|  | 40_17 | SCADA Systems | 631.2 | 30.765 | -600.435 | -95.13% | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 631.2 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 30.765 | 0 | 0 | 0 | 0 | 0 |  | 40_17 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 |  | 40_17 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0
|  | 40_18 | AC Supply | 0 | 171.7076 | 171.7076 | 'NA' | C | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 171.7076 | 0 | 0 | 0 | 0 | 0 |  | 40_18 | 124 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | 0 |  | 40_18 | 159 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0
|  | 40_19 | Water Supply | 100 | 12 | -88 | -88% | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_19 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_19 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40_20 | Huntly Circuit 1 Relocation to Bay 502 | 0 | 101.6105 | 101.6105 | 'NA' | D | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 51% | 49% | 0% | 0% | 0% | 0% |  |  | 0 | 0 | 51.8214 | 49.7892 | 0 | 0 | 0 | 0 |  | 40_20 | 33 | 0 | 0 | 16.83 | 16.17 | 0 | 0 | 0 | 0 |  | 40_20 | 33 | 0 | 0 | 16.83 | 16.17 | 0 | 0 | 0 | 0
|  | 40_29 | Project Management | 781.84 | 2051.905 | 1270.065 | 162.4% |  | 30% | 20% | 25% | 25% | 0% | 0% | 0% | 0% | 0 |  | 234.552 | 156.368 | 195.46 | 195.46 | 0 | 0 | 0 | 0 | [10 empty] | 615.5715 | 410.381 | 512.9763 | 512.9763 | 0 | 0 | 0 | 0 |  | 40_29 | 1487 | 446.1 | 297.4 | 371.75 | 371.75 | 0 | 0 | 0 | 0 |  | 40_29 | 2017 | 605.1 | 403.4 | 504.25 | 504.25 | 0 | 0 | 0 | 0
|  | 40_30 | Vector Cable Relocation & LS Supply | 0 | 683.1757 | 683.1757 | 'NA' | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 683.1757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40_30 | 425 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40_31 | Overall Site Fencing/Security | 0 | 0 | 0 | 'NA' | A | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40_85 | SWN & OTA 'C' Cables & Post Commissioning | 0 | 2666.3882 | 2666.3882 | 'NA' |  | 15% | 0% | 15% | 70% | 0% | 0% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 399.9582 | 0 | 399.9582 | 1866.4717 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40_90 | Contingency | 898.3422 | 10 | -888.3422 | -98.89% |  | 30% | 20% | 25% | 25% | 0% | 0% | 0% | 0% | 0 |  | 269.5027 | 179.6684 | 224.5856 | 224.5856 | 0 | 0 | 0 | 0 | [10 empty] | 3 | 2 | 2.5 | 2.5 | 0 | 0 | 0 | 0 |  | 40_90 | 1891.62 | 567.486 | 378.324 | 472.905 | 472.905 | 0 | 0 | 0 | 0 |  | 40_90 | 1258 | 377.4 | 251.6 | 314.5 | 314.5 | 0 | 0 | 0 | 0
#REF! | GIS/AIS EHV Cable Design Build | 50_01 | MS1 Contract Agreement | 3411.7 | 3761.7275 | 350.0275 | 10.26% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 3411.7 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 3761.7275 | 0 | 0 |  | 50_01 | 132.375 | 0 | 0 | 0 | 0 | 0 | 132.375 | 0 | 0 |  | 50_01 | 3720.4 | 0 | 0 | 0 | 0 | 0 | 3720.4 | 0 | 0
|  | 50_02 | MS2 Plant & Bldg Design & Spec | 8331.1726 | 9396 | 1064.8274 | 12.78% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 8331.1726 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 9396 | 0 | 0 |  | 50_02 | 728.424 | 0 | 0 | 0 | 0 | 0 | 728.424 | 0 | 0 |  | 50_02 | 9085 | 0 | 0 | 0 | 0 | 0 | 9085 | 0 | 0
|  | 50_03 | MS3 Factory Test Reports | 1978.665 | 2271.2882 | 292.6232 | 14.79% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 1978.665 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 2271.2882 | 0 | 0 |  | 50_03 | 182.106 | 0 | 0 | 0 | 0 | 0 | 182.106 | 0 | 0 |  | 50_03 | 2157.7 | 0 | 0 | 0 | 0 | 0 | 2157.7 | 0 | 0
|  | 50_04 | MS4 Civil Works | 8824.1653 | 10075.7792 | 1251.614 | 14.18% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 8824.1653 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 10075.7792 | 0 | 0 |  | 50_04 | 539.197 | 0 | 0 | 0 | 0 | 0 | 539.197 | 0 | 0 |  | 50_04 | 9622.6 | 0 | 0 | 0 | 0 | 0 | 9622.6 | 0 | 0
|  | 50_05 | MS5 AIS Substation Plant | 2446.9896 | 2734.0335 | 287.0439 | 11.73% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 2446.9896 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 2734.0335 | 0 | 0 |  | 50_05 | 17634.665 | 0 | 0 | 0 | 0 | 0 | 17634.665 | 0 | 0 |  | 50_05 | 2668.4 | 0 | 0 | 0 | 0 | 0 | 2668.4 | 0 | 0
|  | 50_06 | MS6 GIS Substation Plant | 6902.0807 | 7518.5498 | 616.469 | 8.932% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 6902.0807 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 7518.5498 | 0 | 0 |  | 50_06 | 671.84 | 0 | 0 | 0 | 0 | 0 | 671.84 | 0 | 0 |  | 50_06 | 7526.6 | 0 | 0 | 0 | 0 | 0 | 7526.6 | 0 | 0
|  | 50_07 | MS7 220 kV Cables & Accessories | 6918.4038 | 5862.4173 | -1055.9865 | -15.26% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 6918.4038 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 5862.4173 | 0 | 0 |  | 50_07 | 5431.348 | 0 | 0 | 0 | 0 | 0 | 5431.348 | 0 | 0 |  | 50_07 | 7544.4 | 0 | 0 | 0 | 0 | 0 | 7544.4 | 0 | 0
|  | 50_08 | MS8 Substation Installation | 2472.9415 | 2559.3579 | 86.4164 | 3.494% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 2472.9415 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 2559.3579 | 0 | 0 |  | 50_08 | 5363.8678 | 0 | 0 | 0 | 0 | 0 | 5363.8678 | 0 | 0 |  | 50_08 | 2696.7 | 0 | 0 | 0 | 0 | 0 | 2696.7 | 0 | 0
|  | 50_09 | MS9 220 kV Cables Installation | 2474.1336 | 1669 | -805.1336 | -32.54% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 2474.1336 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1669 | 0 | 0 |  | 50_09 | 13345.53 | 0 | 0 | 0 | 0 | 0 | 13345.53 | 0 | 0 |  | 50_09 | 2698 | 0 | 0 | 0 | 0 | 0 | 2698 | 0 | 0
|  | 50_10 | MS10 O&M Manuals & Training | 486.4818 | 549.1529 | 62.6711 | 12.88% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 486.4818 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 549.1529 | 0 | 0 |  | 50_10 | 5575.375 | 0 | 0 | 0 | 0 | 0 | 5575.375 | 0 | 0 |  | 50_10 | 530.5 | 0 | 0 | 0 | 0 | 0 | 530.5 | 0 | 0
|  | 50_11 | MS11 Taking Over Certificate | 2252.3969 | 2576.8087 | 324.4118 | 14.4% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 2252.3969 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 2576.8087 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50_11 | 2456.2 | 0 | 0 | 0 | 0 | 0 | 2456.2 | 0 | 0
|  | 50_12 | MS12 Contract Closeout | 2479.3606 | 2901 | 421.6394 | 17.01% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 2479.3606 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 2901 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50_12 | 2703.7 | 0 | 0 | 0 | 0 | 0 | 2703.7 | 0 | 0
|  | 50_13 | MS13 Tests After Commissioning | 91.7025 | 100 | 8.2975 | 9.048% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 91.7025 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50_13 | 100 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0
|  | 50_14 | Cable Test Set | 534.5339 | 0 | -534.5339 | -100% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 534.5339 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50_14 | 582.9 | 0 | 0 | 0 | 0 | 0 | 582.9 | 0 | 0
|  | 50_15 | Variations | 0 | 3534 | 3534 | 'NA' | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 3534 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50_15 | 3431 | 0 | 0 | 0 | 0 | 0 | 3431 | 0 | 0
|  | 50_85 | SWN & OTA 'C' Cables & Post Commissioning | 0 | 3015.1 | 3015.1 | 'NA' | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 3015.1 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 50_90 | Contingency | 4950.24 | 10 | -4940.24 | -99.8% | F | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 4950.24 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 |  | 50_90 | 3271.8061 | 0 | 0 | 0 | 0 | 0 | 3271.8061 | 0 | 0 |  | 50_90 | 2443 | 0 | 0 | 0 | 0 | 0 | 2443 | 0 | 0
70 | Land Easement |  | Land Easement | 0 | 1200 | 1200 | 'NA' | G | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#REF! | Capitalised Interest | 80_00 | Capitalised Interest | 3203.27 | 6914.2827 | 3711.0127 | 115.9% | H | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3203.27 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6914.2827 |  | 80_00 | 4939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4939 |  | 80_00 | 7778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7778
[19 empty] | 3528.1275 | 2352.1767 | 2807.4272 | 3170.0936 | 3386.0423 | 58163.9448 | 0 | 3203.27 | [9 empty] | 76611.082 | 11000.8935 | 4193.2277 | 7669.9265 | 7068.0213 | 3904.181 | 64198.6644 | 1200 | 6914.2827 | 106149.1971 |  | 78075.5589 | 4935.2653 | 3436.1053 | 3177.8228 | 3758.5821 | 3373.7329 | 54455.0505 | 0 | 4939 | 0 |  | 96790.266 | 9658.4594 | 4021.3664 | 5380.5492 | 4384.2359 | 3487.654 | 62080.0011 | 0 | 7778 | 0
|  |  | TOTAL | 76611.082 | 106149.1971 | 29538.1151 | 38.56%
|  |  | Check | 0 | [13 empty] | Share | 4.605% | 3.07% | 3.665% | 4.138% | 4.42% | 75.92% | 0% | 4.181% | [10 empty] | 10.36% | 3.95% | 7.226% | 6.659% | 3.678% | 60.48% | 1.13% | 6.514% | 100%
|  |  | For copying into Com Com application | [14 empty] | Share for 1 to many only | 3.957% | 3.098% | 3.039% | 2.949% | 4.76% | 77.64% | 0% | 4.559% | [10 empty] | 9.709% | 4.75% | 5.135% | 3.022% | 4.142% | 64.32% | 1.319% | 7.599%
|  | ID | Overspend Category | PAD Budget | Actual | Variance | Percent Change
|  | A | Enabling Works Civil General | 3.5281 | 11.0009 | 7.4728 | 211.8%
|  | B | Transmission Line Deviations | 2.3522 | 4.1932 | 1.8411 | 78.27%
|  | C | Enabling Works Secondary Equipment Design & Install | 2.8074 | 7.6699 | 4.8625 | 173.2%
|  | D | EW Transition Station & Cable Termination Design & Install | 3.1701 | 7.068 | 3.8979 | 123%
|  | E | Enabling Works Procurement | 3.386 | 3.9042 | 0.51814 | 15.3%
|  | F | Design Build GIS/AIS & EHV Cable | 58.1639 | 64.1987 | 6.0347 | 10.38%
|  | G | Land Easement | 0 | 1.2 | 1.2 | 'NA'
|  | H | Interest During Construction | 3.2033 | 6.9143 | 3.711 | 115.9%
|  |  | TOTAL | 76.6111 | 106.1492 | 29.5381 | 38.56%
|  |  | Enabling Works Design & Install Subtotal | 11.8578 | 29.9321 | 18.0742 | 152.4%
|  |  | EW Procure & DB Works Subtotal | 61.55 | 68.1028 | 6.5529 | 10.65%
|  | D | EW Transition Station & Cable Termination Design & Install | Breakdown by Item - Core EW Construction Only |  |  |  |  | Work Package to Overspend Category Map - PAD Budget G: Transfer Secondary systems contract costs from final D to C categories for amounts below and adjust for current forecast
|  | C | Cable Terminations | 901.55 | 1607.9959 |  |  | 363 | Work Package to Overspend Category Map - PAD Budget A: Incl $742k as initially journalled to 40_85 minus $379k transferred to Cat; Work Package to Overspend Category Map - PAD Budget G: 379
|  | T | Transition Stations | 1177.15 | 2947.6925 |  |  | 85% SWN-OTC excl amount journalled to 40_85 | Work Package to Overspend Category Map - PAD Budget G: 0
|  | S | AIS Switchyard Works | 211.6 | 737.8645 |  |  | -534 | Work Package to Overspend Category Map - PAD Budget A: Excl $534 transferred to Cat C and 15% SWN-OTC excl amount journalled to 40_85; Work Package to Overspend Category Map - PAD Budget G: 534
|  |  |  | 2290.3 | 5293.5529
|  |  | Category total - prorated by item below | 3170.0936 | 7068.0213 |  |  | 1.3352 | Work Package to Overspend Category Map - PAD Budget A: Factor to incl design,& TSL & TP PM etc final
|  | C | Cable Terminations | 1247.8705 | 2147.0173 |  |  | 1.3841 | Work Package to Overspend Category Map - PAD Budget A: Factor to incl design,& TSL & TP PM etc actual
|  | T | Transition Stations | 1629.3393 | 3935.7977
|  | S | AIS Switchyard Works | 292.8838 | 985.2063
|  |  | Zero Check | 0 | 0
Note on L93: oakdeng: 19% of $742k journalled from _05 and _06 should be against C rather than D
Note on L89: oakdeng: 51% of actual is against category C as adjusted
Note on L76: oakdeng: 51% of actual is against category C as adjusted
Note on L75: oakdeng: 19% of actual is against category C as adjusted
Note on L74: oakdeng: 19% of actual is against category C as adjusted
Note on L73: oakdeng: 19% of actual is against category C as adjusted
Note on L72: oakdeng: 19% of actual is against category C as adjusted
Note on BK52: oakdeng: Includes 20_13 & 14
Note on AZ52: oakdeng: Includes 20_13 & 14.
Note on AF21: oakdeng: Assessed based upon actual relative effort - more EW than DB
Note on BE19: Sef Truyens: 1200 is the easement cost
Note on E39: Sef Truyens: WP 20_18 has been included
Note on E50: Kim Bannon: included in 20_05
Note on E66: Graeme Oakden: includes the 30_04 Scada
Note on F66: Graeme Oakden: Add $150k for SCADA consolidated with 30_06 (was 30_04). 9/09
Note on F112: Graeme Oakden:
Note on B95: Graeme Oakden: 6/08 Revised WBS from price schedules to the 13 major milestones plus Test Set. Calculate Budget pro rata from contract price of total original PAD budget of $49.605M. Could do more accurately by mapping from PAD budget against MS categories.

## CA Level
Otahuhu Overspend - PAD Budget
This is a formatted and transposed version of the worksheet "UR-Summary PAD"
CO | CA | Workstream / Work Package Description | PAD Budget ($,000)
10_00 |  | Management/Support
| 10_10 | Project Management | 3381.661
| 10_20 | Transpower Technical Support | 354.8841
| 10_30 | External Technical Support | 287.5545
| 10_40 | RMA | 32.972
| 10_50 | Property | 24.729
| 10_60 | Switching | 60.1
| 10_90 | Conitingency | 426.4248
|  | Subtotal | 4568.3253
20_00 |  | Enabling Works Design
| 20_01 | 110 kV Tie Line Deviation | 104.96
| 20_02 | OTA - PEN C Deviation | 94.9
| 20_03 | Warehouse Relocation/Alteration | 36.52
| 20_04 | Manhole and Contact Sewer Relocation | 12.5
| 20_05 | Site Platform Formation and Stormwater Relocation | 63.03
| 20_06 | 220 kV Switchyard Extensions | 101.31
| 20_07 | 220 kV Bus Zone Protection Modifications | 157.3
| 20_08 | 220 kV Protection System | 225
| 20_09 | Cable Transition Stations | 61.6
| 20_10 | Communications | 0
| 20_11 | SCADA | 58.72
| 20_12 | Local Service Power Supplies | 0
| 20_13 | Security System | 0
| 20_14 | Station Lighting | 0
| 20_15 | Earthgrid Connections | 0.81
| 20_16 | Sewerage Connection | 0
| 20_17 | Water Supply | 5
| 20_18 | Roading | 3.45
| 20_19 | Vector Cable Relocation | 0
| 20_20 | Miscellaneous Site Works | 0
| 20_21 | Cable Route Security | 0
| 20_90 | Contingency | 94.8853
|  | Subtotal | 1019.9853
30_00 |  | Procurement
| 30_01 | Miscellaneous | 50
| 30_02 | Primary Equipment | 1538.5
| 30_03 | Protection | 560.4
| 30_04 | SCADA | 150
| 30_05 | Secondary Equipment | 152.25
| 30_06 | Communications | 0
| 30_07 | Lines Materials | 590
| 30_90 | Contingency | 303.6014
|  | Subtotal | 3344.7514
40_00 |  | Enabling Works Construction
| 40_01 | 110 kV Tie Line Deviation | 961.8
| 40_02 | OTA - PEN C Deviation | 735
| 40_03 | 220 kV Bay Tie Line 4 | 280
| 40_04 | Tie Line 5 Cable Termination | 18.15
| 40_05 | Southdown Cable Termination | 301.7
| 40_06 | OTA 'C' Bus Tie Cable Termination | 301.7
| 40_07 | 220 kV Bus Sections 478 & 488 | 211.6
| 40_08 | Henderson Circuit Transition Station | 357.85
| 40_09 | Southdown Circuit Transition Station | 189.65
| 40_10 | Huntly Circuit 2 Transition Station | 208.55
| 40_11 | Ohinewai (WKM3) Circuit Transition Station | 208.55
| 40_12 | OTA 'C' Bus Tie Transition Station | 212.55
| 40_13 | Earthing Connections | 16.2
| 40_14 | General Civil Works | 2441.9
| 40_15 | Communications/Protection Signalling | 47.2
| 40_16 | Protection Systems | 1016
| 40_17 | SCADA Systems | 631.2
| 40_18 | AC Supply | 0
| 40_19 | Water Supply | 100
| 40_20 | Huntly Circuit 1 Relocation to Bay 502 | 0
| 40_29 | Project Management | 781.84
| 40_90 | Contingency | 898.3422
|  | Subtotal | 9919.7822
50_00 |  | GIS/AIS EHV Cable Design Build
| 50_01 | Documentation & Training | 132.375
| 50_02 | Spares | 728.424
| 50_03 | Special Tools and Maintenance Equipment | 182.106
| 50_04 | Temporary Works | 539.197
| 50_05 | Substation Primary Plant Supply | 17634.665
| 50_06 | Substation Secondary Plant Supply | 671.84
| 50_07 | Substation Site Works and Building | 5431.348
| 50_08 | Substation Plant Installlation and Testing | 5363.8678
| 50_09 | Cable Manufacture, Test and Delivery | 13345.53
| 50_10 | Cable Installation and Commisioning | 5575.375
| 50_90 | Contingency | 4950.2363
|  | Subtotal | 54554.9641
80_00 | 80_00 | Capitalised Interest | 3203.27
|  | TOTAL | 76611.0783
50_00 |  | GIS/AIS EHV Cable Design Build (new WBS)
| 50_01 | MS1 Contract Agreement | 3411.7
| 50_02 | MS2 Plant & Bldg Design & Spec | 8331.1726
| 50_03 | MS3 Factory Test Reports | 1978.665
| 50_04 | MS4 Civil Works | 8824.1653
| 50_05 | MS5 AIS Substation Plant | 2446.9896
| 50_06 | MS6 GIS Substation Plant | 6902.0807
| 50_07 | MS7 220 kV Cables & Accessories | 6918.4038
| 50_08 | MS8 Substation Installation | 2472.9415
| 50_09 | MS9 220 kV Cables Installation | 2474.1336
| 50_10 | MS10 O&M Manuals & Training | 486.4818
| 50_11 | MS11 Taking Over Certificate | 2252.3969
| 50_12 | MS12 Contract Closeout | 2479.3606
| 50_13 | MS13 Tests After Commissioning | 91.7025
| 50_14 | Cable Test Set | 534.5339
| 50_15 | Variations | 0
| 50_85 | SWN & OTA 'C' Cables & Post Commissioning | 0
| 50_90 | Contingency | 4950.24
|  | Subtotal | 54554.9678
|  | TOTAL | 76611.082

## UR-Summary PAD
Otahuhu 220 kV diversity
PAD Budget showing original breakdown
Work Package (CA) ID and Name
[15 empty] | Total | 10_10 | 10_20 | 10_30 | 10_40 | 10_50 | 10_60 | 10_90 | 20_01 | 20_02 | 20_03 | 20_04 | 20_05 | 20_06 | 20_07 | 20_08 | 20_09 | 20_10 | 20_11 | 20_12 | 20_13 | 20_14 | 20_15 | 20_16 | 20_17 | 20_18 | 20_19 | 20_20 | 20_21 | 20_90 | 30_01 | 30_02 | 30_03 | 30_04 | 30_05 | 30_06 | 30_07 | 30_90 | 40_01 | 40_02 | 40_03 | 40_04 | 40_05 | 40_06 | 40_07 | 40_08 | 40_09 | 40_10 | 40_11 | 40_12 | 40_13 | 40_14 | 40_15 | 40_16 | 40_17 | 40_18 | 40_19 | 40_20 | 40_29 | 40_90 | 50_01 | 50_02 | 50_03 | 50_04 | 50_05 | 50_06 | 50_07 | 50_08 | 50_09 | 50_10 | 50_90 | 80_00
|  | Totals $000's | 220kV Cable | 220 kV GIS and AIS Switchyard | 220 kV AIS Switchyard (Enabling Works) | Enabling Works - 110 kV Tie Line 1 and 2 | Enabling Works OTA - PEN C | General Civil works (Enabling Works) | OTA - Henderson 220 kV Transition Station | OTA - C - Transition Station | OTA - Southdown 220 kV Transition Station | OTA - Ohinewai 220 kV Transition Station | OTA - Huntly 220 kV Transition Station |  |  | Project Management | Transpower Technical Support | External Technical Support | RMA | Property | Switching | Conitingency | 110 kV Tie Line Deviation | OTA - PEN C Deviation | Warehouse Relocation/Alteration | Manhole and Contact Sewer Relocation | Site Platform Formation and Stormwater Relocation | 220 kV Switchyard Extensions | 220 kV Bus Zone Protection Modifications | 220 kV Protection System | Cable Transition Stations | Communications | SCADA | Local Service Power Supplies | Security System | Station Lighting | Earthgrid Connections | Sewerage Connection | Water Supply | Roading | Vector Cable Relocation | Miscellaneous Site Works | Cable Route Security | Contingency | Miscellaneous | Primary Equipment | Protection | SCADA | Secondary Equipment | Communications | Lines Materials | Contingency | 110 kV Tie Line Deviation | OTA - PEN C Deviation | 220 kV Bay Tie Line 4 | Tie Line 5 Cable Termination | Southdown Cable Termination | OTA 'C' Bus Tie Cable Termination | 220 kV Bus Sections 478 & 488 | Henderson Circuit Transition Station | Southdown Circuit Transition Station | Huntly Circuit 2 Transition Station | Ohinewai (WKM3) Circuit Transition Station | OTA 'C' Bus Tie Transition Station | Earthing Connections | General Civil Works | Communications/Protection Signalling | Protection Systems | SCADA Systems | AC Supply | Water Supply | Huntly Circuit 1 Relocation to Bay 502 | Project Management | Contingency | Documentation & Training | Spares | Special Tools and Maintenance Equipment | Temporary Works | Substation Primary Plant Supply | Substation Secondary Plant Supply | Substation Site Works and Building | Substation Plant Installlation and Testing | Cable Manufacture, Test and Delivery | Cable Installation and Commisioning | Contingency | Capitalised Interest
|  | Totals $000's |  | Totals $000's | Totals $000's | Totals $000's | Totals $000's | Totals $000's | Totals $000's | Totals $000's | Totals $000's | Totals $000's | Totals $000's
[14 empty] | 0. 220 kV Cable | 23065.0959 | 1159.1 | 5.7605 | 5.7605 | 0 | 0 | 0 | 120.5502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13345.53 | 5575.375 | 1888.6198 | 964.4
Line Materials |  | 2549.792 |  | 0 | 0 | 1111.462 | 1438.33 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Enabling Works 110 kV Tie Lines | 2133.3683 | 142.48 | 12.0083 | 0 | 0 | 0 | 8.6 | 16.7247 | 104.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.1498 | 0 | 369 | 0 | 0 | 0 | 0 | 160 | 52.0324 | 961.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.49 | 105.9231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2
Buildings |  | 5187.99 |  | 4144.73 | 0 | 0 | 0 | 1043.26 | 0 | 0 | 0 | 0 | 0 | 2. Enabling Wks OTA-PEN C | 1679.65 | 111.5 | 12 | 0 | 0 | 0 | 8.6 | 13.1679 | 0 | 94.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7786 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 42.4299 | 0 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.11 | 81.9336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.23
Civil Works (Bulk excavation, earth grid, fences, roads etc) |  | 6672.8268 | 2339.68 | 1358.1825 | 485.0534 | 0 | 0 | 2037.87 | 141.995 | 79.989 | 79.989 | 75.034 | 75.034 | 3. Enabling Works - General Civil | 3537.13 | 107.159 | 0 | 0 | 32.972 | 24.729 | 0 | 15.4055 | 0 | 0 | 36.52 | 12.5 | 62.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3.45 | 0 | 0 | 0 | 12.3244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2436.1 | 0 | 0 | 0 | 0 | 100 | 0 | 259.96 | 280.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.89
Primary Equipment |  | 28557.1527 |  | 24210.1364 | 2388.1636 | 707.6163 | 0 | 0 | 358.4105 | 245.018 | 157.772 | 245.018 | 245.018 | 4. Henderson Transition | 600.403 | 41.22 | 5.613 | 0 | 0 | 0 | 1.7 | 4.7079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5693 | 0 | 68.9 | 0 | 0 | 5.25 | 0 | 0 | 7.3234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.31 | 38.7094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.11
220 kV Cables |  | 17752.0009 | 17752.0009 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 5. Southdown Transition | 298.8785 | 20.37 | 2.4285 | 0 | 0 | 0 | 1.7 | 2.3436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0416 | 0 | 17.7 | 0 | 0 | 5.25 | 0 | 0 | 2.3436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.69 | 20.3112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5
Protection |  | 3403.0815 |  | 1200.3672 | 2159.2743 | 28.96 | 14.48 | 0 | 0 | 0 | 0 | 0 | 0 | 6. Huntly Transition | 393.3495 | 27.03 | 3.9495 | 0 | 0 | 0 | 1.7 | 3.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0281 | 0 | 68.9 | 0 | 0 | 5.25 | 0 | 0 | 7.5394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.68 | 22.2755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.45
SCADA |  | 923.175 |  | 0 | 923.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7. Ohinewai Transition | 393.3495 | 27.03 | 3.9495 | 0 | 0 | 0 | 1.7 | 3.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0281 | 0 | 68.9 | 0 | 0 | 5.25 | 0 | 0 | 7.5394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.68 | 22.2755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.45
Secondary Equipment |  | 974.0516 |  | 522.4659 | 348.3982 | 0 | 0 | 0 | 20.6375 | 20.6375 | 20.6375 | 20.6375 | 20.6375 | 8. OTA C Transition | 399.0445 | 27.41 | 3.9645 | 0 | 0 | 0 | 1.7 | 3.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0431 | 0 | 68.9 | 0 | 0 | 5.25 | 0 | 0 | 7.3017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.04 | 22.9482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.69
Communications |  | 643.47 |  | 643.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9. Stations AIS EW | 7260.6544 | 473.22 | 11.9244 | 0 | 0 | 0 | 17.2 | 50.5976 | 0 | 0 | 0 | 0 | 0.29 | 101.31 | 157.3 | 225 | 0 | 0 | 58.72 | 0 | 0 | 0 | 0.81 | 0 | 0 | 0 | 0 | 0 | 0 | 56.9223 | 50 | 876.2 | 560.4 | 150 | 126 | 0 | 0 | 177.0916 | 0 | 0 | 280 | 18.15 | 301.7 | 301.7 | 211.6 | 0 | 0 | 0 | 0 | 0 | 16.2 | 5.8 | 47.2 | 1016 | 631.2 | 0 | 0 | 0 | 263.12 | 303.5856 | 0 | 0 | 0 | 0 | 0 | 0 | 423.56 | 0 | 0 | 0 | 44.2729 | 303.58
Land |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10. Stations GIS | 36850.1547 | 1245.142 | 293.2859 | 281.794 | 0 | 0 | 17.2 | 192.5964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.76 | 0 | 132.375 | 728.424 | 182.106 | 539.197 | 17634.665 | 671.84 | 5007.788 | 5363.8678 | 0 | 0 | 3017.3436 | 1540.77
Switching Costs |  | 71.47 |  | 20.08 | 20.59 | 10.3 | 10.3 | 0 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04
[14 empty] | TOTAL | 76611.0783 | 3381.661 | 354.8841 | 287.5545 | 32.972 | 24.729 | 60.1 | 426.4248 | 104.96 | 94.9 | 36.52 | 12.5 | 63.03 | 101.31 | 157.3 | 225 | 61.6 | 0 | 58.72 | 0 | 0 | 0 | 0.81 | 0 | 5 | 3.45 | 0 | 0 | 0 | 94.8853 | 50 | 1538.5 | 560.4 | 150 | 152.25 | 0 | 590 | 303.6014 | 961.8 | 735 | 280 | 18.15 | 301.7 | 301.7 | 211.6 | 357.85 | 189.65 | 208.55 | 208.55 | 212.55 | 16.2 | 2441.9 | 47.2 | 1016 | 631.2 | 0 | 100 | 0 | 781.84 | 898.3422 | 132.375 | 728.424 | 182.106 | 539.197 | 17634.665 | 671.84 | 5431.348 | 5363.8678 | 13345.53 | 5575.375 | 4950.2363 | 3203.27
Sub Total |  | 66735.0105 | 20091.6809 | 32099.4319 | 6324.6544 | 1858.3383 | 1463.11 | 3081.13 | 523.083 | 347.6845 | 260.4385 | 342.7295 | 342.7295
Interest during construction | 4.8% | 3203.2805 | 964.4007 | 1540.7727 | 303.5834 | 89.2002 | 70.2293 | 147.8942 | 25.108 | 16.6889 | 12.501 | 16.451 | 16.451
Contingency | 10% | 6673.5011 | 2009.1681 | 3209.9432 | 632.4654 | 185.8338 | 146.311 | 308.113 | 52.3083 | 34.7685 | 26.0439 | 34.273 | 34.273
Total Estimated Cost |  | 76611.7921 | 23065.2497 | 36850.1478 | 7260.7033 | 2133.3724 | 1679.6503 | 3537.1372 | 600.4993 | 399.1418 | 298.9834 | 393.4535 | 393.4535

## Actual Breakdown
Source: Transfield records
Overspend Category | Sub-category |  | Man hour | Plant/ | Total | Agreed Values SR/ Var | Total new price= (old + change) $
A | B | Demolish the existing Warehouse Nissin Huts and liaise with Transpower's representative to transport the dismantled building to secure storage location on site | 1690 | 17216 | 18906 | -18906 | 0
A | B | Demolish and remove existing Warehouse Nissin Huts foundations and services. | 0 | 9328 | 9328 | -9328 | 0
A | B | Carefully dismantle the existing 'K' shed and liaise with Transpower's representative to transport the dismantled building to secure storage location on site | 4224 | 104338 | 108562 | 2850.07 | 111412.07
A | B | Dismantle the existing 'K' shed foundations and services | 0 | 17755 | 17755 | 0 | 17755
A | B | Construct 15 m wide lean-to extension to three sides of exisiting "Benmore" shed | 0 | 406430 | 406430 | 321715.058 | 728145.058
A | B | Contractor to Specify (Remove concrete foundations TP Store metalled area) | 0 | 16960 | 16960 | 0 | 16960
A | B | Clear a K shed lay down area in the Transpower Steel yard - Nikau Contractors Ltd. Please refer to CQ 007. |  |  |  | 3490.96 | 3490.96
A | B | Additional column and grid for the Benmore Lean-to as per TP64637_0_3 & TP64635_0_4 vis ODP-PF-570 (Lean to fill-in section) T&C price = $2,541.36 (with TSL contract mark-up) United price = $4,370.42 (with TSL contract mark-up) |  |  |  | 7111.92 | 7111.92
A | B | Benmore shed power supply outlet and shifting of the roller door MCB as requested by Dick Harris (included replacing already blown fuses to other power outlets) Materials = $314.34 (includes PDL socket, conduit, fuses, etc) Labour @ $52.52/hr (including TSL overheads & profit mark-up) for 8 hours = $420.15 Total = $734.5 |  |  |  | 734.4862 | 734.4862
A | B | ODP-PF-637 (Revised drawings issued to relocate the column away from the existing roller door at the end of the Benmore shed) Tunnel & Civil: Locally widen excavation by hand for the new footing. Re-survey, dismantle reinforcing from old location and re-tie around exiting tie beam steel Total cost $700 + GST (including TSL margin) |  |  |  | 699.9405 | 699.9405
A | B | Price for works undertaken to construct a triangular concrete infill near the K Shed slab Break out and remove cast in situ nib $2,653.00 Supply and place 50mm GAP40 metal (3m3) = $282.00 Supply and place 200mm concrete with one layer of reinforcing mesh (30m2) = $3,816.00 Total = $6,751.00 |  |  |  | 6751 | 6751
A | B | Tunnel & Civil's variation to fill in the concrete bund area around the Benmore Shed (as per ODP-FP-337): - Subgrade preparation (approx 62 sq.m @ $49.30) $3,056 - Supply, drill & epoxy dowels including debonding (approx 310 No. @ $14.86) $4,606 - Supply and Lay 666 mesh (approx 62sq.m. @ $23.76) $1,473 - Place and finish concrete 150mm thick (approx 62 sq.m. @ $89.43) $5,545 TOTAL $14,680 (excluding TSL margin) Tunnel & Civil's variation for the bund nib wall and associated ramps (ODP-FP-346): Construct bund wall to RL 0.03 Grid Lines E, 11, A: 91.8m $18,497 Construct bund wall to RL 0.03 Grid Line 6 after building works $4,067 Ramp on Grid E: 5m wide as per sketch attached $9,399 Ramp on Grid 6: 5m wide as per sketch attached $6,958 TOTAL $38,921 (excluding TSL margin) Total = $60,220.72 (including TSL margin) |  |  |  | 61221.4435 | 61221.4435
A | B | Stonedale Relocate fire hose at Transpower stores to allow them to knock down the wooden carport $558.38 (charged at day rates) Invoice attached |  |  |  | 558.38 | 558.38
A | B | Temporary works site demarcation fencing (orange mesh safety fencing) ≈ 380m @ $12/m as per attached sketch (Safety fence for along the platform kerb and channel parallel with the k-shed slab [165m], around the HEN TS [92m] and along Hellabys Road for open excavations [128m]) Total = $4,560.00 |  |  |  | 4560 | 4560
A | B | Benmore shed variations - United Engineering Benmore 5 - Variation for installation of translucent sheeting Wall Cladding to Line A & B (Clarification of wall cladding not in original scope of work as per email 9/4/09 - ODP-CQ-157) Total = $15,200.96 Benmore 6 - Variation for installation of footing flashing and timber at bottom of wall cladding as detailed to top of the plinth (Clarification of wall cladding footing not in original scope of work as per email 8/4/09) Total = $5,536.61 Benmore 7 - Variation to install timber to facilitate hip roofing (No support structure detailed for fixing of roof cladding to hip rafter line 10B to 11A. Not in original scope of work as per U.E email 3/4/09 item 8) Total = $3,828.66 Benmore 9 - External gutter changed from original quotation (Not part of original scope of work quoted ) Total = $5,543.35 Benmore 10 - Construct internal guttering, including timberwork to facilitate 1.5mm black butynol membrane (Not part of the original scope of work quoted) Total = $17,039.00 Grand total = $47,148.58 Invoices attached |  |  |  | 47749.0068 | 47749.0068
A | B | Benmore shed sprinkler work (OPUS) submitted and approved under ODPFP-457 Total = $6,830.43 |  |  |  | 6930.5024 | 6930.5024
A | B | Remaining Benmore shed lean-to variations submitted and approved under ODP-FP-472 Benmore shed lean-to variations from united Engineering as submitted under ODP-FP-472: Variation #2 = $123.59 Variation #3 = $1,881.86 Variation #4 = $915.65 Variation #8 = $4,370.42 Total = $7,291.52 United variation pricing attached as per ODP-FP-472 |  |  |  | 7791.8738 | 7791.8738
A | B | T&C roller door weather seal price as submitted and approved under ODP-FP-480 We submit our price for the roller door weather seal detail as per sketch provided. Construct revised roller door bund detail to the 2 roller doors on grid A (between grids 10 & 11) and for the roller door on grid 11 (between grids A & B). New bund detail at 3 roller door locations = $3,058 Less original allowance for blockwork bund 5.76 sq.m. @ $281.80 = $1,623 Extra over cost for revised bund detail = $1,435 ($478 each) [excluding TSL margin] The roller door bund on grid E will not be constructed in blockwork but the same detail will be incorporated into the concrete insitu ramp at this location at no additional cost. Total = $1,612.22 |  |  |  | 1812.366 | 1812.366
A | B | Benmore Shed lean-to door jamb plinths as submitted and approved under ODP-FP-479 We submit our price for the roller door jamb plinths as detailed below: To construct 6 No. Plinths as per sketch provided @ $528 each = $3,168 (excl TSL margin) Base plate grouting (if you require us to do it) 6 No. @$45 each = $270 (excl TSL margin) This price is for the door jambs for the 2 roller doors on grid A (between grids 10 & 11) and for the roller door on grid 11 (between grids A & B). We note the roller door on grid E does not require any door jamb plinths. Total = $3,862.59 |  |  |  | 4062.7365 | 4062.7365
A | B | Removal of lights and aerials and other fittings to enable installation of the internal gutter., Benmore shed |  |  |  | 11398.44 | 11398.44
A | B | To undertake changes to the Benmore Shed Lean to cladding and roofing installations following operational handover to Transpower by TSL Subcontractor (United Engineering). This variation covers site visits by TSL PM for changes to the gutter brackets, rainheads plus capping on extended bund wall plus supply of operator to operate knuckle boom for Aecom Engineer inspection |  |  |  | 27161.24 | 27161.24
A | B | Tunnel & Civil variation for the additional bund wall grid A bay 5-6 (Benmore Shed) Total = $774.17 |  |  |  | 774.1717 | 774.1717
A | B | Benmore Shed lean-to additional roller door connections To run cable through new Benmore shed lean-to at high level then drop down at Northern Corner [NNE & NE] between GL 10 & 11 on GL A and GL A & B on GL 11 for additional roller door controllers. Includes supply of isolator and raise / lower electrical box however excludes supply of limit switches as these were supplied by United Engineering. Variation covers wiring to and connection of 2 additional roller doors [ refer TP 64649 rev 1 issued for construction 30th March 2009] setting of limit switches plus supply of associated electrical equipment. |  |  |  | 13779.062 | 13779.062
A | B | Tunnel & Civil's cost to fit temp gutter and downpipe at GIS Building to ensure that the new concrete driveway was not damaged. |  |  |  | 1939.482 | 1939.482
A | E | Connect new AIS earthgrid to the existing substation earthgrid. | 5528 | 32067 | 37595 | -15493.01 | 22101.99
A | E | Construct sedimentation control system for earthworks | 0 | 36100 | 36100 | 12804.72 | 48904.72
A | E | Maintain sedimentation control system | 0 | 2800 | 2800 | 7269.6 | 10069.6
A | E | Clear site and remove vegetation and trees, incl 2xPhoenix palms in Hellabys rd, and grove of trees in Substation rd at WKM3 Transition station location. | 0 | 7700 | 7700 | 1892.1 | 9592.1
A | E | Construct temporary fencing | 0 | 150000 | 150000 | -95100 | 54900
A | E | Strip top soil | 0 | 24000 | 24000 | 26848 | 50848
A | E | Construct earth bund | 0 | 2400 | 2400 | 0 | 2400
A | E | Stockpile topsoil on site for reuse (150mm depth) | 0 | 18810 | 18810 | 0 | 18810
A | E | Dispose of surplus topsoil off site | 0 | 19500 | 19500 | -19500 | 0
A | E | New AIS and GIS substation platform cut to fill | 0 | 28500 | 28500 | 0 | 28500
A | E | New AIS and GIS substation platform cut to waste | 0 | 19500 | 19500 | 8699.42 | 28199.42
A | E | New AIS and GIS substation platform imported clean fill free of unsuitabls such as organics, topsoil & building waste | 0 | 48000 | 48000 | 225168 | 273168
A | E | Supply, place, AP65 hardfill | 0 | 132825 | 132825 | -132825 | 0
A | E | Supply, place, AP65 basecourse | 0 | 164220 | 164220 | -164220 | 0
A | E | Test soil for contaminants | 0 | 2500 | 2500 | -300.77 | 2199.23
A | E | Dispose of contaminated soil, 50 m3, (Nickel, Chromium, or Arsenic) off site | 0 | 13250 | 13250 | 52788 | 66038
A | E | Supply, place AP40 basecourse | 0 | 225000 | 225000 | -58500 | 166500
A | E | Retaining Wall (if required) 1.5m high, by 20m long to platform edge closest to Contact Energy boundary | 0 | 10400 | 10400 | 25912.55 | 36312.55
A | E | Respread topsoil, harrow and grass seed (150mm depth) | 0 | 10640 | 10640 | 0 | 10640
A | E | Remove sedimentation control system, excluding pond, which shall remain | 0 | 3600 | 3600 | 0 | 3600
A | E | Remove topsoil earth bund and dispose of off site | 0 | 3900 | 3900 | 0 | 3900
A | E | Remove temporary fencing | 0 | 60000 | 60000 | -38040 | 21960
A | E | Clean up site | 0 | 1500 | 1500 | 0 | 1500
A | E | Carry out earthworks, and construct Transfield carpark | 0 | 13500 | 13500 | 75017.04 | 88517.04
A | E | Transfield carpark chip seal grade 3/4 chipseal 180/200 bitumen | 0 | 26100 | 26100 | 0 | 26100
A | E | Construct Transfield carpark fencing | 0 | 31641 | 31641 | 17775 | 49416
A | E | Install bollards along cable route adjacent to Substation Rd for HLY2 & OHW2 cables | 0 | 59200 | 59200 | -59200 | 0
A | E | Install access road and carpark to GIS building | 0 | 36300 | 36300 | 0 | 36300
A | E | Supply and install street lighting to access road and carpark to GIS building - Reduced height of lighting poles, but requirement for cabling to be installed in conduit | 3907 | 13121 | 17028 | 3559.93 | 20587.93
A | E | Extend the northeast existing switchyard fence to beyond 220kV cable trenches | 0 | 0 | 0 | 0 | 0
A | E | Supply and Install Switchyard fence between GIS Building 220kv cable trenches and Transfield offices | 0 | 33602 | 33602 | 3505 | 37107
A | E | Undercut areas of weak sub-grade & replace with GAP65 hard fill (provis qty) | 0 | 0 | 0 | 51357.07 | 51357.07
A | E | Remove existing topsoil & concrete & construct crushed rock & nib wall east end of extg station | 0 | 40000 | 40000 | -40000 | 0
A | E | Lime dry fill with 2% lime (Provisional quantity) | 0 | 0 | 0 | 0 | 0
A | E | Remove rubbish from TP stores outdoor laydown area - As variation Nikau Contractors Ltd removed rubbish from the Transpower stores area in the new AIS platform area near the K Shed. Please refer to CQ 001 |  |  |  | 4215.53 | 4215.53
A | E | Remove existing tower foundation - Remove an existing tower foundation discovered whilst stripping the GIS platform. Included breaking out the 12 feet deep tower foundation and filling the hole with compacted backfill. Please refer to CQ12. |  |  |  | 7332.36 | 7332.36
A | E | Temporary demarcation fencing (orange mesh safety fencing) has been erected (≈225m @ $12/m) in and area between Transfield Services offices and the new GIS cable trench and along the saw cut of the K shed foundation. Please refer to CQ9. |  |  |  | 3233.59 | 3233.59
A | E | Install 6 enviropods - x 3 in Transpowers Store yard, x 3 along Hellabys Road. |  |  |  | 7160.14 | 7160.14
A | E | Vegetation control (cutting & spraying) along Otahuhu site perimeter (19/03/08 - 20/03/08). 2 men x 2 days |  |  |  | 1078.56 | 1078.56
A | E | Platform Layout Plan - original price was to remove kerb & construct 12m concrete access with nib added.old comment. Concrete nib wall added.new comment. Price based on 110m @ $487.50/m |  |  |  | 53625 | 53625
A | E | 220kV GIS/AIS Platform Section 9-9 - temporary access ramp added (not tendered for). Submitted price based on 90m2 @ $151/m2 |  |  |  | 13890.22 | 13890.22
A | E | Straw mulch topsoil area - stabilise dusty top soil area at Contacts request |  |  |  | 3367.44 | 3367.44
A | E | Concrete nib wall detailed on TP63360_0_2 based on 100m @ $ $412.50/m (not tendered for) |  |  |  | 41250 | 41250
A | E | Temporary fencing (orange mesh safety fencing) has been erected (≈110m @ $12/m) along the Hellabys road kerb protecting the unfilled area between the fence and newly erected nib wall. |  |  |  | 1320 | 1320
A | E | Variation works involved extra excavation to move an already constructed silt pond and to realign SWMH01A to allow establishment of drill pit chamber. This was as a result of an unknown water main conflict (unforeseen by the designers) as described by ODP-FP-230. The existing ground level was approx 1.5m higher than the originally designed top of MH which resulted in increased earthwork to establish drll pit. Price breakdown attached. |  |  |  | 3503.1515 | 3503.1515
A | E | New item for the nib/reinforcing wall in between Transfield Services and the GIS platform as per the nib/reinforcing wall constructed for along hellabys Road under item 2.14.57 - $487.50/m @ 107m |  |  |  | 52162.5 | 52162.5
A | E | OTA Substation front entrance gate control and power cable relocation by Magdrive Technologies Ltd (who originally installed the gate controller) Quote attached. |  |  |  | 6286.4431 | 6286.4431
A | E | Additional 54 m of medium security security fence around the Transfield Carpark that was to be completed by AREVA and has now been given to Transfield to complete the security around the TSL carpark. 54 lm of medium security with power fence with an 8m gate (scope refinement 6% mark-up) Price breakdown attached. |  |  |  | 34426.6338 | 34426.6338
A | E | Straw mulch topsoil area - stabilise dusty top soil area at Contacts request where cut to fill on site had been laid. Also approximately 20m x 6m of straw mulching and grass seed laid under the relocated OTA 'C' & PEN 5 towers. Total = $3,617.44 |  |  |  | 3617.44 | 3617.44
A | E | Temporary works site/zoning demarcation fencing (orange mesh safety fencing) ≈ 347m @ $12/m as per attached sketch (Safety fence along Hellabys Rd already charged for). Total = $4,164.00 |  |  |  | 4164 | 4164
A | E | Shifting of the transition station towers and gantries to enable the partial handover of the platform to AREVA. Variation includes the crane hire and some coordination & supervision time. NZ crane hire $1,361.69 |  |  |  | 1820.742 | 1820.742
A | E | ODP-PF-713 (respreading of topsoil from AREVA stockpile) 30 hours of bulldozer works to spread, shape, and track roll the existing stockpiled material @ $115/hr + costs to transport and remove from site $500/per visit = $3,950. As directed a further 40 hours spread over two visits is to be priced for to be claimed against at a later date (40 x $115 + ($500 x 2) = $5,600. Total = $9,550 |  |  |  | 9550 | 9550
A | E | Straw mulch area under SWN & HEN lines as requested by Garry Wright on 27 Feb 2009 $7,600 based on 8,000m2 @ 95c/m2 |  |  |  | 7600 | 7600
A | E | Temporary works site demarcation fencing (orange mesh safety fencing) ≈ 200m @ $12/m as per attached sketch (Safety fence for both the PAK & HLY transition stations) Total = $2,400.00 |  |  |  | 2400 | 2400
A | E | Specifically manufactured pulpit lid lifters to remain on site (for the pulpits installed on the platform and along Hellabys Road) $849.67 for two |  |  |  | 849.67 | 849.67
A | E | Install additional hotmix to the AREVA site office driveway when TSL are hotmixing the Transpower stores drive tomorrow. Area of 20m2 (width varies from 4.6m to 3.7m, and is 4.8m long) The cost of this would be 20m2 @ $47.90/m2 = $958 |  |  |  | 958 | 958
A | E | ODP-PF-808: Sparky Rd Surplus Spoil Dump Site As instructed under ODP-PF-808 As a result of the ARC site meeting/inspection can Transfield Services action the following: 1. This week can the existing spoil piles (and the new ones added by AREVA from the platform) be flattened & straw mulched Flattened under the existing item set up in March under ODP-PF-713. Straw multching $6,400 (two rounds) 2. Can 2 x enviro pods be placed in the sparky rd catch pits opposite the new MH11A $1,444.00 3. Can the existing enviro pods on Hellaby rd opposite the AREVA office & and any others be cleaned (& the rd gutter as well) $1,443.70 Total = $9,287.70 |  |  |  | 9287.7 | 9287.7
A | E | ODP-PF-811: Conflict with existing services CB 48 OTA 110kV AIS and C and I Trench for new GIS T&C submit their costs for the excavation, stand-bye and subsequent backfilling of the C&I cable trench which was started under outage conditions from 16/3/09 to 19/3/09. Due to the presence of underground unforeseen services the work was abandoned and a new cable trench route was designed. 18 March: Excavate, expose services, hand dig around cables and drainage pipe, investigative excavation. Remove excavated spoil from site. 19 March: 5 hrs stand-bye waiting for instruction as to how to proceed. 20 March: Uplift hard fill from on-site stockpile, import bedding sand, backfill and replace yard chip. Materials $156 Labour $2,522 Plant $3,374 Total $6,052 (excluding TSL margin) |  |  |  | 7399.8525 | 7399.8525
A | E | ODP-FP-430: Metal for Transpower stores steel yard Total $7,679.00 Breakdown as per ODP-FP-430 attached |  |  |  | 7679 | 7679
A | E | Construct access track into PAK transition station Total = $2,370 (price breakdown attached) |  |  |  | 2370 | 2370
A | E | ODP-PF-836: Sparky Rd Spoil Dump Site Erosion & Sedimentation Control Plan Implementation Implementation of Erosion & Sediment Control measures in the fill area as instructed under ODP-PF-836 = $9,380.00 See invoice for breakdown |  |  |  | 9380 | 9380
A | E | Hotmix repairs Hotmix repairs under the Otahuhu Enabling Works (Areas 1 - 3) as per attached pricing breakdown. Total = $73,879.40 ($80,357.10 - $6,477.70) |  |  |  | 74379.7587 | 74379.7587
A | E | Road sweeping 30/04 & 01/05 road sweeping (clean road and entrance to tip area) $1,750 02/06 road sweeping $1,035 Total = $2,785.00 |  |  |  | 2785 | 2785
A | E | Construct access track onto tip site (with the hardfill removed from the Contact pond access track) as part of ODP-PF-836. Total = $785.00 (price breakdown attached) |  |  |  | 785 | 785
A | E | Straw mulch around all transition stations (except Henderson as Henderson is surrounded by an existing metal pad). Total = $2,480 (3100m2 @ $0.80/m2) pricing breakdown attached |  |  |  | 2480 | 2480
A | E | Please find attached as discussed / requested our PO for removal of the temporary gates and reinstatement of boundary fence between Contact / Transpower. PO 21112368 $932.80 |  |  |  | 1248.14 | 1248.14
A | E | Remove Northpower spoil from around Ohinewai Transistion Station and place in fill area, trim, shape and compact. Truck - 9hrs @ 95/hr = $855.00 Excavator - 18hrs @ $115.00/hr = $2,070.00 Total = $2,925.00 |  |  |  | 3025.07 | 3025.07
A | E | Install plant mix ramp at entrance to the Otahuhu Substation Control Building (to cover water pipe). This was a request from one of the joint site Safety Meetings. Labour - 4hrs @ $37/hr = $148.00 Plantmix (pre bagged) - 8 @ $86.90/ea = $695.20 Total = $843.20 |  |  |  | 943.27 | 943.27
A | E | ODP-PF-893: Diverse Comms Fibre Duct into the GIS Building Installation of a 50mm comms fibre duct from the Tower 1D (Tower 3A) fibre pit into the GIS Building. Price also includes permanenet drainage works to remove surface water which was filling up the fibre pit. TSL Infrstructure cost to install the duct and draw wire = $5,369.00 Cost of trace wire (100m of 6mm green earth wire) = $252.79 |  |  |  | 5669.22 | 5669.22
A | E | TP Stores Otahu B Train Access - construct truck access from Benmore shed to Henderson Transition Station |  |  |  | 21515.86 | 21515.86
A | E | Close down fill area for winter period as per ARC requirements |  |  |  | 3161.04 | 3161.04
A | E | ODP-PF-894: HEN Transition Station Ducts from lean to for lighting supply - to run cable through Benmore Shed. Lean-to at high level then drop down at northern end and run through conduits to Henderson Transition Station termination tower. Design and fabricate mounting brackets for lights, design and manufacture brackets to mount conduit to towers, erect lights on towers, design and fabricate electrical supply box and commission the same trench, slab and backfill electrical trenches for lighting supply. |  |  |  | 40614.46 | 40614.46
A | E | Remove concrete at rear of entrance of Transpower Warehouse, fill up lip from the new concrete with metal to ensure area is suitable for forklift use |  |  |  | 620.14 | 620.14
A | E | Construct footpath along Gridco/Hellaby's Rd as requested from Co-ordinated Safety Meetings (western side of road adjacent to Diversity Project new GIS/AIS yard). |  |  |  | 14581.79 | 14581.79
A | E | Surveying work of inside corner points of all transition stations |  |  |  | 1845 | 1845
A | E | GIS Building Access Road Topo Surveying work as requested by G Wright 6 Aug 2009 |  |  |  | 1968 | 1968
A | E | Additional ducts were requested in the trench excavation for earthstraps in Technical Meeting Number 63, 16/6/09. (Item 3C) Excavation of trenches for earthstraps and spare ducts across Substation Road to the switchyard fence, |  |  |  | 9497.85 | 9497.85
A | E | To prepare access for Transpower Stores Staff to load and unload insulators near the rear storage gate at Sparky's Road. |  |  |  | 4762.88 | 4762.88
A | E | Refer to ODP-PF-975 To install approx 100m (twin level) of 300mm Nema Trunking in the C&I trench between the 'platform' and C&I trenches interconnecting the AIS with RCN and Existing Control Room. Tray/Ladder installation to the same criteria as as installed by TSL on the Areva C& I section of the same trench [plafform into GIS relay room basement]. |  |  |  | 42859.1844 | 42859.1844
A | E | Changes required to C & I cabling associated with CB528 It was identified during installation of the C&I cabling that 2 cables on the cable schedule [5202 & 5201] designated to be re-routed on the applicable cable schedule could not be as they were direct buried. This variation covers the supply and installation of 4 core PVC / SWA / PVC 2.5 mm cables 5202 & 5201. |  |  |  | 1906.0236 | 1906.0236
A | E | ODP-FP-810 Re prep. OHW and HLY trasition stations in preparation for receiving Transpower isolation chip (TPCR40) undertaken on Wednesday 21/04/2010 and Thursday 22/04/10. Excavator 8hrs @ $95.00/hr = $760.00, Loader 6hrs @ $95.00/hr = $570.00, Labour 15hrs @ $34.00/hr = $510.00, additional establishment of equipment $280.00. Total cost = $2,120.00 |  |  |  | 2220.0718 | 2220.0718
A | E | Scope refinement for increased material costs for TPCR40 crushed aggregate (isolation chip) for OHW and HLY transition stations. The original price of the material was $40.73/m3, current price of material is $42.76/m3, cost increase of material = $2.03/m3. Therefore 512m2 + 519m2 = 1031m2 x 150mm (material thickness) = 154.65m3 Also, there was an additional 12m2 of isolation chip for HLY (schedule item 2.10.3) and 19m2 for OHW (schedule item 2.11.3) @ 12/m2. Original measurements were 500m2 for each Transition Station. An EO of 31m3 @ $12/m2 is being claimed. |  |  |  | 786.7217 | 786.7217
A | E | ODP-FP-782 costs associated with additional establishment for GIS building hotmix, which was abandoned Labour 4 x 5hrs = 20hr @ $34.00/hr = $680.00, Civil Supervisor 2hrs @ $68.00/hr = $136.00, Surveyor 2hrs @ $135.00/hr = $270.00, Transporter 3hrs @ $130.00 = $390.00 Total cost = $1,476.00 |  |  |  | 1576.0718 | 1576.0718
A | E | GIS Building concrete driveway, additional drainage and watermain |  |  |  | 73633.59 | 73633.59
A | E | Strip chip from GIS channel and stockpile at CAP BANKS. |  |  |  | 1699.72 | 1699.72
A | E | Place Transpower chip in Cap Bank Area |  |  |  | 22390.26 | 22390.26
A | E | GIS Driveway including subsoil drain $3147.78, cut down nib wall $1759.29, cut down sewer $640.85, cut to waste $19,124.98, supply isolation chip $5,780.09, construct subbase $32,950.18, construct base course $29,506.84, install concrete entrance $4,188.97, hot mix $26,694.36, new kerbing $10,038.39 and line marking $561.75. |  |  |  | 134293.48 | 134293.48
A | E | AIS driveway - additional work on Gridco road |  |  |  | 30762 | 30762
A | E | ODP-PA-770: Transpower requested that the entire site be "tidied up" prior to the official opening on 19 August 2010. This cost was to be borne by both Transpower and Eberts. This variation covers supplying labour hire personnel, own forces, hired equipment (wheelbarrows), dumping of rubbish and subcontractor costs. Item also includes the following: Main AIS1 entrance - additional concrete crossing for carpark by existing security gate (used by John Key to park his car) plus level carpark and tidy up and add additional GAP40 layer Grounds maintenance work by Infrastructure to tidy up substation which included placing haybales and general topsoil on pasture along Gridco Road |  |  |  | 33508.5 | 33508.5
A | E | Cover GIS driveway with polythene to protect against rain damage prior to sealing and cement stabilisation of basecourse metal prior to sealing |  |  |  | 1847.4085 | 1847.4085
A | E | Gridco Road - new kerb and nib installed, concrete footpath, fencing post and mowing strip, concrete collars to cesspit and service lid. |  |  |  | 9492.5799 | 9492.5799
A | E | Supply and place Transpower chip to GIS channel |  |  |  | 9237.3972 | 9237.3972
A | E | Supply and place insulation chip in 1m strip outside GIS switchyard fence |  |  |  | 15701.6508 | 15701.6508
A | E | Supply potable water supply to GIS building | 0 | 12000 | 12000 | -12000 | 0
A | S | Supply and install stormwater system to AIS and GIS substation platform. Allow for 300mm pipework. | 0 | 152000 | 152000 | 603089.6 | 755089.6
A | S | Supply and install stormwater half round channel to AIS and GIS substation platform. Allow for 300mm half round | 0 | 63000 | 63000 | -39001.5 | 23998.5
A | S | Stormwater Catchpit | 0 | 19000 | 19000 | -6650 | 12350
A | S | Stormwater Manhole. Allow 1 metre daimetre, by 1 metre deep. | 0 | 10800 | 10800 | 4600 | 15400
A | S | Pipe, manhole and Backfill existing Contact Energy Stormwater containment pond | 0 | 13900 | 13900 | 4104.94 | 18004.94
A | S | Supply and install stormwater system for Transfield carpark, treated to MMC system. Allow for 300mm pipework | 0 | 57000 | 57000 | -57000 | 0
A | S | Supply and install Hynds Up-Flow filter treatment (or similar) to Transfield carpark stormwater | 0 | 22500 | 22500 | 90561.55 | 113061.55
A | S | Modify existing warehouse area stormwater, treated to MMC stormwater. Allow for 300mm pipework | 0 | 28500 | 28500 | -28500 | 0
A | S | Supply and install Hynds Up-Flow filter treatment (or similar) to warehouse stormwater | 0 | 22500 | 22500 | 90561.55 | 113061.55
A | S | Supply and install stormwater system for GIS driveway & carpark, treated to MMC system. Allow for 300mm pipework | 0 | 38000 | 38000 | -38000 | 0
A | S | Supply and install Hynds Up-Flow filter treatment (or similar) to GIS Driveway & Carpark stormwater | 0 | 22500 | 22500 | 90561.55 | 113061.55
A | S | Supply and install precast concrete cable trench between new AIS fence and existing 110kV switchyard trench system | 0 | 79000 | 79000 | 121126.8357 | 200126.8357
A | S | Drainage Section A-A & B-B - Surface drain detail A added (not tendered for). Submitted price based on 156m @ $76/m. |  |  |  | 104595.1288 | 104595.1288
A | S | Remove 4 concrete chambers along Hellabys Road @ $940 each. |  |  |  | 3980.22 | 3980.22
A | S | Removal of existing stormwater from the platform as specified on TP63300 and taken off site. $210.28/lm @ 107m |  |  |  | 35166.96 | 35166.96
A | S | Removal of 126m of stormwater near the cut k shed slab as per TP63300. This is in addition to stormwater already removed on the platform and claimed in July under item 2.14.62. Please refer to the attached breakdown. |  |  |  | 57968.09 | 57968.09
A | S | Backfilling of storm water trenches with GAP65 in addition to new rates provided for extra depth and over diameter pipes. As specified those rates only included backfilling with excavated material and hardfill compacted material would be required in addition. Estimated volume is 279m3 @ 94m3. This scope refinement was submitted in July and now needs to be reversed as costs have been re allocated under items 2.14.18, 2.14.63 and 2.14.64. |  |  |  | 0 | 0
A | S | Install SW Filter System (items 2.14.33A, 2.14.34A, 2.14.35A). As per SW breakdown - rev04.xls |  |  |  | 431587.2 | 431587.2
A | S | ODP-FP-268 Temporary fence installation for Transpower's Stores area access gates to enable the installation of storm water pipes between MH02 & 02A. A hot wire was installed on a temporary fence section for a period of weeks to allow for installation. Paul Nathan = $4,743.51 (with TSL margin) |  |  |  | 4743.5069 | 4743.5069
A | S | ODP-PF-698: Hellaby Rd Catch Pit Relocation Works Price to install catch pits G & H and associated drainage in Hellaby’s Road. Prices for modifying / replacing catchpits A, B,C & D will be forwarded in the near future. Total $49,998.00 (as per Stonedale invoice). Price does not include removal of old pipes. These pipes can be removed under dayworks rates. Stonedale invoice attached |  |  |  | 49997.997 | 49997.997
A | S | Makeup risers for SW / WW MH's due to changes in finished levels as follows: - 1050dia = $882/m - 1200dia = $1,102/m - 1500dia = $1,432/m - 1800dia = $2,084/m - 2300dia = $4,168/m Submitted and approved in November 08 Now: Manhole 01A 1500mm diameter raised 1.09m [1.09m x $1,432.00/m = $1,560.88] Manhole 02 1500mm diameter raised 0.18m [0.18m x $1,432.00/m = $257.76] Manhole 02A 1500mm diameter raised 0.36m [0.36m x $1,432.00/m = $515.52] Manhole 04 1600mm diameter raised 0.13m [0.13m x $1,432.00/m = $186.16] Manhole 05 1500mm diameter raised 0.77m [0.77m x $1,432.00/m = $1,102.64] Manhole 06 1200mm diameter raised 0.31m [0.31m x $1,102.00/m = $341.62] Manhole 07 1050mm diameter raised 0.1m [0.10m x $882.00/m = $88.20] Total $4,052.78 |  |  |  | 4052.78 | 4052.78
A | S | Clean out debris from Stormfilter next to Hendn Transition Station and install new media |  |  |  | 3496.11 | 3496.11
A | S | Construct stormwater connections to Benmore Shed |  |  |  | 0 | 0
A | S | Benmore Shed Stormwater connections work as requested at the Technical Meeting on 5 May & 23 June. Note - additional costs from United Engineering to come for additional downwater pipes etc |  |  |  | 17562.93 | 17562.93
A | S | As per ODP-PF-992 & ODP-PF-229 a request during a safety walk-around a request was made to cover the centre drain on the traverser track. Tunnel & Civil (through TSL) submitted a price to install metal grating. This price was rejected initially by Transpower with a cheaper option request. A cheaper proposal was submitted and accepted. 19mm Plywood was placed over the drain. Due to heavy traffic movements the plywood deteriorated and became a hazard itself. A further request was made to remove the temp plywood replacing it with webforge grating. This variation covers temporary and permanent installation. |  |  |  | 55170.3904 | 55170.3904
A | S | Supply staff & Hiab to install medium silt filters as instructed Following an Inspection by AECOM prior to the ARC inspection it was identified that due to the earlier than planned use the sand filters required additional medium installed. TSL Infrastructure have already claimed for the medium [ref 18353] however TSL Electrical services omitted to submit our claim for staff and equipment whom assisted with the loading and filling of the medium. This variation is for supply of staff plus a truck mounted crane [Palfinger] to uplift and offload the medium through the MH covers of the sand filters. |  |  |  | 784.2806 | 784.2806
A | S | Supply and install 200mm diameter PVC pipe beneath GIS channel |  |  |  | 48819.4 | 48819.4
A | S | Transpower requested that the temporary plug placed in the sand filter inlet be removed to alow operation of the filters now construction activities have been completed. |  |  |  | 698.5174 | 698.5174
A | U | Relocation of approx 146.0m of existing 150mm water main by Stonedale. Price includes (please find attached pricing breakdown): 1. Establishment 2. All excavation and reinstatement works including road pavement and grass berm 3. Allowed to place new water main aprox 5.0m to the East of the existing main and to reconnect the 3 existing 150mm branches to new water main 4. Allowed to lower the first 5.0m along Hellaby Rd to allow new cable trough to pass over top 5. Chlorination and testing of new lines 6. After hours shut down and connection of new line to minimise disturbance during normal working hours |  |  |  | 49028.4165 | 49028.4165
A | U | Stonedale service relocation site investigations: - 17/10/2008 - 22/10/2008 - 19/09/2008 - 18/09/2008 All works based on daily charge out rates. Please find attached worksheets. |  |  |  | 3246.915 | 3246.915
A | U | Site Service relocation management. Man hours to date = 183. Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) & 7% (profit) |  |  |  | 15888.415 | 15888.415
A | U | Site Service relocation management. Man hours to date = 323. 183 charged last month (incorrectly) with a variation margin as it was decided this would be charged at a cost rate (including overheads). Therefore a 'give back' of $1039.43 is included in this price. Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) @ 139 hours = $11,278.74 - $1,039.43 = Total $10,239.31 |  |  |  | 10239.308 | 10239.308
A | U | Stonedale Civil relocation of 150D Water Main along the front of the OTA Switchyard and along Hellabys Road. Variations works for Epoxy coated steel sections (PVC lowered to 2.5m below Hellabys Road over 28m & AC lowered to 3m below Heabblabys Road over 30m) Total $47,583.00 (without TSL 5% & 7% mark-up for subcontractor variations) Price breakdown attached. |  |  |  | 53459.5005 | 53459.5005
A | U | Stonedale Civil Service Exploratory Works Dayworks rate for 10.5 days from the 4th to the 21st of November @ $840/day (without TSL 5% & 7% mark-up for subcontractor variations) Quote attached. |  |  |  | 9909.27 | 9909.27
A | U | Fibre relocation $32,094 (TSL Infrastructure portion) + $87,650.98 (Downers portion including TSL margin) = $119,744.98 TSL directional drilling includes installation of 1 x 110 mm green duct complete with draw string (no allowance has been made for the obtaining of resource consent for working under the drip line of a protected trees and no allowance has been made for any unforeseen ground conditions). Downers price includes: Supply ducting, supply and install 2 manholes and uplift and re-install concrete panels to install ducting. $32,038.50 Supply and install fibre into buildings, joint and divert, then remove old plant. $44967.40 Telecom permits $1010.10 Any additional TSL labour input outside the infrastructure thrusting will be charged at cost under the Site Service Relocation variation code. |  |  |  | 119744.976 | 119744.976
A | U | Oil interceptor relocation works Stonedale Civil price for the oil interceptor relocation works as per the FOR CONSTRUCTION drawings issued under ODP-PF-578 is $84,863.24 (as per ODP-PF-585 & including TSL margin). This does not include TSL Safety Standover hours required whilst trenching within the Switchyard. These will be charged under the 'Investigation shifting of existing site services' variation code. |  |  |  | 84863.24 | 84863.24
A | U | Site Service relocation management. Man hours to date = 694. 371 hours since last claim. This includes 143.5 hours from another JDE code (Engineering for existing site services - the time was mainly Hec Sutherland's hours since 24/08/08). This code was used in conjunction with the main code and has now been closed and all TSL time booked to the one code. Original code hours includes cable locating, trench cover fabrication and placement, management and safety observing. Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) @ 240.5 hours = $19,514.65 Electrical fitter rate = $33.85 + 45% (overheads) @ 130.5 hours = $6,405.27 Total = $25,919.92 |  |  |  | 25919.9172 | 25919.9172
A | U | Investigate shifting of existing site services (Site service relocation man hours) - 694 as at Jan changes - 882 hours to date (as at Feb changes) - 694 claimed up to Jan changes = 188hours (185hours @ T1 and 3hours @ T1 1/2) Labour: Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) @ 144 hours = $11,684.45 Electrical fitter rate (T1) = $33.85 + 45% (overheads) @ 41 hours = $2,012.38 Electrical fitter rate (T1 1/2) = $42.75 + 45% (overheads) @ 3 hours = $185.96 Total = $13,882.79 Subcontractors: Tana Enterprise Ltd (contractor safety observing for the oil interceptor works) 29 hours @ $56.18/hr = $1,629.22 Grout Seal Ltd (smoke and video tests) = $870.71 Total = $2,499.93 Materials: Copy & Print for A1 drawings = $42.69 Timber for damaged wooden cable lids = $200.48 Cadweld charges for earth wire relocation = $1,117.73 Total = $1,360.90 Grand total = $17,743.62 |  |  |  | 17743.623 | 17743.623
A | U | Stonedale Expose, remove existing main, supply and place new section of 150mm main lowering the existing to 2.5m deep (over 4m) = $7,645.42 (including TSL margin) Invoice attached |  |  |  | 7645.4175 | 7645.4175
A | U | Stonedale Works locating underground services at Otahuhu. Dayworks completed from 3/12/08 to 12/01/09 = $6,280.37 (including TSL margin) Invoice attached |  |  |  | 6280.365 | 6280.365
A | U | Stonedale Stormwater relocation - divert the existing SW pipe currently located directly under the HLY Transition station = $9,795.68 (including TSL margin) Invoice attached |  |  |  | 9795.6841 | 9795.6841
A | U | Investigate shifting of existing site services 1055 hours as at March changes - 882 claimed up to Feb changes = 173 hours Labour: Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) @ 140 hours = $11,359.88 Electrical fitter rate (T1) = $33.85 + 45% (overheads) @ 33 hours = $1,619.72 Total = $12,979.60 Subcontractors: Hirepool barriers hire for 8 weeks along Hellabys Road (PO21110973). $429.20/wk = $3,433.42 Total = $3,433.42 Materials: Timber for damaged wooden cable lids = $95.73 Total = $107.55 Total = $16,520.57 |  |  |  | 16520.5727 | 16520.5727
A | U | Stondale Stormwater relocation - divert the existing SW pipe currently located directly under the HLY Transition station = $9,795.68 Now $12,175.93 with additional costs for an additional 15m - 20m of 225dia RCRRJ stormwater pipe Therefore, EO = $2,380.25 Invoice attached |  |  |  | 2380.25 | 2380.25
A | U | Stonedale New 50mm connection to main and 50mm valve 50mm valve to supply new construction area $820.26 Invoice attached |  |  |  | 820.26 | 820.26
A | U | Stonedale Dayworks (18, 19 & 20/02/09) = $2,595.29 Invoice attached |  |  |  | 2595.285 | 2595.285
A | U | Investigate shifting of existing site services (April) 1337 hours as at April changes - 1055 claimed up to March changes = 282 hours Labour: Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) @ 166 hours = $13,469.57 Electrical fitter rate = $33.85 + 45% (overheads) @ 60 hours = $2,944.95 Trades Assistant / Trainee = $25.6 + 45% (overheads) @ 48 hours = $1,781.76 Communications Technician = $46.87 + 45% (overheads) @ 8 hours = $543.69 Total = $18,739.97 Subcontractors: Tana Enterprise Ltd (contractor safety observing for the 11kV relocation works) 28 hours @ $56.18/hr = $1,572.90 Treecare services (consent & reports) = $2,2022.30 Trecare services (removal of trees) = $1,674.00 INF for 11kV relocation works = $4,979.91 Total = $10,249.13 Materials: Safety signs for the gates on gate 6 = $155.04 Cadweld mould = $522.42 Cadweld chargers = $3,072.73 Miscelleous materials = $218.91 Total = $3,969.10 Grand total = $32,958.20 |  |  |  | 32958.204 | 32958.204
A | U | Investigate shifting of existing site services - April/May 1568 hours as at April changes - 1337 claimed up to April changes = 231 hours Labour: Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) @ 118 hours = $9,574.76 Electrical fitter rate = $33.85 + 45% (overheads) @ 105 hours = $5,153.66 Trades Assistant / Trainee = $25.6 + 45% (overheads) @ 8 hours = $296.96 Total = $15,025.38 Materials: General cable (PO21111764) = $3,080.00 Miscellaneous materials = $1,105.50 Total = $4,184.50 Grand total = $19,209.88 |  |  |  | 19209.8785 | 19209.8785
A | U | Stonedale Civil Dayworks Dayworks completed during the period of March - see invoice Total = $6,552.25 Invoice attached |  |  |  | 6552.252 | 6552.252
A | U | Shifting of existing site services (outside the sub for May) 1653 hours as at May changes - 1337 claimed up to April changes = 316 hours Labour: Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) @ 194 hours = $15,741.55 Electrical fitter rate = $33.85 + 45% (overheads) @ 84 hours = $4,122.93 Trades Assistant / Trainee = $25.6 + 45% (overheads) @ 38 hours = $1,410.56 Total = $21,275.04 Subcontractors: Treecare (removal of stumps) = $1,674.01 Stonedale (dayworks for April/May - invoice attached) = $3,086.25 Detection of services = $337.05 Total = $5,097.31 Materials: Cable repairs materials (incl. cable) = $2,059.35 Padlocks = $113.28 Total = $2,172.63 Total = $28,544.98 |  |  |  | 28544.9835 | 28544.9835
A | U | Shifting of existing site services (inside the sub for May) 55 hours as at May changes - 0 claimed up to April changes = 55 hours Labour: Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) @ 32 hours = $2,596.54 Electrical fitter rate = $33.85 + 45% (overheads) @ 12 hours = $588.99 Trades Assistant / Trainee = $25.6 + 45% (overheads) @ 11 hours = $408.32 Total = $3,593.85 Subcontractors: Stonedale Civil - Redirection of 225 dia Oil Interceptor line within the switchyard = $15,893.03 (invoice attached) Concrete cutting = $308.96 Tana Enterprises Ltd (safety observing) @ 31 hours = $1,741.43 Total = $17,943.42 Materials: N/A Total = $21,537.27 |  |  |  | 21537.2725 | 21537.2725
A | U | Site Service relocation (outside the substation) JUNE Investigate shifting of existing site services (outside the sub in June). This job number is to be closed down by the end of this month and all remaining service relocation costs will be captured under 18140. 1697 hours as at June changes - 1653 claimed up to May changes = 44 hours Labour: Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) @ 42 hours = $3,407.96 Trades Assistant / Trainee = $25.6 + 45% (overheads) @ 2 hours = $74.24 Total = $3,482.20 Subcontractors: Clean up rubbish, fill material from around OTA'C', HLY, OHW & SWN transition station as a result of relocation works = $1,407.00 Total = $1,407.00 Materials: Additional cable repairs materials (damaged cable by EBERT (cable claimed last month) = $575.32 Digger hire = $1,044.41 Miscellaneous materials = $215.04 Total = $1,834.77 Total = $6,723.97 |  |  |  | 6723.97 | 6723.97
A | U | Site service relocation (inside the substation) JUNE Shifting of existing site services (after June, this code will be utilised for any remaining site service relocation works inside or outside the Substation) 67.5 hours as at june changes - 55 claimed up to May changes = 12.5 hours Labour: Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) @ 12.5 hours = $1,014.28 Electrical fitter rate = $33.85 + 45% (overheads) @ 0 hours = $0.00 Trades Assistant / Trainee = $25.6 + 45% (overheads) @ 0 hours = $0.00 Total = $1,014.28 Subcontractors: N/A Materials: N/A Total = $1,014.28 |  |  |  | 1014.28 | 1014.28
A | U | Relocation of services July/August |  |  |  | 8760.86 | 8760.86
A | U | Shifting of site services - not yet invoiced. Identified during reconcilliation activities. Sep/Oct/Nov/Dec 72 hours claimed for July/August - 153.50 hours to date = 81.50hours Labour: Project Engineer / Planning Co-ordinator rate = $55.96 + 45% (overheads) @ 43 hours = $3,489.11 Electrical fitter rate = $33.85 + 45% (overheads) @ 32 hours = $1,570.64 Electrical fitter rate (T1 1/2) = $42.75 + 45% (overheads) @ 6.5 hours = $402.92 Materials: Light Bulbs (for the basement lights) $187.28 Subcontractors: Control room clean out $224.70 Indirects: Digger hire $1,071.68 Barrier hire (Substation Road continued - PO21110973 $3,433.42 already claimed) $1,799.40 Barrier hire (PO21113011 & 21113037) $2,088.81 Total = $10,834.54 |  |  |  | 10834.3205 | 10834.3205
A | W | Seal over exisitng Watercare sewer manhole MH11, and satelite MH's | 0 | 25705 | 25705 | 44386 | 70091
A | W | Replace MH11 with new manhole near Hellabys Rd. Allow 1.2M diametre by 12 M deep. | 0 | 87600 | 87600 | 150168.22 | 237768.22
A | W | Replace MH11 with new manhole near Sparkys Rd. Allow 1.2M diametre by 12 M deep. | 0 | 87600 | 87600 | 148589.72 | 236189.72
A | W | Reconnect Contact Energy sewer into the MH near Sparky's Rd, via satelite MH. Allow 220mm dia pipework. | 0 | 40400 | 40400 | 88455.51 | 128855.51
A | W | Contact Energy sewer satelite MH beside new Watercare MH in Sparky's Rd. Allow 1.2 M diametre, by 12 M deep. | 0 | 113600 | 113600 | 7225.8 | 120825.8
A | W | Reconnect warehouse sewer into the MH near Sparky's Rd, via satelite MH. Allow 150mm dia pipework. | 0 | 34100 | 34100 | 32968 | 67068
A | W | Warehouse sewer satelite MH beside new Watercare MH in Sparky's Rd. Allow 1.2 M diametre, by 1.0M deep. | 0 | 11804 | 11804 | 0 | 11804
A | W | Supply and install sewer connection for GIS building into MH near Hellaby's Rd via satelite MH. Allow 100mm dia pipework. | 0 | 31000 | 31000 | 29144 | 60144
A | W | GIS Building sewer satelite MH beside new Watercare MH in Sparky's Rd. Allow 1.2 M diametre, by 1.0M deep. | 0 | 11804 | 11804 | 50017 | 61821
A | W | Investigate blocked sewer near Transpower Stores (blocked between SSMH 03 and Watercare SSMH 11). Tried locating point of blockage with a CCTV camera and unblocking unit, ecavate pipe, repair blockage and reinstate (backfil and hardfil). Please refer to ODP-FP-183. |  |  |  | 6100 | 6100
A | W | Preparation of the RCN Building structural crack report for the instllation of MH11B. This report was prepared by Hec Sutherland and issued under ODP-FP-196. Includes 19 hours of Hec's time at a Project Engineer rate. |  |  |  | 1736.44 | 1736.44
A | W | Remove existing MH discovered at location of MH03 and removal of contaminated spoil. Whilst excavating to install MH03 on the Benmore wastewater pipeline, an existing dry chamber manhole was encountered. Due to the location (off set from HDD line) the dry chamber required removal. |  |  |  | 8033.025 | 8033.025
A | W | Remove the top of existing MH D. Seal pipeline, backfill manhole with concrete and hardfill. |  |  |  | 7613.9595 | 7613.9595
A | W | Waste Water Variation No. 3 - Delays on MH11 construction (Clive Tilby approval for $47,670.11 as per ODP-PF-574) NOTE: TSL subcontractor margin mark-up of 5% (overheads) and 7% (profit) for variations as per TSL's tender still to be applied (no processing costs applied) after resolution as to the understanding of Clive's last sentence in his report. |  |  |  | 42430.0045 | 42430.0045
A | W | Waste Water Variation No. 9 - Additional Dewatering Sump at MH11A (Clive Tilby approval for $28,692.24 as per ODP-PF-574). NOTE: TSL subcontractor margin mark-up of 5% (overheads) and 7% (profit) for variations as per TSL's tender still to be applied (no processing costs applied) after resolution as to the understanding of Clive's last sentence in his report. |  |  |  | 25538.2644 | 25538.2644
A | W | Waste Water Variation No. 19 - Load Test on Srew Piles (Clive Tilby approval for $7,135.35 as per ODP-PF-574) NOTE: TSL subcontractor margin mark-up of 5% (overheads) and 7% (profit) for variations as per TSL's tender still to be applied (no processing costs applied) after resolution as to the understanding of Clive's last sentence in his report. |  |  |  | 6351.0013 | 6351.0013
A | W | Waste Water Variation No. 20 - Change in Pipe Size (Clive Tilby approval for $11,010.30 as per ODP-PF-574) NOTE: TSL subcontractor margin mark-up of 5% (overheads) and 7% (profit) for variations as per TSL's tender still to be applied (no processing costs applied) after resolution as to the understanding of Clive's last sentence in his report. |  |  |  | 9800 | 9800
A | W | Waste Water Variation No. 21 - Oversize Dewater Sump (Clive Tilby approval for $14,346.12 as per ODP-PF-574) NOTE: TSL subcontractor margin mark-up of 5% (overheads) and 7% (profit) for variations as per TSL's tender still to be applied (no processing costs applied) after resolution as to the understanding of Clive's last sentence in his report. |  |  |  | 12769.1322 | 12769.1322
A | W | TSL mark-up applied to WW variations approved by Clive Tilby without the 5% BPC "processing costs" (as clarified under ODP-PF-593). Total value approved in December (VO3, 9, 19, 21 & 21) = $96,888.40, therefore, minus 5% processing costs = $92,274.67 and with TSL's 12.35% subcontractor (overheads + profit) mark-up applied the total is $103,670.59 Therefore the total EO for the TSL margin excluding the 5% BPC processing cost = $6,782.19 ($103,670.59 - $96,888.40) |  |  |  | 6782.19 | 6782.19
A | W | Additional GIS Building Sewer Satellite MH03 located in the GIS platform to allow for future connection . Allow 1.2m D by 2m deep, benched ,channelled complete with HD lids = $12,046.50 Approved by Maunsell (16/01/09) |  |  |  | 12046.5 | 12046.5
A | W | Installation of the sealed manhole lid at Transpower stores MH (existing) Hynds quote $1,060.80 (cost) Labour 1.5 hr @ $37/hr $55.50 Subtotal $1,116.30 Margin (5%+7%) $147.20 Total $1,263.50 |  |  |  | 1263.5 | 1263.5
A | W | Clive Tilby's Report dated 16 December 2008 related to the Contact Sewer Pipeline (ODP-PF-582) Claim as per page 8 for $61,750, 50% of the $123,500 BPC claim and $20,226, 50% of the $40,452 for standing time Total = $81,976 (excluding TSL margin as per the report) |  |  |  | 81976 | 81976
A | W | MP 375, TP66490, installation of GIS wastewater from manhole. There is a previously approved rate and scope refinement for the construction of stormwater lines from 1.5m deep to 2.4m deep, which include hardfill backfill, and preparation of 'As Built' drawings. Item 2.14.18 (Installation of 225mm concrete pipes between 1.5m and 2.5m - based on a 600mm wide trench) the rate for this is $235.00/m. The new wastewater line that was installed was 100mm PVC pipe, varying in depth from 2.2m to 1.8m. The pipe was installed in a 600mm wide trench to ensure stability, safety of the trench, and to provide room for the drainlayer to move and lay the pipe. The length installed was 49m @ $235.00/m = $11,515.00 (based on 225D pipe - deduct the cost of a 225mm class Z concrete pipe, -49m @ $38.20/m = $-1,871.80, and replace with the cost of a 100mm SN16 PVC Sewer pipe, 49m @ $21.60/m = $1,058.40. Cost to install pipe and hardfill is $10,701.60. The previously approved rates were based on cut to fill of the excavated material. As the on site tip area has been closed for the winter period, additional costs were incurred with the excvated material taken to an offsite tip, where tipfees were charged. The additional cost for the offsite tip fees for 8 loads @ $102.00/load = $816.00. The additional time for a truck to remove surplus material to an off site tip, compared to tipping on site is, 6hrs @ $95.00 = $570.00, Total price is $12,087.60 |  |  |  | 12387.8152 | 12387.8152
A | W | VO17 as per Clive Tilby's report as agreed under ODP-FP-685 Total = $45,393.00 |  |  |  | 45393 | 45393
B | F | Install piled foundations for tower 3B (one 1.8 m dia pile per leg, 20m deep) | 3311 | 370132 | 373443 | -9920.6512 | 363522.3489
B | F | Install piled foundations for tower 3D (one 1.8 m dia pile per leg, 20m deep) | 3311 | 370132 | 373443 | 0 | 373443
B | F | Install piled foundations for tower 3E (one 1.8 m dia pile per leg, 20m deep) | 3311 | 370132 | 373443 | 0 | 373443
B | F | Install piled foundations for tower 3F (one 1.8 m dia pile per leg, 20m deep) | 3311 | 370132 | 373443 | 0 | 373443
B | F | Install new 220kV tower 3B | 39028 | 18689 | 57717 | 30931.23 | 88648.23
B | F | Install new 220kV tower 3D | 39028 | 18689 | 57717 | 20188.9452 | 77905.9452
B | F | Install new 220kV tower 3E | 39028 | 18689 | 57717 | 20188.9452 | 77905.9452
B | O | 110kV Tie Lines 1 & 2 Deviation
B | O | Re-route, terminate OTA B tie line 2 at 110kV bay 72 (existing postion tie line 1) | 18584 | 19270 | 37854 | 44488.442 | 82342.442
B | O | Modify and strengthen tie line 1 tower T1 for double circuit | 7254 | 28146 | 35400 | -12520.368 | 22879.632
B | O | Relocate and teminate tie line 1 into adjacent spare bay 62. | 4317 | 3141 | 7458 | 0 | 7458
B | O | Remove three off existing tie line 2 towers, and lines | 65796 | 19306 | 85102 | -16879.41 | 68222.59
B | O | Remove top 1200mm of existing tie line 2 terminal tower foundation | 0 | 6180 | 6180 | 4933.98 | 11113.98
B | O | Install new 110kV circuit breaker CB62 | 2305 | 4678 | 6983 | 1700 | 8683
B | O | Install new 110kV 110kV CT62 | 1766 | 1473 | 3239 | 2098 | 5337
B | O | Install line disconnector in bay 62. | 2985 | 1473 | 4458 | 1756 | 6214
B | O | Install two bus disconnectors in bay 62. | 6490 | 3791 | 10281 | 10118 | 20399
B | O | Install foundation for new CB2 | 99 | 9653 | 9752 | 4008 | 13760
B | O | Install foundation for CT62 | 0 | 0 | 0 | 0 | 0
B | O | Install line disconnector foundation | 99 | 11391 | 11490 | -3640 | 7850
B | O | Install bus disconnector foundations | 198 | 22783 | 22981 | -8281 | 14700
B | O | Supply and install foundation & other civil work for Bus Posts | 198 | 4392 | 4590 | -30 | 4560
B | O | Supply and install CT Stands | 142 | 6573 | 6715 | 1385 | 8100
B | O | Modify Tie line 1 & 2 protection systems and settings | 6528 | 1892 | 8420 | 8575 | 16995
B | O | Modify SCADA/RTU systems and settings | 0 | 0 | 0 | 0 | 0
B | O | Install secondary cabling from ODJBs to control/relay room | 3854 | 3791 | 7645 | 17032 | 24677
B | O | Install equipment earth connections | 1612 | 1941 | 3553 | 6924 | 10477
B | O | Test and commission | 9520 | 1953 | 11473 | 0 | 11473
B | O | Decommission and remove Bay 222 equipment, droppers, and line termination | 16555 | 7085 | 23640 | 5765 | 29405
B | O | Contractor to Specify (Relable Line) | 1000 | 244 | 1244 | 1498.1436 | 2742.1436
B | O | 110kV Bus Zone | 6528 | 132 | 6660 | 0 | 6660
B | O | Our price did not include the cost to supply & install any bus support posts. No price schedule item for these. Cost is for supply and installation of 3 only 110kV bus support posts. |  |  |  | 4058 | 4058
B | O | Exspose power cable running across new VT pads (cap with 100mm PVC conduit and warp in denso tape). Please refer to CQ25. |  |  |  | 676.85 | 676.85
B | O | Bay 60 (General Notes) - Need to provide copy to Tunnel & Civil but should not have an effect on the price. Cost for impact from this drawing is included with the foundation scope refinement pricing 2.1.10 except for the soil bearing strength tests. This price submitted is for all of bay 62 testing. Further soil testing will be included in scope refinements of individual foundations going forward. |  |  |  | 1658.27 | 1658.27
B | O | Bay 60 Earthmat - varaition to the contract (includes excavations, supply and installation of twin 50x4mm CU, jointing, QA and 'As builts'). |  |  |  | 44204.69 | 44204.69
B | O | Lost time due to incorrect leg supplied with Line DIS (Work conducted on Saturday 16 Febuary). Time includes recrating and returning disconnectors to Transpower stores whilst picking up the new ones - CQ37. Also included is the time spent in correcting the locking hooks on all three phases - CQ41. |  |  |  | 1611.49 | 1611.49
B | O | Supply of the IDB/K (DIS-ES 66-69) steelwork & stands. Disconnectors to be supplied by Transpower. Supplied without stands. |  |  |  | 23913.03 | 23913.03
B | O | Cleaning up of TP supplied equipment (water blasting IDB/K 3's and 5's Disconnectors). |  |  |  | 635.51 | 635.51
B | O | Bay 60 (3's & 5's DIS pads) - Foundation is smaller than priced. Scope refinement was - Foundation decreased by: Area 7m2, Concrete Volume 3.15m3, Reinforcing 192kg, Ducts 2x 100mm. Operator Mat increased by: Area 0.75m2, Depth 70mm. Now - Foundation increased by: Area 2.94m2, Concrete Volume 1.32m3, Reinforcing 317kg (due to rev 2 steel already being ordered), Ducts 1 x 100mm. Operator Mat decreased by: Area 0.75m2, Depth is the same. |  |  |  | 5608.67 | 5608.67
B | O | There was no pricing under item 2.1.17 for modifying the SCADA/RTU systems and settings for the Tie Lines 1 & 2 relocation so a variation for this work has arisen as a result of updating the OTA RTU and modifying some SCADA wiring. Variation includes SCADA wiring and config download and testing - OTA RTU (TX42316/8 Re-designed and 'as built'). |  |  |  | 2391.45 | 2391.45
B | O | Technician and management time associated with the additional changes to the SPO and Commissioning Plans as a result of the cancelled outages (8/3 - 16/3/08). Price includes coordination with Transpower and TSL release coordinator. |  |  |  | 2700.17 | 2700.17
B | O | Expose power cables running across the newly positioned DIS65 in bay 50. Cap with 100mm PVC conduit and denso tape. Photo taken |  |  |  | 326.99 | 326.99
B | O | Locate earth grid cables between the 110kV OTA and GT switchyards (excavation and reinstatement. This variation includes the time spent investigating the completeness of the existing earthgrid and testing to ascertain connectivity. This does not include the variation works to install a new connection between the two switchyards. It does however include the investigative work for proposing a new cable route. |  |  |  | 7165.81 | 7165.81
B | O | Ferrule changes in ODJB62 and CB/CT62 (Drawings superseded under transmittal issue 84-1 of 20 Feb). Please note: work completed prior to drawings being superseded. |  |  |  | 805.93 | 805.93
B | O | Supply and installation of 6 transition/adaptor plates for CT62. Please refer to CQ019. |  |  |  | 984.25 | 984.25
B | O | Incorrect wiring in CB62 mech boxe as per Design drawings and manufacturing drawings issued. Please refer to CQ 44. Specifically the cable numbering was quite different to both the construction drawings & the Areva drawing for the same [Dwg 6 000 003] contained with the operation instruction folder retained with the mech box. This was a result of an early model CB being supplied. This variation includes the time spent sourcing the appropriate Areva drawings, making the changes and 'As Builds". |  |  |  | 2038.3525 | 2038.3525
B | O | Additional 2c 2.5mm PVC PVC SWA cable run between CB62 - ODJB62 - control room at 189m for the CB62 motor supply. Please refer to DQ 13. We unable to use the CB222 cable as per Maunsell design as CB222 still in service as per Transfield's SPO. |  |  |  | 2198.85 | 2198.85
B | O | Lost time incurred as a result of cancelled outages on the 3's and 5's bus to remove the jumpers between bay 60 & 70 on the weekend of the 8/9th of March. This variation includes the work for both the Saturday and Sunday (removal and restoration of jumpers) including the associated stand down time whilst awaiting operation control feedback on system stability. Unproductive time for Monday 10 of March has also been charged for 4 men. |  |  |  | 10774.5386 | 10774.5386
B | O | Remove redundant equipment from OTA-OTG 110kV Tie Lines Protection 2 Panel 61 as instructed (please refer to CQ056). Includes 'As Built' drawings. |  |  |  | 1515.01 | 1515.01
B | O | Transmission Line staff were planned and mobilised to site for intended outage work of Item 2.1.1 this was not allowed due to system outage release constraints. This Variation claim is for recovery of planning expended, reviews/adjustments to programme, mobilisation/demobilisation expended and loss of momentum of site crew for an intended work flow and productivity disruption. |  |  |  | 8900.7217 | 8900.7217
B | O | Stations overtime worked during the weekends of the Tie Line 1 & 2 relocation outages (overtime only). As per TSL Tender Schedule 2, Form E, Section 2. |  |  |  | 9178.24 | 9178.24
B | O | Tension spring adjustment for Tie Line 1 take-off points. Extra time involved in fitting tension springs (slotting the girder attachments) and investigation. |  |  |  | 744.78 | 744.78
B | O | Stainless Steel bolt replacements on jumpers between bay 60 & 70 for the relocation of Tie Lines 1 & 2. |  |  |  | 502.99 | 502.99
B | O | Rotate transverse bus in Bay 60 during the outage. Original layout had dropper tails at the opposite end to the terminal span attachment point. Work conducted on a Sunday during the outage. Two knuckle booms and a hiab required. |  |  |  | 4367.37 | 4367.37
B | O | Constructability of the 220kV cable trench through bay 60 resulted in the repositioning ODJB 1R (SCADA cabling) instead of ODJB62, neither of which was in the original price. Includes supply and installation of 250m of 0.6mm 7pair cable for cables run from primary equipment around other bays to the ODJB. Foundation installed by Tunnel & Civil. The main cable back to the control room was retained, however all points required testing after repositioning and termination of new cabling. Please refer to CQ60 & 43 and ODP-PF-43. |  |  |  | 15719.49 | 15719.49
B | O | Two 415V LV AC supply cables running between ODJB62 and ODJB48 were embeded in the old VT2 foundation. Two new cables (4 core 16mm PVC SWA) were required to be run between the ODJB's. This variation includes trenching between cable trenches, concrete cutting of the cable trench, supply and installation of the cable and termination. |  |  |  | 6470.58 | 6470.58
B | O | Tie Line 1 & 2 protection and SCADA issues. DQ18 - CB62 missing SCADA Alarms (5 hours for M. Scrimgeour). ODP-FP-166 - CB62, CB Fail Timers settings confirmation sheets issue (14 hours for M. Scrimgeour). Variation includes Technician time to raise and rectify the issues & 2 hours PE time. |  |  |  | 1740.43 | 1740.43
B | O | 220kV OTA-PEN 5 & 6(C) Deviation |  |  |  | 0 | 0
B | O | Install hardwood pole to provide temporary deviation of OTC | 3627 | 1671 | 5298 | -5297.71 | 0.29
B | O | Install temporary deviation for OTC via 110kV tower 1/2 (via hardwood pole) | 12949 | 18336 | 31285 | -31285 | 0
B | O | Install new 220kV tower 3F | 39028 | 18689 | 57717 | 20188.9452 | 77905.9452
B | O | Temporary modifications to OTA-PEN cct Tower T1 | 12949 | 26795 | 39744 | -39744.14 | -0.14
B | O | Restring Transmission line OTA-PEN 6 circuits on new towers | 12949 | 9706 | 22655 | 48865.9368 | 71520.9368
B | O | Restring Transmission line OTA-PEN 5 circuits on new towers | 12949 | 9706 | 22655 | 21812.4645 | 44467.4645
B | O | Modify and strengthen other towers as required | 12949 | 26795 | 39744 | 0 | 39744
B | O | Relocate PEN 6 line from temporary deviation to new 3B Tower | 8633 | 3233 | 11866 | 61659.16 | 73525.16
B | O | Remove existing 220kV OTA-PEN tower T1 | 22273 | 12588 | 34861 | 0 | 34861
B | O | Remove existing 220kV OTA-PEN tower T2 | 22273 | 10559 | 32832 | -8113.75 | 24718.25
B | O | Remove Temporary hardwood pole | 3627 | 2132 | 5759 | -5759 | 0
B | O | Install earth wire and connections | 4317 | 4048 | 8365 | -81.2098 | 8283.7902
B | O | Conductor and termination of PEN 5 to GIS gantry (Gantry by others) | 8633 | 2714 | 11347 | 5726.4445 | 17073.4445
B | O | Modify protection, control and SCADA panels | 0 | 0 | 0 | 0 | 0
B | O | Test and commission | 2176 | 924 | 3100 | 0 | 3100
B | O | Test and commission Scope included changes to the protection system, not just setting changes |  |  |  | 47825 | 47825
B | O | Contractor to Specify | 0 | 0 | 0 | 0 | 0
B | O | remove conductorfrom gantry to t1 pen6 | 10881 | 18807 | 29688 | 0 | 29688
B | O | remove conductorfrom gantry to t1 pen5 | 10881 | 18807 | 29688 | 0 | 29688
B | O | transfer cct 6 across face of tower 3D | 8633 | 7940 | 16573 | 0 | 16573
B | O | access metal for sites | 0 | 20000 | 20000 | 0 | 20000
B | O | install cross arm on Tower 3E | 7944 | 31750 | 39694 | 0 | 39694
B | O | Transfer cct 6 across face of tower 3D (Price includes the setting up of gear line outage and swinging the conductor across the face of the tower to new position). Now: Temporary OTA 'C' bonding/jumpering at TWR 1A See attached separate Lines pricing sheet and refer Neville Cole's email of 21 June 2010 |  |  |  | 29290.0909 | 29290.0909
B | O | Amend E & SC pond to accommodate pylon base for tower foundation of 3D (Bulldozer 3hrs, compactor 3hrs, excavator 2.5hrs, and supervisor 3hrs). |  |  |  | 1833.8 | 1833.8
B | O | OTG-OTA Earth bond variation. During cut to fill activities it was discovered that the earth bond wire between OTG & OTA had a significant portion of the wire cut and removed by unknown parties. Under separate variations. TSL have located and tested the continuity of the conductors [refer VPR 18026]. Transpower have requested the earth wire be replaced over the entire route. Likewise Contact Energy requested that their section be thrust as they did not want their service road "open cut". Price also includes termination provision for testing at specified locations in OTA & OTG. |  |  |  | 86140.25 | 86140.25
B | O | OPGW relocation old twr 2 - 3B OPGW from Highbrook contract was terminated on to old twr 2 of OTA-PEN before new twr 3B was built. Transfer OPGW from old twr 2 to new 3B & terminate, thread OPGW into twr body & secure down inside twr leg to an available joint box position 3m above ground (Note: excludes fibre jointing and ground laid fibre installation and hanging of joint box) |  |  |  | 6384.0191 | 6384.0191
B | O | Carry out 4 x Twr Earth Resistively Tests (related to items 2.2.7 through to 2.2.10) |  |  |  | 2178.0267 | 2178.0267
B | O | Tie Line 2 Insulator assembly adjustment & Shackle supply When installing and making-off conductors from Twrs 1/2 to 2/2 the Strain Insulator Set specified (479) on drawing TP63381, Sh1, revA has 2 issues. 1/ The L02 2028 shackles are not suppose to connect on to a round section twr attachment point (flat on round… NOT Std) We rearranged hardware to Std (round on round). 2/ The L02 2028 shackles do not fit the Twr attachment points the clevis opening of the shackle is not big enough. We purchased rigging shackles that could be permanent fixings. |  |  |  | 2619.2573 | 2619.2573
Item not included in extract
A | U | 40_30 Vector Cable Relocation & LS Supply |  |  |  |  | 683175.69
10817.3785
Overspend Category/Subcategory Summary $k
|  | Stormwater Drainage Subtotal (A-S) |  |  |  |  | 2182.778
|  | Wastewater Drainage Subtotal (A-W) |  |  |  |  | 1274.7881
|  | Underground Services Relocation Subtotal (A-U) |  |  |  |  | 1255.3931
|  | Warehouse Building Relocation (Subtotal A-B) |  |  |  |  | 1082.7991
|  | Earthworks and General (Subtotal A-E) |  |  |  |  | 2041.2538
|  | Earthworks Civil General Subtotal (A) |  |  |  |  | 7837.0121
|  | 220 Kv Tower Piled Foundations and Installation (B-F) |  |  |  |  | 1728.3115
|  | Other Transmission Line Deviation (B-O) |  |  |  |  | 1252.0548
|  | Transmission Line Deviations Subtotal (B) |  |  |  |  | 2980.3663
|  | Total Earthworks and Transmission Line Deviation |  |  |  |  | 10817.3785
|  | Check |  |  |  |  | 0
Note on H294: oakdeng: Includes Vector relocation in 40_30

## 2. Transmission Line Deviations
Otahuhu 220 kV diversity - extract from PAD estimate workbook |  |  | Summary
From PAD workbook: Enabling Works OTA - PEN C | [15 empty] | Prepared By: | Transpower - John Heaney
[5 empty] | Checked / reviewed by: | [11 empty] | Transpower - Daniel Crawshay
values entered by the user |  |  |  |  | Date of Estimate: | [11 empty] | 2007-09-18
System populated - please don't alter unless adding in non standard items | [7 empty] | Estimate revision: | [8 empty] | 3
Drop down pick list | [14 empty] | Revision date:
[8 empty] | Pricebook Version: | [8 empty] | B08
[8 empty] | Pricebook Date | [8 empty] | 2006-06-12
Site / Region |  | ota | Otahuhu | NNI
Design
Locality Factor labour |  |  | 0% |  | Building layouts and design | [7 empty] | 3%
Switching costs - operator costs |  | Low | 1720 |  | Transmission design | [7 empty] | 8%
Switching costs - operator costs |  | Low | 1720 |  | Civil, structural design | [7 empty] | 5%
[5 empty] | Primary Equipment layout & design | [7 empty] | 3%
[5 empty] | Transformer Design / Selection | [7 empty] | 3%
[5 empty] | Protection design and settings | [7 empty] | 25%
[5 empty] | SCADA Design and Management | [7 empty] | 8%
[5 empty] | Secondary Equipment layouts & design | [7 empty] | 15%
[5 empty] | Communications design | [7 empty] | 15%
Management
Transpower
[6 empty] | Transpower Management | [6 empty] | 2%
[6 empty] | Project Support group costs (Procurement/Inventory, Warehousing, Contract Support) | [6 empty] | 3% | 12000 | 2.5% | 480000
[6 empty] | Transformers (Project Support Group, Procurement & Factory Inspects) | [6 empty] | 2% | 24000 |  | 12000
[6 empty] | Transformers (TP PM) | [6 empty] | 1%
Consultants
[6 empty] | Engineer to Contract (including ETC representative) | [6 empty] | 7%
[6 empty] | Project Doucmentation (Design consultants) | [6 empty] | 0.5%
[6 empty] | Transformers (ETC, Factory Inspects) | [6 empty] | 1.9%
[5 empty] | Contractor Overheads |  |  |  |  | 27144 |  |  | 10.25%
[5 empty] | Contractors Project Management |  |  |  |  | 27144 |  |  | 4%
[5 empty] | Site Establishment /Disestablishment |  |  |  |  | 0 |  |  | 1.25%
[5 empty] | Station Operating Information |  |  |  |  | 0 |  |  | 1.5%
[5 empty] | Project Setup / Design /site meetings |  |  |  |  | 0 |  |  | 2%
[5 empty] | Contractor Travel / accommodation |  |  |  |  | 0 |  |  | 1%
[5 empty] | Insurances |  |  |  |  | 0 |  |  | 0.5%
All Costs are in NZ$ and exclude GST
Description | Code | Qty | UOM | Material | Install | Material totals (1a) | Install Subtotals (1b) | Sub Total $000's (1 ) | Design $000's (2) | Management $000's (3) | Project Support Costs (3a) | Contractor Overheads (4) | Site Factor $000's (5) | Sub Total (1A+2+3+3a+4+5) $000's | Manual Adjustments % | Total $000's
Line materials
OTA-PEN C Deviation
Remove existing 220 kV tower |  | 1 | Sum | 0 | 15000 | 0 | 15000 | 15 | 1.2 | 1.43 | 0 | 1.54 | 0 | 19.17 |  | 19.17
New 220 kV Towers |  | 4 | Sum | 95000 | 15000 | 380000 | 60000 | 440 | 35.2 | 41.8 | 9.5 | 6.15 | 0 | 532.65 |  | 532.65
Deviate Transmission line OTA-PEN 5& 6 ccts |  | 1 | Sum | 50000 | 450000 | 50000 | 450000 | 500 | 40 | 47.5 | 1.25 | 46.13 | 0 | 634.88 |  | 634.88
Modify and strengthen other towers as required |  | 1 | Sum | 50000 | 150000 | 50000 | 150000 | 200 | 16 | 19 | 1.25 | 15.38 | 0 | 251.63 |  | 251.63
[6 empty] | 480000 | 660000 | 1155 | 92.4 | 109.73 | 12 | 69.2 | 0 | 1438.33 |  | 1438.33
Protection
220 kV
Modification to existing OTA-PEN C line protection schemes as required |  | 2 | No | 0 | 5000 | 0 | 10000 | 10 | 2.5 | 0.95 | 0 | 1.03 | 0 | 14.48 |  | 14.48
[6 empty] | 0 | 10000 | 10 | 2.5 | 0.95 | 0 | 1.03 | 0 | 14.48 | 0 | 14.48
Switching Costs
|  | 5 | days | 0 | 1720 | 0 | 8600 | 8.6 |  | 0.82 | 0 | 0.88 |  | 10.3 |  | 10.3
[6 empty] | 0 | 8600 | 8.6 | 0 | 0.82 | 0 | 0.88 |  | 10.3 |  | 10.3
Sub Total ($000's) | [5 empty] | 480000 | 678600 | 1173.6 | 94.9 | 111.5 | 12 | 71.11 | 0 | 1463.11 | 0 | 1463.11
FALSE
Interest during construction |  |  |  | 4.8% |  |  |  | 56.33 | 4.56 | 5.35 | 0.58 | 3.41 | 0 | 70.23 | 0 | 70.23
Contingency |  |  |  | 10% |  |  |  | 117.36 | 9.49 | 11.15 | 1.2 | 7.11 | 0 | 146.31 | 0 | 146.31
Total Estimated Cost ($000's) | [7 empty] | 1347.29 | 108.95 | 128 | 13.78 | 81.63 | 0 | 1679.65 | 0 | 1679.65
Note on B1: Do not change as this comes from Summary Sheet

## 3.Enabling Wks - General Civil
Otahuhu 220 kV diversity - extract of from PAD estimate workbook |  |  | Summary
From PAD workbook: General Civil works (Enabling Works) | [15 empty] | Prepared By: | Transpower - John Heaney
[5 empty] | Checked / reviewed by: | [11 empty] | Transpower - Daniel Crawshay
values entered by the user |  |  |  |  | Date of Estimate: | [11 empty] | 2007-09-18
System populated - please don't alter unless adding in non standard items | [7 empty] | Estimate revision: | [8 empty] | 3
Drop down pick list | [14 empty] | Revision date:
[8 empty] | Pricebook Version: | [8 empty] | B08
[8 empty] | Pricebook Date | [8 empty] | 2006-06-12
Site / Region |  | ota | Otahuhu | NNI
Design
Locality Factor labour |  |  | 0% |  | Building layouts and design | [7 empty] | 3%
Switching costs - operator costs |  | Low | 1720 |  | Transmission design | [7 empty] | 8%
Switching costs - operator costs |  | Low | 1720 |  | Civil, structural design | [7 empty] | 5%
[5 empty] | Primary Equipment layout & design | [7 empty] | 3%
[5 empty] | Transformer Design / Selection | [7 empty] | 3%
[5 empty] | Protection design and settings | [7 empty] | 25%
[5 empty] | SCADA Design and Management | [7 empty] | 8%
[5 empty] | Secondary Equipment layouts & design | [7 empty] | 15%
[5 empty] | Communications design | [7 empty] | 15%
Management
Transpower
[6 empty] | Transpower Management | [6 empty] | 1%
[6 empty] | Project Support group costs (Procurement/Inventory, Warehousing, Contract Support) | [6 empty] | 3% | 12000
[6 empty] | Transformers (Project Support Group, Procurement & Factory Inspects) | [6 empty] | 2% | 24000
[6 empty] | Transformers (TP PM) | [6 empty] | 1%
Consultants
[6 empty] | Engineer to Contract (including ETC representative) | [6 empty] | 5%
[6 empty] | Project Doucmentation (Design consultants) | [6 empty] | 0.5%
[6 empty] | Transformers (ETC, Factory Inspects) | [6 empty] | 1.9%
[5 empty] | Contractor Overheads |  |  |  |  | 101442.002 |  |  | 10.25%
[5 empty] | Contractors Project Management |  |  |  |  | 101442.002 |  |  | 4%
[5 empty] | Site Establishment /Disestablishment |  |  |  |  | 0 |  |  | 1.25%
[5 empty] | Station Operating Information |  |  |  |  | 0 |  |  | 1.5%
[5 empty] | Project Setup / Design /site meetings |  |  |  |  | 0 |  |  | 2%
[5 empty] | Contractor Travel / accommodation |  |  |  |  | 0 |  |  | 1%
[5 empty] | Insurances |  |  |  |  | 0 |  |  | 0.5%
All Costs are in NZ$ and exclude GST
Description | Code | Qty | UOM | Material | Install | Material totals (1a) | Install Subtotals (1b) | Sub Total $000's (1 ) | Design $000's (2) | Management $000's (3) | Project Support Costs (3a) | Contractor Overheads (4) | Site Factor $000's (5) | Sub Total (1A+2+3+3a+4+5) $000's | Manual Adjustments % | Total $000's
Buildings
Form new 15 m wide "lean to" to perimeter of Benmore shed | #N/A | 1 | Sum | 0 | 445250.0488 | 0 | 445250.0488 | 445.3 | 22.27 | 28.94 | 0 | 45.64 | 0 | 542.15 |  | 542.15
Remove existing office/ emergency accommodation including foundations and services | #N/A | 1 | Sum | 0 | 12000 | 0 | 12000 | 12 | 0.6 | 0.78 | 0 | 1.23 | 0 | 14.61 |  | 14.61
Remove the large steel framed warehouse including breaking out foundations and services | #N/A | 1 | Sum | 0 | 50000 | 0 | 50000 | 50 | 2.5 | 3.25 | 0 | 5.13 | 0 | 60.88 |  | 60.88
Remove the three existing Nissan sheds including breaking out foundations and services | #N/A | 1 | Sum | 0 | 25000 | 0 | 25000 | 25 | 1.25 | 1.63 | 0 | 2.56 | 0 | 30.44 |  | 30.44
Modify Transfield carparking and fence line |  | 1 | item | 0 | 150000 | 0 | 150000 | 150 | 4.5 | 9.75 | 0 | 15.38 | 0 | 179.63 |  | 179.63
Other Warehouse Relocation Costs |  | 1 | item | 0 | 180000 | 0 | 180000 | 180 | 5.4 | 11.7 | 0 | 18.45 | 0 | 215.55 |  | 215.55
[6 empty] | 0 | 862250.0488 | 862.3 | 36.52 | 56.05 | 0 | 88.39 | 0 | 1043.26 |  | 1043.26
Civil Works (Bulk excavation, fences, roads etc)
Strip top soil from site average 300mm thick, stock pile for future use or disposal off site | CWK_-___-1- | 22000 | m2 | 0 | 2.9 | 0 | 63800 | 63.8 | 3.19 | 4.15 | 0 | 6.54 | 0 | 77.68 |  | 77.68
Bulk earthworks (Bulk excavation down to formation level -average 1.0m deep, fill up to base level 500mm of fill, but excludes final switchyard metalling) | CWK_-___-2- | 22000 | m2 | 0 | 53 | 0 | 1166000 | 1166 | 58.3 | 75.79 | 0 | 119.52 | 0 | 1419.61 |  | 1419.61
Roads (based on 5m wide x 0.3m thick basecourse, asphalt surface, concrete kerb and channel | CWK_-___-4-____ | 300 | m | 0 | 230 | 0 | 69000 | 69 | 3.45 | 4.49 | 0 | 7.07 | 0 | 84.01 |  | 84.01
Modify existing stormwater services connect Contact Sewer into Manhole at Sparky's Rd | #N/A | 1 | Sum | 0 | 50000 | 0 | 50000 | 50 | 2.5 | 3.25 | 0 | 5.13 | 0 | 60.88 |  | 60.88
New Manhole to sewer system at Sparkys Road | #N/A | 1 | Sum | 0 | 100000 | 0 | 100000 | 100 | 5 | 6.5 | 0 | 10.25 | 0 | 121.75 |  | 121.75
New Manhole to sewer system at Hellaby's Road | #N/A | 1 | Sum | 0 | 100000 | 0 | 100000 | 100 | 5 | 6.5 | 0 | 10.25 | 0 | 121.75 |  | 121.75
Modify existingwater services if required | #N/A | 1 | Sum | 0 | 100000 | 0 | 100000 | 100 | 5 | 6.5 | 0 | 10.25 | 0 | 121.75 |  | 121.75
Modify existing other servcies and fences as required | #N/A | 1 | Sum | 0 | 25000 | 0 | 25000 | 25 | 1.25 | 1.63 | 0 | 2.56 | 0 | 30.44 |  | 30.44
[6 empty] | 0 | 1673800 | 1673.8 | 83.69 | 108.81 | 0 | 171.57 | 0 | 2037.87 |  | 2037.87
Sub Total ($000's) | [5 empty] | 0 | 2536050.0488 | 2536.1 | 120.21 | 164.86 | 0 | 259.96 | 0 | 3081.13 | 0 | 3081.13
FALSE
Interest during construction |  |  |  | 4.8% |  |  |  | 121.73 | 5.77 | 7.91 | 0 | 12.48 | 0 | 147.89 | 0 | 147.89
Contingency |  |  |  | 10% |  |  |  | 253.61 | 12.02 | 16.49 | 0 | 26 | 0 | 308.11 | 0 | 308.11
Total Estimated Cost ($000's) | [7 empty] | 2911.44 | 138 | 189.26 | 0 | 298.44 | 0 | 3537.13 | 0 | 3537.13
[16 empty] | 3389.24 | Total Excl IDC
Overspend Category Item Split
[16 empty] | 66.968 | A - S Stormwater
[16 empty] | 267.85 | A - W Wastewater
[16 empty] | 167.409 | A - U Underground Services
[16 empty] | 1147.586 | A - B Building
[16 empty] | 1739.43 | A - E Earthworks
3389.243
Note on B1: Do not change as this comes from Summary Sheet

## Checks
Worksheet name |  | CHECKS
Summary Sheet |  | 0
Actual Breakdown |  | 0
Cost Assignment
| TOTALS | 0
| % | 0
| % | 0