## Cover
QUALITY PATH
Planned SAIDI/SAIFI MODEL
Final
2017-06-02
Document information
Author: | Powerco
Created:
Last updated: | 2017-06-02
Status: | Final

## Approach
Purpose
This model builds up a complete profile for the Planned SAIDI Forecast 2017-2027 through a combination of historical trending and planned deltas during the forecast period
a) trending historical SAIDI FY11-FY15 as a base-line of work tasks which are expected to continue without significant change during the forecast period
b) forecasting required uplift in future SAIDI based on expected increases (or decreases) in future planned Capex and Opex works
Forecasting Approach
Forecast figures are based on determineing the expected uplift (work deltas) across Powerco's planned Capex (e.g. asset renewals, automation installs) and Opex (e.g. insulator replacements, vegetation works) works.
Primary inputs are as below:
Base SAIDI
Outside of key CPP areas where analysis has shown uplift is required, it is expected that the base-line of network Capex and Opex work tasks, and their mix, will continue as they have historically according to existing asset management practices.
As such, this model forms this base SAIDI based on This is a record of historic SAIDI (disclosed), rolled-forward to act as a baseline of future SAIDI FY17-FY27 of historic SAIDI.
SAIDI/asset figure
Derived from analysis of historic planned outages Outdef (FY04-FY14), NAPA (FY15-FY16) linked to work orders data
Network Development allocation
Uses FY16 Growth & Security Capex base rate, and prorates additional SAIDI/SAIFI requirements Capex based on forecast Growth & Security & Automation Uplift
Renewals allocation
This is a copy of the the forecast Renewal quantities by year and type
Direct Network Opex allocation
Forecast changes in Opex - new work (quantities x rate) and prorated allocation by expenditure
Structure
Workbook colour coding
Input worksheets are
Calculation worksheets are
Output worksheets are
Grouping/guidance worksheets are
Worksheet structure
Direct input cells are:
Inputs from other model outputs
| Worksheet Type | Worksheets | Description
| Input | Inputs & Calcs | Modelling inputs and initial calculations
| Calcs | Work quantities to SAIDI SAIFI | Calculation of asset renewals quantity uplift and blended SAIDI/SAIFI per asset rates
| Output | Outputs | Calculation of SAIDI SAIFI baseline and CPP programme driven uplift
| Output | Summary Output | Summarised output SAIDI SAIFI forecast
End

## Inputs & Calcs
Inputs
Portfolio |  | Quality of Supply
Author |  | Kewen Kueh
Status |  | Draft
Last modified |  | 2017-06-03
Asset Data last refreshed
Base SAIDI/SAIFI
Historic SAIDI/SAIFI Figures
FY12-FY16 is used to set the baseline forecast SAIDI/SAIFI, which includes both storm weather years and benign weather years, as well as renewals ramp ups in the recent years
Source: CPP quality path - calc and output.xlsx (consistent with previously disclosed information)
Reliability measure | FY08 | FY09 | FY10 | FY11 | FY12 | FY13 | FY14 | FY15 | FY16 | FY17
Planned SAIDI | 36.0329 | 46.2467 | 41.7925 | 56.287 | 30.3594 | 60.0155 | 36.05 | 46.0028 | 48.1279 | 45.8509
Planned SAIFI | 0.1945 | 0.20717 | 0.21174 | 0.26839 | 0.13646 | 0.22567 | 0.15024 | 0.19577 | 0.23092 | 0.22747
Historic Thresholds
Planned SAIDI Weightings
This allows Planned SAIDI overall totals to be weighting between Planned/Unplanned SAIDI. Current DPP (years FY17-FY19) weights Planned SAIDI at 50% of Unplanned SAIDI. Forecast uses weighting of 100%
CPP
Planned SAIDI Weighting | FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
Planned SAIDI | bar: FY17 to CPP FY27
See AMP16 Section 7: Network Targets Table 7.9 DPP reliability targets
SAIDI & SAIFI Unit rates and modifiers
SAIDI & SAIFI per Asset Figures
These are figures for average SAIDI/SAIFI impact per installed asset unit, derived from analysis of historic planned outages (FY04-FY14) and NAPA data (FY15)
Source: SAIDI per asset workbook
|  |  | Large Scale Construction |  | Small Scale Construction
Portfolio | FY17: Fleet; FY18: Sub-fleet; FY19: Avg SAIDI per asset; FY20: Avg SAIFI per asset; CPP FY21: Avg SAIDI per asset; CPP FY22: Avg SAIFI per asset
Overhead Structures | FY17: Poles; FY18: Low Voltage; FY19: 0.000506; FY20: 3.1445e-06; CPP FY21: 0.000506; CPP FY22: 3.1445e-06
Overhead Structures | FY17: Poles; FY18: Distribution; FY19: 0.0019; FY20: 3.136e-05; CPP FY21: 0.012065; CPP FY22: 4.082e-05
Overhead Structures | FY17: Poles; FY18: Subtransmission; FY19: 0.010943; FY20: 3.978e-05; CPP FY21: 0.010943; CPP FY22: 3.978e-05
Overhead Structures | FY17: Crossarms; FY18: Low Voltage; FY19: 1.67e-05; FY20: 5.439e-08; CPP FY21: 1.67e-05; CPP FY22: 5.439e-08
Overhead Structures | FY17: Crossarms; FY18: Distribution; FY19: 0.0018156; FY20: 2.1271e-06; CPP FY21: 0.0049881; CPP FY22: 1.7011e-05
Overhead Structures | FY17: Crossarms; FY18: Subtransmission; FY19: 0.0007409; FY20: 3.104e-06; CPP FY21: 0.0007409; CPP FY22: 3.104e-06
Overhead Conductor | FY17: Conductor; FY18: Low Voltage; FY19: 0.00352; FY20: 4.641e-06; CPP FY21: 0.00352; CPP FY22: 4.641e-06
Overhead Conductor | FY17: Conductor; FY18: Distribution; FY19: 0.040601; FY20: 0.00010542; CPP FY21: 0.1045; CPP FY22: 0.00026585
Overhead Conductor | FY17: Conductor; FY18: Subtransmission; FY19: 3.534e-06; FY20: 1.224e-08; CPP FY21: 3.534e-06; CPP FY22: 1.224e-08
Distribution Transformers | FY17: Pole Mounted Transformers; FY18: Pole Mounted Transformers; FY19: 0.0058017; FY20: 2.6819e-05; CPP FY21: 0.0058017; CPP FY22: 2.6819e-05
Distribution Transformers | FY17: Pole Mounted Transformers; FY18: LV Fusing; FY19: 0.0058017; FY20: 2.6819e-05; CPP FY21: 0.0058017; CPP FY22: 2.6819e-05
Distribution Transformers | FY17: Ground Mounted Transformers; FY18: Ground Mounted Transformers; FY19: 0.017179; FY20: 8.379e-05; CPP FY21: 0.017179; CPP FY22: 8.379e-05
Distribution Transformers | FY17: Distribution Other; FY18: Distribution Other; FY19: 0.017179; FY20: 8.379e-05; CPP FY21: 0.017179; CPP FY22: 8.379e-05
Distribution Switchgear | FY17: Pole Mounted Switches; FY18: Air Break; FY19: 0.010844; FY20: 5.695e-05; CPP FY21: 0.010844; CPP FY22: 5.695e-05
Distribution Switchgear | FY17: HV Fuses; FY18: HV Fuses; FY19: 0.00044; FY20: 4e-06; CPP FY21: 0.00044; CPP FY22: 4e-06
Distribution Switchgear | FY17: Ground Mounted Switchgear; FY18: RMU; FY19: 0.024874; FY20: 0.00016719; CPP FY21: 0.024874; CPP FY22: 0.00016719
Distribution Switchgear | FY17: Circuit Breakers/Reclosers/Sectionalisers; FY18: Circuit Breakers/Reclosers/Sectionalisers; FY19: 0.02232; FY20: 7e-05; CPP FY21: 0.02232; CPP FY22: 7e-05
Cables | FY17: Low Voltage Cables; FY18: Cables; FY19: 0.1281; FY20: 0.00045925; CPP FY21: 0.1281; CPP FY22: 0.00045925
Cables | FY17: Distribution Cables; FY18: Cables; FY19: 0.2121; FY20: 0.00060895; CPP FY21: 0.2121; CPP FY22: 0.00060895
Cables | FY17: Subtransmission Cables; FY18: Cables; FY19: 0.0049; FY20: 0.000187; CPP FY21: 0.0049; CPP FY22: 0.000187
Automation | FY17: Automation; FY18: Automation; FY19: 0.036897; FY20: 0.017179; CPP FY21: 0.036897; CPP FY22: 0.017179
Small Scale vs. Large Scale ratios
Percentage small scale (vs. large scale) construction works - used to combine small scale vs. large scale values.
Current percentage splits come out of OutDef analysis looking at curve fit result of historical planned SAIDI/asset figures representing small scale/large scale and totalling associated quantities
Source: SAIDI per asset workbook
CPP
Portfolio | Fleet | Sub-fleet | FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
Overhead Structures | Poles | Low Voltage | 36% | 40% | 40% | 36% | 36% | 36% | 36% | 36% | 36% | 36% | 36%
Overhead Structures | Poles | Distribution | 36% | 40% | 40% | 36% | 36% | 36% | 36% | 36% | 36% | 36% | 36%
Overhead Structures | Poles | Subtransmission | 36% | 40% | 40% | 36% | 36% | 36% | 36% | 36% | 36% | 36% | 36%
Overhead Structures | Crossarms | Low Voltage | 36% | 40% | 40% | 36% | 36% | 36% | 36% | 36% | 36% | 36% | 36%
Overhead Structures | Crossarms | Distribution | 36% | 40% | 40% | 36% | 36% | 36% | 36% | 36% | 36% | 36% | 36%
Overhead Structures | Crossarms | Subtransmission | 36% | 40% | 40% | 36% | 36% | 36% | 36% | 36% | 36% | 36% | 36%
Overhead Conductor | Conductor | Low Voltage | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11%
Overhead Conductor | Conductor | Distribution | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11%
Overhead Conductor | Conductor | Subtransmission | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11% | 11%
Distribution Transformers | Pole Mounted Transformers | Pole Mounted Transformers | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Distribution Transformers | Pole Mounted Transformers | LV Fusing | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Distribution Transformers | Ground Mounted Transformers | Ground Mounted Transformers | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Distribution Transformers | Distribution Other | Distribution Other | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Distribution Switchgear | Pole Mounted Switches | Air Break | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Distribution Switchgear | HV Fuses | HV Fuses | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Distribution Switchgear | Ground Mounted Switchgear | RMU | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Distribution Switchgear | Circuit Breakers/Reclosers/Sectionalisers | Circuit Breakers/Reclosers/Sectionalisers | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Cables | Low Voltage Cables | Cables | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
Cables | Distribution Cables | Cables | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
Cables | Subtransmission Cables | Cables | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
Live line/Deadline allowances
There is expected to be increases in the work carried out dead. These inputs determine the allowance of SAIDI increase due to the increased amount of work being performed dead
Source: Operational experience
Changes in Worksafe means there is a possible future change in the amount of allowable live works to take place. Asset replaced live-line have no (or greatly reduced) SAIDI impact, so the effect of this input is to allow (1) decrease future renewal quantities by the "Percentage of work currently performed live" (assumes amount of live line works will remain consistent with today's levels), and then (2) apply a modification to add back in asset quantities that now have SAIDI impact (decrease in live line quantities)
Portfolio | Fleet | Sub-fleet | FY17: Percentage of work currently performed live; FY18: Percentage increase in deadline work during CPP
Overhead Structures | Poles | Low Voltage | FY17: 10%; FY18: 20%
Overhead Structures | Poles | Distribution | FY17: 10%; FY18: 20%
Overhead Structures | Poles | Subtransmission | FY17: 10%; FY18: 20%
Overhead Structures | Crossarms | Low Voltage | FY17: 10%; FY18: 20%
Overhead Structures | Crossarms | Distribution | FY17: 10%; FY18: 20%
Overhead Structures | Crossarms | Subtransmission | FY17: 10%; FY18: 20%
Overhead Conductor | Conductor | Low Voltage | FY17: 10%; FY18: 20%
Overhead Conductor | Conductor | Distribution | FY17: 10%; FY18: 20%
Overhead Conductor | Conductor | Subtransmission | FY17: 10%; FY18: 20%
Distribution Transformers | Pole Mounted Transformers | Pole Mounted Transformers | bar: FY17 to FY18
Distribution Transformers | Pole Mounted Transformers | LV Fusing | FY17: 10%; FY18: 20%
Distribution Transformers | Ground Mounted Transformers | Ground Mounted Transformers | bar: FY17 to FY18
Distribution Transformers | Distribution Other | Distribution Other | bar: FY17 to FY18
Distribution Switchgear | Pole Mounted Switches | Air Break | FY17: 10%; FY18: 20%
Distribution Switchgear | HV Fuses | HV Fuses | FY17: 10%; FY18: 20%
Distribution Switchgear | Ground Mounted Switchgear | RMU | bar: FY17 to FY18
Distribution Switchgear | Circuit Breakers/Reclosers/Sectionalisers | Circuit Breakers/Reclosers/Sectionalisers | bar: FY17 to FY18
Cables | Low Voltage Cables | Cables | bar: FY17 to FY18
Cables | Distribution Cables | Cables | bar: FY17 to FY18
Cables | Subtransmission Cables | Cables | bar: FY17 to FY18
Baseline SAIDI modification
The SAIDI/SAIFI baseline will contain our historic quantity of live works, at an accumulated level. Changes to the amount of work carried out live line affects the SAIDI/SAIFI impact within our baseline of works
Source: Operational experience
CPP
| FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
Percentage of work currently performed Live | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
Percentage increase in deadline work during CPP | 0% | 0% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20%
Asset Renewals historic and forecast Quantities
Baseline quantities (historical)
Baselined last three years (FY14/15/16) corresponding with ramping up of renewal expenditure. Figures from Fleet asset renewals models
Portfolio | Fleet | Sub-fleet | FY12 | FY13 | FY14 | FY15 | FY16 | Average | Source
Overhead Structures | Poles | Low Voltage | 299 | 435 | 761 | 669 | 1056 | 828.6667 | 1.1 Poles Expenditure Forecast Model
Overhead Structures | Poles | Distribution | 1064 | 999 | 2354 | 1608 | 1603 | 1855 | 1.1 Poles Expenditure Forecast Model
Overhead Structures | Poles | Subtransmission | 180 | 95 | 241 | 184 | 173 | 199.3333 | 1.1 Poles Expenditure Forecast Model
Overhead Structures | Crossarms | Low Voltage | 1214.416 | 1257.4758 | 1691.4819 | 1864.6182 | 2051.1848 | 1869.095 | 1.2 Crossarm expenditure forecast model, corrected LV/Dist/Subtrans quantity splits
Overhead Structures | Crossarms | Distribution | 2147.4127 | 2589.7699 | 2893.913 | 2978.4862 | 2881.2596 | 2917.8863 | 1.2 Crossarm expenditure forecast model, corrected LV/Dist/Subtrans quantity splits
Overhead Structures | Crossarms | Subtransmission | 485.5376 | 480.7813 | 371.068 | 623.516 | 871.8119 | 622.132 | 1.2 Crossarm expenditure forecast model, corrected LV/Dist/Subtrans quantity splits
Overhead Conductor | Conductor | Low Voltage | 1.6 | 2.9 | 5.2 | 10.4 | 7.2 | 7.6 | 2.3 LV Conductor expenditure forecast model
Overhead Conductor | Conductor | Distribution | 20.586 | 49.573 | 110.004 | 51.369 | 61.446 | 74.273 | 2.2 Distribution Conductor expenditure forecast model
Overhead Conductor | Conductor | Subtransmission | 0 | 0 | 0.1 | 0.5 | 0.6 | 0.4 | 2.1 - Subtransmission Conductor expenditure forecast model
Distribution Transformers | Pole Mounted Transformers | Pole Mounted Transformers | 281 | 294 | 373 | 308 | 435 | 372 | 5.1 Distribution Transformers - Pole Mounted - expenditure forecast model
Distribution Transformers | FY17: Pole Mounted Transformers; FY18: LV Fusing; CPP FY24: 294; CPP FY25: 5.1 Distribution Transformers - Pole Mounted - expenditure forecast model
Distribution Transformers | Ground Mounted Transformers | Ground Mounted Transformers | 65 | 69 | 81 | 85 | 98 | 88 | 5.2 Distribution Transformers - Ground Mounted - expenditure forecast model
Distribution Transformers | Distribution Other | Distribution Other | 1 | 0 | 0 | 7 | 10 | 5.6667 | 5.3 Distribution Transformers - Other - expenditure forecast model
Distribution Switchgear | Pole Mounted Switches | Air Break | 173 | 161 | 188 | 138 | 157 | 161 | 6.2 Distribution Switchgear - Pole Mount Switchgear - expenditure forecast model
Distribution Switchgear | HV Fuses | HV Fuses | 334 | 300 | 427 | 565 | 682 | 558 | 6.1 Distribution Switchgear - Fuses - expenditure forecast model
Distribution Switchgear | Ground Mounted Switchgear | RMU | 30 | 42 | 46 | 62 | 52 | 53.3333 | 6.4 Distribution Switchgear - Ground Mount Switchgear - forecast model
Distribution Switchgear | Circuit Breakers/Reclosers/Sectionalisers | Circuit Breakers/Reclosers/Sectionalisers | 6 | 9 | 17 | 18 | 16 | 17 | 6.3 Distribution Switchgear - CBs, Recl and Sect - expenditure forecast model
Cables | Low Voltage Cables | Cables | 0.51256 | 1.3714 | 1.7197 | 2.0299 | 1.4248 | 1.7248 | 3.3 LV Cable Fleet - expenditure forecast model
Cables | Distribution Cables | Cables | 4.809 | 10.342 | 3.393 | 8.731 | 2.742 | 4.9553 | 3.3 Distribution Cable Fleet - expenditure forecast model
Cables | Subtransmission Cables | Cables | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 Subtrans Cable Fleet - expenditure forecast model
Forecast Quantities
Forecast renewal quantities from renewals forecast expenditure models
CPP
Portfolio | Fleet | Sub-fleet | FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27 | Source
Overhead Structures | Poles | Low Voltage | 518.254 | 518.854 | 614.494 | 732.094 | 854.1761 | 837.579 | 786.9853 | 708.2533 | 613.3094 | 610.0473 | 607.4018 | 1.1 Poles Expenditure Forecast Model | 787 | 0.001872%
Overhead Structures | Poles | Distribution | 2356.2211 | 2440.3911 | 3045.2451 | 3719.5791 | 3882.7196 | 4186.0038 | 4261.8857 | 4182.0906 | 3932.0966 | 3916.8934 | 3909.4272 | 1.1 Poles Expenditure Forecast Model | 4262 | 0.002681%
Overhead Structures | Poles | Subtransmission | 213.4121 | 135.2329 | 164.5856 | 187.6465 | 197.2519 | 190.8886 | 185.9842 | 167.9894 | 146.6392 | 147.0365 | 147.4364 | 1.1 Poles Expenditure Forecast Model | 186 | 0.008491%
Overhead Structures | Crossarms | Low Voltage | 1906.4977 | 1910.7377 | 2685.4577 | 2830.6577 | 3723.2193 | 3885.758 | 4143.2441 | 3654.3002 | 3084.3721 | 3162.6514 | 3237.8307 | 1.2 Crossarm expenditure forecast model | 4143.2441 | 0%
Overhead Structures | Crossarms | Distribution | 2715.0219 | 2779.6219 | 3909.0419 | 4230.4219 | 4945.637 | 5359.9351 | 5846.936 | 5407.1891 | 4782.226 | 4852.1723 | 4918.5046 | 1.2 Crossarm expenditure forecast model | 5846.936 | 0%
Overhead Structures | Crossarms | Subtransmission | 796.1423 | 758.315 | 1101.6507 | 1529.3019 | 1062.9798 | 744.123 | 318.1055 | 152.1505 | 148.8687 | 153.2266 | 157.5871 | 1.2 Crossarm expenditure forecast model | 318.1055 | 0%
Overhead Conductor | Conductor | Low Voltage | 7.8771 | 8.6648 | 16.5728 | 24.4808 | 32.3888 | 39.773 | 46.9997 | 51.0662 | 55.3216 | 59.7236 | 64.2536 | 2.3 LV Conductor expenditure forecast model | 47 | 0.0005912%
Overhead Conductor | Conductor | Distribution | 71.103 | 83.412 | 117.528 | 151.271 | 218.072 | 283.6332 | 318.011 | 338.1399 | 341.1741 | 343.2294 | 344.1937 | 2.2 Distribution Conductor expenditure forecast model | 318.011 | -7.243e-07%
Overhead Conductor | Conductor | Subtransmission | 17.5738 | 15.5042 | 14.0336 | 12.6661 | 13.7609 | 16.5952 | 16.5712 | 16.575 | 16.575 | 16.575 | 16.575 | 2.1 - Subtransmission Conductor expenditure forecast model | 16.6 | 0.1737%
Distribution Transformers | Pole Mounted Transformers | Pole Mounted Transformers | 330.1683 | 325.3745 | 330.1896 | 335.6059 | 338.9366 | 341.4178 | 341.7976 | 345.3424 | 353.5325 | 355.0217 | 355.7259 | 5.1 Distribution Transformers - Pole Mounted - expenditure forecast model | 342 | 0.05923%
Distribution Transformers | Pole Mounted Transformers | LV Fusing | 429 | 429 | 429 | 429 | 429 | 429 | 429 |  |  |  |  | 5.1 Distribution Transformers - Pole Mounted - expenditure forecast model | 429 | 0%
Distribution Transformers | Ground Mounted Transformers | Ground Mounted Transformers | 53.8351 | 55.5991 | 89.4904 | 90.2924 | 92.0405 | 93.087 | 94.0845 | 95.7723 | 97.453 | 99.1258 | 101.5475 | 5.2 Distribution Transformers - Ground Mounted - expenditure forecast model | 94 | -0.08977%
Distribution Transformers | Distribution Other | Distribution Other | 1 | 2 | 2 | 1 | 1 | 0.9875 | 1.95 | 1.95 | 0.975 | 0 | 0.975 | 5.3 Distribution Transformers - Other - expenditure forecast model | 2 | 2.564%
Distribution Switchgear | Pole Mounted Switches | Air Break | 146.405 | 141.405 | 142.405 | 111.405 | 95.405 | 91.5675 | 72.205 | 80.005 | 89.755 | 102.43 | 118.03 | 6.2 Distribution Switchgear - Pole Mount Switchgear - expenditure forecast model | 72 | -0.2839%
Distribution Switchgear | HV Fuses | HV Fuses | 467.4241 | 448.1235 | 454.6876 | 465.6823 | 468.2676 | 474.0883 | 480.6792 | 473.0055 | 483.2511 | 499.0028 | 517.4216 | 6.1 Distribution Switchgear - Fuses - expenditure forecast model | 481 | 0.06673%
Distribution Switchgear | Ground Mounted Switchgear | RMU | 60 | 60 | 67.692 | 73.2612 | 80.5873 | 87.7562 | 77.688 | 65.2353 | 50.8353 | 35.8924 | 18.0901 | 6.4 Distribution Switchgear - Ground Mount Switchgear - forecast model | 78 | 0.4016%
Distribution Switchgear | Circuit Breakers/Reclosers/Sectionalisers | Circuit Breakers/Reclosers/Sectionalisers | 14.7143 | 26.5143 | 27.5143 | 27.5143 | 25.5143 | 25.5143 | 12.7143 | 6 | 6 | 6 | 7 | 6.3 Distribution Switchgear - CBs, Recl and Sect - expenditure forecast model | 13 | 2.247%
Cables | Low Voltage Cables | Cables | 6.8646 | 7.3795 | 7.9329 | 8.5279 | 9.1675 | 9.7319 | 10.3294 | 11.1041 | 11.9369 | 12.8321 | 13.7945 | 3.3 LV Cable Fleet - expenditure forecast model | 10.3294 | 1.738e-08%
Cables | Distribution Cables | Cables | 8.5565 | 8.9333 | 10.6998 | 11.6887 | 12.1745 | 9.3956 | 7.7454 | 7.5333 | 7.16 | 7.1792 | 7.8999 | 3.3 Distribution Cable Fleet - expenditure forecast model | 7.75 | 0.05894%
Cables | Subtransmission Cables | Cables | 7.1 | 0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 Subtrans Cable Fleet - expenditure forecast model | 0 | #DIV/0!
Network Opex allowances
Nework Opex (Volume changes)
These are Opex activities which are currently scheduled, but have an expected uplift during FY17-FY27 and thus will require SAIDI allowance above what is available in historical SAIDI counts.
The approach is to baseline FY16 KPI and associated expenditure, and prorate SAIDI and SAIFI allocation by future expenditure uplift
Vegetation Planned SAIDI and SAIFI FY16 Base
FY16 S-VEG SAIDI | FY17: FY16 S-VEG SAIFI; FY18: FY16 S-VEG Expenditure ($000)
0.89975 | FY17: 0.0039054; FY18: 6026.2417
Source: FY16 base SAIDI SAIFI VM ND and defects.xlsx | FY17: Source: FY16 base SAIDI SAIFI VM ND and defects.xlsx; FY18: Source: Network opex - VM
Vegetation Planned SAIDI and SAIFI Forecast allocation | CPP FY21: CPP
| FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
Forecast S-VEG Expenditure ($000) | 5750 | 5500 | 9939.1772 | 9237.489 | 8956.8137 | 9230.7806 | 8676.707 | 8455.0775 | 7502.0268 | 7502.0268 | 7502.0268
Prorated SAIDI Minutes | 0.85851 | 0.82118 | 1.484 | 1.3792 | 1.3373 | 1.3782 | 1.2955 | 1.2624 | 1.1201 | 1.1201 | 1.1201
Prorated SAIFI | 0.0037264 | 0.0035644 | 0.0064412 | 0.0059865 | 0.0058046 | 0.0059821 | 0.0056231 | 0.0054794 | 0.0048618 | 0.0048618 | 0.0048618
Marginal Increase SAIDI | 0 | 0 | 0.58422 | 0.47946 | 0.43755 | 0.47846 | 0.39573 | 0.36264 | 0.22034 | 0.22034 | 0.22034
Marginal Increase SAIFI | 0 | 0 | 0.0025358 | 0.0020811 | 0.0018992 | 0.0020767 | 0.0017177 | 0.001574 | 0.0009564 | 0.0009564 | 0.0009564
Increased Amber defect expenditure
FY16 SD Defects R-ARR-O SAIDI | FY17: FY16 SD Defects R-ARR-O SAIFI; FY18: FY16 RMI-O ARR-O Expenditure ($000)
1.22 | FY17: 0.0094; FY18: 16510
Source: FY16 base SAIDI SAIFI VM ND and defects.xlsx | FY17: Source: FY16 base SAIDI SAIFI VM ND and defects.xlsx; FY18: Source: Network opex - maintenance step changes
Defect Planned SAIDI and SAIFI Forecast allocation | CPP FY21: CPP
| FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
Forecast RMI-O ARR-O Expenditure | 19390.2341 | 20375.1373 | 23846.0051 | 25951.7536 | 26238.3757 | 24302.0718 | 23785.3694 | 22378.969 | 21038.8337 | 21710.4166 | 21147.6236
Prorated SAIDI Minutes | 1.4328 | 1.5056 | 1.7621 | 1.9177 | 1.9389 | 1.7958 | 1.7576 | 1.6537 | 1.5547 | 1.6043 | 1.5627
Prorated SAIFI | 0.01104 | 0.011601 | 0.013577 | 0.014776 | 0.014939 | 0.013836 | 0.013542 | 0.012742 | 0.011979 | 0.012361 | 0.01204
Marginal Increase SAIDI | 0.21283 | 0.28561 | 0.54209 | 0.69769 | 0.71887 | 0.57579 | 0.53761 | 0.43369 | 0.33466 | 0.38428 | 0.3427
Marginal Increase SAIFI | 0.0016399 | 0.0022006 | 0.0041768 | 0.0053757 | 0.0055389 | 0.0044364 | 0.0041422 | 0.0033415 | 0.0025785 | 0.0029609 | 0.0026404
Summary Network Opex volume change allocations
Source: Network opex - maintenance step changes | CPP FY22: CPP
KPI | Maintenance task | FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
SAIDI | Increased work on Vegetation | 0 | 0 | 0.58422 | 0.47946 | 0.43755 | 0.47846 | 0.39573 | 0.36264 | 0.22034 | 0.22034 | 0.22034
SAIDI | Increased work on Amber Defects | 0.21283 | 0.28561 | 0.54209 | 0.69769 | 0.71887 | 0.57579 | 0.53761 | 0.43369 | 0.33466 | 0.38428 | 0.3427
Total |  | 0.21283 | 0.28561 | 1.1263 | 1.1772 | 1.1564 | 1.0542 | 0.93334 | 0.79632 | 0.555 | 0.60463 | 0.56304
SAIFI | Increased work on Vegetation | 0 | 0 | 0.0025358 | 0.0020811 | 0.0018992 | 0.0020767 | 0.0017177 | 0.001574 | 0.0009564 | 0.0009564 | 0.0009564
SAIFI | Increased work on Amber Defects | 0.0016399 | 0.0022006 | 0.0041768 | 0.0053757 | 0.0055389 | 0.0044364 | 0.0041422 | 0.0033415 | 0.0025785 | 0.0029609 | 0.0026404
Total |  | 0.0016399 | 0.0022006 | 0.0067126 | 0.0074568 | 0.0074381 | 0.0065132 | 0.0058599 | 0.0049156 | 0.0035349 | 0.0039173 | 0.0035968
OPEX Deltas (New Tasks)
These are new Opex activities with expected SAIDI impact which will not be accounted for in historical SAIDI counts.
Forecast allocations are carried out using a Quantity x Unit rate approach. Quantities sourced from bottom up Opex delta forecasts, rates used are SAIDI/Asset SAIFI/Asset from Outdef/NAPA analysis
Source:
CPP
Maintenance task | SAIDI Assessement | Notes | Per annum quantity | FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
Insulator replacements - sub transmission | 1, Yes 2, this work may involve replacing insulators for whicha safety notice prevents being done energised, or may be in area where live line work is not possible on N Security circuits |  | 70.2 |  |  | 0.052011 | 0.052011 | 0.052011 | 0.052011 | 0.052011 | 0.052011 | 0.052011 | 0.052011 | 0.052011
Dist transformer & kiosk repairs/overhauls/painting mtce | 1, Yes 2, this may require the shutting down of transformers to effect the repairs |  | 44.9 |  |  | 0.77135 | 0.77135 | 0.77135 | 0.77135 | 0.77135 | 0.77135 | 0.77135 | 0.77135 | 0.77135
Storm hardening network feeders | 1, Yes 2, likely this work will require shutdowns due to terrain, conductor size and condition |  | 50 |  |  | 0.2983 | 0.27797 | 0.27797 | 0.27797 | 0.27797 | 0.27797 | 0.27797 | 0.27797 | 0.27797
Vacuum circuit breaker interrupter replacements | 1, Yes 2, there is a small possibilty that SAIDI maybe required for this work |  | 6.8 |  |  | 0.15178 | 0.15178 | 0.15178 | 0.15178 | 0.15178 | 0.15178 | 0.15178 | 0.15178 | 0.15178
HV fuse element replacement due to fire hazard | 1, yes 2, isolation of 11kV fuses incur SAIDI (assuming customers de-energised) |  | 100 |  |  | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044
Service line maintenance (which we took on 3 or 4 years ago) | 1, yes 2, generally terrain and economics will mean this work needs to b e done de-energised |  | 2 |  |  | 0.09526 | 0.09526 | 0.09526 | 0.09526 | 0.09526 | 0.09526 | 0.09526 | 0.09526 | 0.09526
Legal obligation re height over road | 1, yes 2, if the work involves HV roadcrossing it is likely to incur SAIDI |  | 2.5 |  |  | 0.11907 | 0.11907 | 0.11907 | 0.11907 | 0.11907 | 0.11907 | 0.11907 | 0.11907 | 0.11907
Defective insulator replacements - distribution 11KV | 1, Yes, 2, likely that some of this work will need to be done de-energised |  | 66.6667 |  |  | 0.20564 | 0.19718 | 0.19718 | 0.19718 | 0.19718 | 0.19718 | 0.19718 | 0.19718 | 0.19718
Decommisioning old redundant network lines | 1, yes 2, possibly the need to have outages to do this work |  | 1 |  |  | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763
Total |  |  |  | 0 | 0 | 1.785 | 1.7563 | 1.7563 | 1.7563 | 1.7563 | 1.7563 | 1.7563 | 1.7563 | 1.7563
CPP
Maintenance task | SAIDI Assessement | Notes | Per annum quantity | FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
Insulator replacements - sub transmission | 1, Yes 2, this work may involve replacing insulators for whicha safety notice prevents being done energised, or may be in area where live line work is not possible on N Security circuits |  | 70.2 |  |  | 0.0002179 | 0.0002179 | 0.0002179 | 0.0002179 | 0.0002179 | 0.0002179 | 0.0002179 | 0.0002179 | 0.0002179
Dist transformer & kiosk repairs/overhauls/painting mtce | 1, Yes 2, this may require the shutting down of transformers to effect the repairs |  | 44.9 |  |  | 0.0037622 | 0.0037622 | 0.0037622 | 0.0037622 | 0.0037622 | 0.0037622 | 0.0037622 | 0.0037622 | 0.0037622
Storm hardening network feeders | 1, Yes 2, likely this work will require shutdowns due to terrain, conductor size and condition |  | 50 |  |  | 0.0017572 | 0.0017383 | 0.0017383 | 0.0017383 | 0.0017383 | 0.0017383 | 0.0017383 | 0.0017383 | 0.0017383
Vacuum circuit breaker interrupter replacements | 1, Yes 2, there is a small possibilty that SAIDI maybe required for this work |  | 6.8 |  |  | 0.000476 | 0.000476 | 0.000476 | 0.000476 | 0.000476 | 0.000476 | 0.000476 | 0.000476 | 0.000476
HV fuse element replacement due to fire hazard | 1, yes 2, isolation of 11kV fuses incur SAIDI (assuming customers de-energised) |  | 100 |  |  | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004
Service line maintenance (which we took on 3 or 4 years ago) | 1, yes 2, generally terrain and economics will mean this work needs to b e done de-energised |  | 2 |  |  | 6.289e-06 | 6.289e-06 | 6.289e-06 | 6.289e-06 | 6.289e-06 | 6.289e-06 | 6.289e-06 | 6.289e-06 | 6.289e-06
Legal obligation re height over road | 1, yes 2, if the work involves HV roadcrossing it is likely to incur SAIDI |  | 2.5 |  |  | 0.00030766 | 0.00030766 | 0.00030766 | 0.00030766 | 0.00030766 | 0.00030766 | 0.00030766 | 0.00030766 | 0.00030766
Defective insulator replacements - distribution 11KV | 1, Yes, 2, likely that some of this work will need to be done de-energised |  | 66.6667 |  |  | 0.0082044 | 0.0082044 | 0.0082044 | 0.0082044 | 0.0082044 | 0.0082044 | 0.0082044 | 0.0082044 | 0.0082044
Decommisioning old redundant network lines | 1, yes 2, possibly the need to have outages to do this work |  | 1 |  |  | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307
Total |  |  |  | 0 | 0 | 0.015255 | 0.015236 | 0.015236 | 0.015236 | 0.015236 | 0.015236 | 0.015236 | 0.015236 | 0.015236
Network Development allowance
Exact Growth related quantities are complex to obtain given the relatively small minutes allocated to this area, so allocation is performed top down via expenditure. Majority of works performed at Subtransmission level will have mitigations applied to decrease SAIDI impact, which lowers the overall impact of Growth & Security works on the Planned SAIDI SAIFI KPI
SAIDI SAIFI allocation restricted to Network work of Growth & Security and Reliability (Automation) SAIDI allowance and expenditure, as these are by majority associated with network reconfigurations specificially.
FY16 S-GRO + R-GRO + S-QOS SAIDI | FY16 S-GRO + R-GRO + S-QOS SAIFI | FY16 Growth & Security + Reliability Expenditure ($M)
8.5925 | 0.038066 | 30286.6119
Source: FY16 base SAIDI SAIFI VM ND and defects.xlsx | Source: FY16 base SAIDI SAIFI VM ND and defects.xlsx
CPP
| FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
Forecast Growth Expenditure | 39057.3947 | 49784.4701 | 60051.1964 | 54455.7866 | 57276.1261 | 58517.7183 | 55620.2566 | 50430.7019 | 49075.528 | 52195.9854 | 46667.6376
Prorated SAIDI Minutes | 11.0808 | 14.1241 | 17.0369 | 15.4494 | 16.2496 | 16.6018 | 15.7798 | 14.3075 | 13.923 | 14.8083 | 13.2399
Prorated SAIFI Minutes | 0.04909 | 0.062573 | 0.075477 | 0.068444 | 0.071989 | 0.073549 | 0.069907 | 0.063385 | 0.061682 | 0.065604 | 0.058655
Marginal Increase SAIDI | 2.4883 | 5.5317 | 8.4444 | 6.8569 | 7.6571 | 8.0093 | 7.1873 | 5.715 | 5.3305 | 6.2158 | 4.6474
Marginal Increase SAIFI | 0.011024 | 0.024506 | 0.03741 | 0.030378 | 0.033922 | 0.035483 | 0.031841 | 0.025318 | 0.023615 | 0.027537 | 0.020589
End
Note on D37: Author: Associated with large-scale planned works and BLITZ type jobs
Note on F37: Author: Associated with small scale works, reactive defect replacement etc.
Note on D239: Author: 1053 insulators over 5 years, 3 insulators per arm, ~30% Subtransmisison is N-security. Ref Subtransmission xarm replacement
Note on D240: Author: 449 sites over 5 years, assume 50% require shut. Ref Dist GM Transformer replacement
Note on D241: Author: 1x feeder length per year over 5 years, average 50 poles. Ref Dist Poles replacement
Note on D242: Author: 34 over 5 years. Ref CB/Recloser/Sectionaliser replacement
Note on D243: Author: 100 per year. Ref HV Fuse replacement
Note on D244: Author: 20 per year, equivalent to 100m each. Ref Dist Conductor replacement
Note on D245: Author: 50/year, assume 5m each. Ref Dist Conductor replacement
Note on D246: Author: 200/year, 3 insulators per arm. Ref Dist Crossarm replacement
Note on D247: Author: 10 per year, assume 100m each. Ref Dist Conductor Replacement
Note on D252: Author: 1053 insulators over 5 years, 3 insulators per arm, ~30% Subtransmisison is N-security. Ref Subtransmission xarm replacement
Note on D253: Author: 449 sites over 5 years, assume 50% require shut. Ref Dist GM Transformer replacement
Note on D254: Author: 1x feeder length per year over 5 years, average 50 poles. Ref Dist Poles replacement
Note on D255: Author: 34 over 5 years. Ref CB/Recloser/Sectionaliser replacement
Note on D256: Author: 100 per year. Ref HV Fuse replacement
Note on D257: Author: 20 per year, equivalent to 100m each. Ref Dist Conductor replacement
Note on D258: Author: 50/year, assume 5m each. Ref Dist Conductor replacement
Note on D259: Author: 200/year, 3 insulators per arm. Ref Dist Crossarm replacement
Note on D260: Author: 10 per year, assume 100m each. Ref Dist Conductor Replacement

## Q_Forecast_All (hidden)
Select DTU Type | Grand Total
Select DTU RR | All Condition Driven RR Detail
Unit Cost | #REF!
Age | No of Assets | Retirement Rate | Renew 14/15 | Surv 14/15 | Renew 15/16 | Surv 15/16 | Renew 16/17 | Surv 16/17 | Renew 17/18 | Surv 17/18 | Renew 18/19 | Surv 18/19 | Renew 19/20 | Surv 19/20 | Renew 20/21 | Surv 20/21 | Renew 21/22 | Surv 21/22 | Renew 22/23 | Surv 22/23 | Renew 23/24 | Surv 22/232
0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
28 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
29 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
30 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
31 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
32 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
33 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
34 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
35 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
36 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
37 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
38 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
39 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
40 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
41 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
42 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
43 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
44 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
45 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
46 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
47 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
48 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
49 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
50 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
51 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
52 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
53 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
54 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
55 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
56 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
57 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
58 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
59 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
60 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
61 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
62 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
63 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
64 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
65 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
66 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
67 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
68 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
69 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
70 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
71 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
72 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
73 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
74 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
75 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
76 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
77 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
78 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
79 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
80 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
81 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
82 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
83 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
84 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
85 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
86 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
87 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
88 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
89 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
90 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
91 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
TOTALS | 0 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Graph Data Export
FYE | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24
Renewals | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total Cost | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## Work quantities to SAIDI SAIFI
Outputs
Incrememental SAIDI/SAIFI Based on Planned works
Activity Uplift and associated SAIDI impact
Incorporates Small scale/large scale ratio and efficiency allowance
SAIDI | [6 empty] | CPP
Portfolio | Fleet | Sub-fleet | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
Overhead Structures | Poles | Low Voltage | 0.000506 | 0.000506 | 0.000506 | 0.000506 | 0.000506 | 0.000506 | 0.000506 | 0.000506 | 0.000506 | 0.000506 | 0.000506
Overhead Structures | Poles | Distribution | 0.0055594 | 0.005966 | 0.005966 | 0.0055594 | 0.0055594 | 0.0055594 | 0.0055594 | 0.0055594 | 0.0055594 | 0.0055594 | 0.0055594
Overhead Structures | Poles | Subtransmission | 0.010943 | 0.010943 | 0.010943 | 0.010943 | 0.010943 | 0.010943 | 0.010943 | 0.010943 | 0.010943 | 0.010943 | 0.010943
Overhead Structures | Crossarms | Low Voltage | 1.67e-05 | 1.67e-05 | 1.67e-05 | 1.67e-05 | 1.67e-05 | 1.67e-05 | 1.67e-05 | 1.67e-05 | 1.67e-05 | 1.67e-05 | 1.67e-05
Overhead Structures | Crossarms | Distribution | 0.0029577 | 0.0030846 | 0.0030846 | 0.0029577 | 0.0029577 | 0.0029577 | 0.0029577 | 0.0029577 | 0.0029577 | 0.0029577 | 0.0029577
Overhead Structures | Crossarms | Subtransmission | 0.0007409 | 0.0007409 | 0.0007409 | 0.0007409 | 0.0007409 | 0.0007409 | 0.0007409 | 0.0007409 | 0.0007409 | 0.0007409 | 0.0007409
Overhead Conductor | Conductor | Low Voltage | 0.00352 | 0.00352 | 0.00352 | 0.00352 | 0.00352 | 0.00352 | 0.00352 | 0.00352 | 0.00352 | 0.00352 | 0.00352
Overhead Conductor | Conductor | Distribution | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763 | 0.04763
Overhead Conductor | Conductor | Subtransmission | 3.534e-06 | 3.534e-06 | 3.534e-06 | 3.534e-06 | 3.534e-06 | 3.534e-06 | 3.534e-06 | 3.534e-06 | 3.534e-06 | 3.534e-06 | 3.534e-06
Distribution Transformers | Pole Mounted Transformers | Pole Mounted Transformers | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017
Distribution Transformers | Pole Mounted Transformers | LV Fusing | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017 | 0.0058017
Distribution Transformers | Ground Mounted Transformers | Ground Mounted Transformers | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179
Distribution Transformers | Distribution Other | Distribution Other | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179 | 0.017179
Distribution Switchgear | Pole Mounted Switches | Air Break | 0.010844 | 0.010844 | 0.010844 | 0.010844 | 0.010844 | 0.010844 | 0.010844 | 0.010844 | 0.010844 | 0.010844 | 0.010844
Distribution Switchgear | HV Fuses | HV Fuses | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044
Distribution Switchgear | Ground Mounted Switchgear | RMU | 0.024874 | 0.024874 | 0.024874 | 0.024874 | 0.024874 | 0.024874 | 0.024874 | 0.024874 | 0.024874 | 0.024874 | 0.024874
Distribution Switchgear | Circuit Breakers/Reclosers/Sectionalisers | Circuit Breakers/Reclosers/Sectionalisers | 0.02232 | 0.02232 | 0.02232 | 0.02232 | 0.02232 | 0.02232 | 0.02232 | 0.02232 | 0.02232 | 0.02232 | 0.02232
Cables | Low Voltage Cables | Cables | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281
Cables | Distribution Cables | Cables | 0.2121 | 0.2121 | 0.2121 | 0.2121 | 0.2121 | 0.2121 | 0.2121 | 0.2121 | 0.2121 | 0.2121 | 0.2121
Cables | Subtransmission Cables | Cables | 0.0049 | 0.0049 | 0.0049 | 0.0049 | 0.0049 | 0.0049 | 0.0049 | 0.0049 | 0.0049 | 0.0049 | 0.0049
SAIFI |  |  | CPP 2021: CPP
Portfolio | Fleet | Sub-fleet | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
Overhead Structures | Poles | Low Voltage | 3.1445e-06 | 3.1445e-06 | 3.1445e-06 | 3.1445e-06 | 3.1445e-06 | 3.1445e-06 | 3.1445e-06 | 3.1445e-06 | 3.1445e-06 | 3.1445e-06 | 3.1445e-06
Overhead Structures | Poles | Distribution | 3.4766e-05 | 3.5144e-05 | 3.5144e-05 | 3.4766e-05 | 3.4766e-05 | 3.4766e-05 | 3.4766e-05 | 3.4766e-05 | 3.4766e-05 | 3.4766e-05 | 3.4766e-05
Overhead Structures | Poles | Subtransmission | 3.978e-05 | 3.978e-05 | 3.978e-05 | 3.978e-05 | 3.978e-05 | 3.978e-05 | 3.978e-05 | 3.978e-05 | 3.978e-05 | 3.978e-05 | 3.978e-05
Overhead Structures | Crossarms | Low Voltage | 5.439e-08 | 5.439e-08 | 5.439e-08 | 5.439e-08 | 5.439e-08 | 5.439e-08 | 5.439e-08 | 5.439e-08 | 5.439e-08 | 5.439e-08 | 5.439e-08
Overhead Structures | Crossarms | Distribution | 7.4855e-06 | 8.0809e-06 | 8.0809e-06 | 7.4855e-06 | 7.4855e-06 | 7.4855e-06 | 7.4855e-06 | 7.4855e-06 | 7.4855e-06 | 7.4855e-06 | 7.4855e-06
Overhead Structures | Crossarms | Subtransmission | 3.104e-06 | 3.104e-06 | 3.104e-06 | 3.104e-06 | 3.104e-06 | 3.104e-06 | 3.104e-06 | 3.104e-06 | 3.104e-06 | 3.104e-06 | 3.104e-06
Overhead Conductor | Conductor | Low Voltage | 4.641e-06 | 4.641e-06 | 4.641e-06 | 4.641e-06 | 4.641e-06 | 4.641e-06 | 4.641e-06 | 4.641e-06 | 4.641e-06 | 4.641e-06 | 4.641e-06
Overhead Conductor | Conductor | Distribution | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307 | 0.00012307
Overhead Conductor | Conductor | Subtransmission | 1.224e-08 | 1.224e-08 | 1.224e-08 | 1.224e-08 | 1.224e-08 | 1.224e-08 | 1.224e-08 | 1.224e-08 | 1.224e-08 | 1.224e-08 | 1.224e-08
Distribution Transformers | Pole Mounted Transformers | Pole Mounted Transformers | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05
Distribution Transformers | Pole Mounted Transformers | LV Fusing | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05 | 2.6819e-05
Distribution Transformers | Ground Mounted Transformers | Ground Mounted Transformers | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05
Distribution Transformers | Distribution Other | Distribution Other | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05 | 8.379e-05
Distribution Switchgear | Pole Mounted Switches | Air Break | 5.695e-05 | 5.695e-05 | 5.695e-05 | 5.695e-05 | 5.695e-05 | 5.695e-05 | 5.695e-05 | 5.695e-05 | 5.695e-05 | 5.695e-05 | 5.695e-05
Distribution Switchgear | HV Fuses | HV Fuses | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06
Distribution Switchgear | Ground Mounted Switchgear | RMU | 0.00016719 | 0.00016719 | 0.00016719 | 0.00016719 | 0.00016719 | 0.00016719 | 0.00016719 | 0.00016719 | 0.00016719 | 0.00016719 | 0.00016719
Distribution Switchgear | Circuit Breakers/Reclosers/Sectionalisers | Circuit Breakers/Reclosers/Sectionalisers | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05
Cables | Low Voltage Cables | Cables | 0.00045925 | 0.00045925 | 0.00045925 | 0.00045925 | 0.00045925 | 0.00045925 | 0.00045925 | 0.00045925 | 0.00045925 | 0.00045925 | 0.00045925
Cables | Distribution Cables | Cables | 0.00060895 | 0.00060895 | 0.00060895 | 0.00060895 | 0.00060895 | 0.00060895 | 0.00060895 | 0.00060895 | 0.00060895 | 0.00060895 | 0.00060895
Cables | Subtransmission Cables | Cables | 0.000187 | 0.000187 | 0.000187 | 0.000187 | 0.000187 | 0.000187 | 0.000187 | 0.000187 | 0.000187 | 0.000187 | 0.000187
Incremental asset replacement increases
SAIDI |  |  | CPP 2021: CPP
Portfolio | Fleet | Sub-fleet | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
Overhead Structures | Poles | Low Voltage | -269.0063 | -268.4543 | -180.4655 | -72.2735 | 40.0421 | 24.7727 | -21.7736 | -94.207 | -181.5554 | -184.5565 | -186.9903
Overhead Structures | Poles | Distribution | 498.2235 | 575.6599 | 1132.1255 | 1752.5128 | 1902.6021 | 2181.6235 | 2251.4349 | 2178.0234 | 1948.0289 | 1934.0419 | 1927.173
Overhead Structures | Poles | Subtransmission | 16.9391 | -54.9858 | -27.9812 | -6.7653 | 2.0718 | -3.7825 | -8.2945 | -24.8498 | -44.4919 | -44.1264 | -43.7585
Overhead Structures | Crossarms | Low Voltage | 71.7924 | 75.6932 | 788.4356 | 922.0196 | 1743.1763 | 1892.7119 | 2129.599 | 1679.7706 | 1155.4368 | 1227.4538 | 1296.6187
Overhead Structures | Crossarms | Distribution | -128.2774 | -68.8454 | 970.221 | 1265.8906 | 1923.8884 | 2305.0427 | 2753.0835 | 2348.5163 | 1773.5503 | 1837.9009 | 1898.9266
Overhead Structures | Crossarms | Subtransmission | 172.5322 | 137.7311 | 453.5999 | 847.039 | 418.0227 | 124.6744 | -267.2617 | -419.9403 | -422.9596 | -418.9503 | -414.9386
Overhead Conductor | Conductor | Low Voltage | 0.40693 | 1.1316 | 8.407 | 15.6824 | 22.9577 | 29.7511 | 36.3997 | 40.1409 | 44.0559 | 48.1057 | 52.2733
Overhead Conductor | Conductor | Distribution | -1.4309 | 9.8933 | 41.2801 | 72.3236 | 133.7805 | 194.0968 | 225.7244 | 244.243 | 247.0345 | 248.9253 | 249.8125
Overhead Conductor | Conductor | Subtransmission | 15.8079 | 13.9039 | 12.5509 | 11.2928 | 12.3 | 14.9076 | 14.8855 | 14.889 | 14.889 | 14.889 | 14.889
Distribution Transformers | Pole Mounted Transformers | Pole Mounted Transformers | -41.8317 | -46.6255 | -41.8104 | -36.3941 | -33.0634 | -30.5822 | -30.2024 | -26.6576 | -18.4675 | -16.9783 | -16.2741
Distribution Transformers | Pole Mounted Transformers | LV Fusing | 130.08 | 130.08 | 130.08 | 130.08 | 130.08 | 130.08 | 130.08 | -264.6 | -264.6 | -264.6 | -264.6
Distribution Transformers | Ground Mounted Transformers | Ground Mounted Transformers | -34.1649 | -32.4009 | 1.4904 | 2.2924 | 4.0405 | 5.087 | 6.0845 | 7.7723 | 9.453 | 11.1258 | 13.5475
Distribution Transformers | Distribution Other | Distribution Other | -4.6667 | -3.6667 | -3.6667 | -4.6667 | -4.6667 | -4.6792 | -3.7167 | -3.7167 | -4.6917 | -5.6667 | -4.6917
Distribution Switchgear | Pole Mounted Switches | Air Break | -10.2074 | -14.8074 | -13.8874 | -42.4074 | -57.1274 | -60.6579 | -78.4714 | -71.2954 | -62.3254 | -50.6644 | -36.3124
Distribution Switchgear | HV Fuses | HV Fuses | -72.1698 | -89.9263 | -83.8874 | -73.7722 | -71.3938 | -66.0388 | -59.9751 | -67.0349 | -57.609 | -43.1174 | -26.1721
Distribution Switchgear | Ground Mounted Switchgear | RMU | 6.6667 | 6.6667 | 14.3587 | 19.9279 | 27.254 | 34.4229 | 24.3547 | 11.902 | -2.498 | -17.441 | -35.2432
Distribution Switchgear | Circuit Breakers/Reclosers/Sectionalisers | Circuit Breakers/Reclosers/Sectionalisers | -2.2857 | 9.5143 | 10.5143 | 10.5143 | 8.5143 | 8.5143 | -4.2857 | -11 | -11 | -11 | -10
Cables | Low Voltage Cables | Cables | 5.1398 | 5.6547 | 6.2082 | 6.8031 | 7.4427 | 8.0071 | 8.6046 | 9.3793 | 10.2121 | 11.1073 | 12.0697
Cables | Distribution Cables | Cables | 3.6012 | 3.9779 | 5.7444 | 6.7333 | 7.2192 | 4.4403 | 2.7901 | 2.578 | 2.2047 | 2.2239 | 2.9446
Cables | Subtransmission Cables | Cables | 7.1 | 0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
End

## Outputs
Outputs
Base SAIDI/SAIFI
Avg. SAIDI FY12-FY16 (to roll forward as Planned SAIDI/SAIFI baseline)
Measure | SAIDI | SAIFI
Quantity | 44.1111 | 0.18781
SAIDI/SAIFI Buildup | [13 empty] | CPP
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
Actual Data Points (Historic) | 36.0329 | 46.2467 | 41.7925 | 56.287 | 30.3594 | 60.0155 | 36.05 | 46.0028 | 48.1279 | 45.8509
Base Planned SAIDI rolled forward | [10 empty] | 44.1111 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914
Total Base SAIDI | 36.0329 | 46.2467 | 41.7925 | 56.287 | 30.3594 | 60.0155 | 36.05 | 46.0028 | 48.1279 | 45.8509 | 44.1111 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914
SAIDI/SAIFI Buildup | [13 empty] | CPP
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
Actual Data Points (Historic) | 0.1945 | 0.20717 | 0.21174 | 0.26839 | 0.13646 | 0.22567 | 0.15024 | 0.19577 | 0.23092 | 0.22747
Base Planned SAIFI rolled forward | [10 empty] | 0.18781 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199
Total Base SAIDI | 0.1945 | 0.20717 | 0.21174 | 0.26839 | 0.13646 | 0.22567 | 0.15024 | 0.19577 | 0.23092 | 0.22747 | 0.18781 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199
Incrememental SAIDI/SAIFI Based on Planned works
Incremental assest replacement increases SAIDI
CPP
Portfolio | Fleet | Sub-fleet | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
Overhead Structures | Poles | Low Voltage | -0.13612 | -0.13584 | -0.091316 | -0.03657 | 0.020261 | 0.012535 | -0.011017 | -0.047669 | -0.091867 | -0.093386 | -0.094617
Overhead Structures | Poles | Distribution | 2.7698 | 3.4344 | 6.7543 | 9.7429 | 10.5773 | 12.1285 | 12.5166 | 12.1085 | 10.8299 | 10.7521 | 10.7139
Overhead Structures | Poles | Subtransmission | 0.18536 | -0.60171 | -0.3062 | -0.074032 | 0.022671 | -0.041392 | -0.090767 | -0.27193 | -0.48688 | -0.48288 | -0.47885
Overhead Structures | Crossarms | Low Voltage | 0.0011989 | 0.0012641 | 0.013167 | 0.015398 | 0.029111 | 0.031608 | 0.035564 | 0.028052 | 0.019296 | 0.020498 | 0.021654
Overhead Structures | Crossarms | Distribution | -0.37941 | -0.21236 | 2.9928 | 3.7442 | 5.6903 | 6.8177 | 8.1429 | 6.9463 | 5.2457 | 5.436 | 5.6165
Overhead Structures | Crossarms | Subtransmission | 0.12783 | 0.10204 | 0.33607 | 0.62757 | 0.30971 | 0.092371 | -0.19801 | -0.31113 | -0.31337 | -0.3104 | -0.30743
Overhead Conductor | Conductor | Low Voltage | 0.0014324 | 0.0039833 | 0.029593 | 0.055202 | 0.080811 | 0.10472 | 0.12813 | 0.1413 | 0.15508 | 0.16933 | 0.184
Overhead Conductor | Conductor | Distribution | -0.068155 | 0.47122 | 1.9662 | 3.4448 | 6.3719 | 9.2448 | 10.7512 | 11.6333 | 11.7662 | 11.8563 | 11.8985
Overhead Conductor | Conductor | Subtransmission | 5.5865e-05 | 4.9136e-05 | 4.4355e-05 | 3.9909e-05 | 4.3468e-05 | 5.2683e-05 | 5.2605e-05 | 5.2618e-05 | 5.2618e-05 | 5.2618e-05 | 5.2618e-05
Distribution Transformers | Pole Mounted Transformers | Pole Mounted Transformers | -0.2427 | -0.27051 | -0.24257 | -0.21115 | -0.19182 | -0.17743 | -0.17523 | -0.15466 | -0.10714 | -0.098504 | -0.094418
Distribution Transformers | Pole Mounted Transformers | LV Fusing | 0.75469 | 0.75469 | 0.75469 | 0.75469 | 0.75469 | 0.75469 | 0.75469 | -1.5351 | -1.5351 | -1.5351 | -1.5351
Distribution Transformers | Ground Mounted Transformers | Ground Mounted Transformers | -0.58693 | -0.55663 | 0.025604 | 0.039381 | 0.069413 | 0.087392 | 0.10453 | 0.13352 | 0.1624 | 0.19113 | 0.23274
Distribution Transformers | Distribution Other | Distribution Other | -0.08017 | -0.062991 | -0.062991 | -0.08017 | -0.08017 | -0.080385 | -0.06385 | -0.06385 | -0.0806 | -0.09735 | -0.0806
Distribution Switchgear | Pole Mounted Switches | Air Break | -0.11069 | -0.16057 | -0.15059 | -0.45986 | -0.61948 | -0.65777 | -0.85093 | -0.77312 | -0.67585 | -0.5494 | -0.39377
Distribution Switchgear | HV Fuses | HV Fuses | -0.031755 | -0.039568 | -0.03691 | -0.03246 | -0.031413 | -0.029057 | -0.026389 | -0.029495 | -0.025348 | -0.018972 | -0.011516
Distribution Switchgear | Ground Mounted Switchgear | RMU | 0.16583 | 0.16583 | 0.35716 | 0.49569 | 0.67792 | 0.85624 | 0.6058 | 0.29605 | -0.062135 | -0.43383 | -0.87664
Distribution Switchgear | Circuit Breakers/Reclosers/Sectionalisers | Circuit Breakers/Reclosers/Sectionalisers | -0.051017 | 0.21236 | 0.23468 | 0.23468 | 0.19004 | 0.19004 | -0.095657 | -0.24552 | -0.24552 | -0.24552 | -0.2232
Cables | Low Voltage Cables | Cables | 0.65841 | 0.72437 | 0.79526 | 0.87148 | 0.95341 | 1.0257 | 1.1022 | 1.2015 | 1.3082 | 1.4228 | 1.5461
Cables | Distribution Cables | Cables | 0.76381 | 0.84372 | 1.2184 | 1.4281 | 1.5312 | 0.94178 | 0.59178 | 0.54679 | 0.46762 | 0.47169 | 0.62455
Cables | Subtransmission Cables | Cables | 0.03479 | 0.00245 | 0 | 0.0049 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Incremental assest replacement increases SAIFI
CPP
Portfolio | Fleet | Sub-fleet | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
Overhead Structures | Poles | Low Voltage | -0.00084589 | -0.00084415 | -0.00056747 | -0.00022726 | 0.00012591 | 7.7898e-05 | -6.8467e-05 | -0.00029623 | -0.0005709 | -0.00058034 | -0.00058799
Overhead Structures | Poles | Distribution | 0.017321 | 0.020231 | 0.039787 | 0.060927 | 0.066145 | 0.075845 | 0.078272 | 0.07572 | 0.067724 | 0.067238 | 0.066999
Overhead Structures | Poles | Subtransmission | 0.00067384 | -0.0021873 | -0.0011131 | -0.00026912 | 8.2415e-05 | -0.00015047 | -0.00032996 | -0.00098852 | -0.0017699 | -0.0017553 | -0.0017407
Overhead Structures | Crossarms | Low Voltage | 3.9048e-06 | 4.117e-06 | 4.2883e-05 | 5.0149e-05 | 9.4811e-05 | 0.00010294 | 0.00011583 | 9.1363e-05 | 6.2844e-05 | 6.6761e-05 | 7.0523e-05
Overhead Structures | Crossarms | Distribution | -0.00096022 | -0.00055633 | 0.0078402 | 0.0094758 | 0.014401 | 0.017254 | 0.020608 | 0.01758 | 0.013276 | 0.013758 | 0.014214
Overhead Structures | Crossarms | Subtransmission | 0.00053554 | 0.00042752 | 0.001408 | 0.0026292 | 0.0012975 | 0.00038699 | -0.00082958 | -0.0013035 | -0.0013129 | -0.0013004 | -0.001288
Overhead Conductor | Conductor | Low Voltage | 1.8886e-06 | 5.2519e-06 | 3.9017e-05 | 7.2782e-05 | 0.00010655 | 0.00013808 | 0.00016893 | 0.00018629 | 0.00020446 | 0.00022326 | 0.0002426
Overhead Conductor | Conductor | Distribution | -0.0001761 | 0.0012175 | 0.0050802 | 0.0089005 | 0.016464 | 0.023887 | 0.027779 | 0.030058 | 0.030401 | 0.030634 | 0.030743
Overhead Conductor | Conductor | Subtransmission | 1.9349e-07 | 1.7018e-07 | 1.5362e-07 | 1.3822e-07 | 1.5055e-07 | 1.8247e-07 | 1.822e-07 | 1.8224e-07 | 1.8224e-07 | 1.8224e-07 | 1.8224e-07
Distribution Transformers | Pole Mounted Transformers | Pole Mounted Transformers | -0.0011219 | -0.0012505 | -0.0011213 | -0.00097605 | -0.00088673 | -0.00082018 | -0.00081 | -0.00071493 | -0.00049528 | -0.00045534 | -0.00043646
Distribution Transformers | Pole Mounted Transformers | LV Fusing | 0.0034886 | 0.0034886 | 0.0034886 | 0.0034886 | 0.0034886 | 0.0034886 | 0.0034886 | -0.0070963 | -0.0070963 | -0.0070963 | -0.0070963
Distribution Transformers | Ground Mounted Transformers | Ground Mounted Transformers | -0.0028627 | -0.0027149 | 0.00012488 | 0.00019208 | 0.00033855 | 0.00042624 | 0.00050982 | 0.00065124 | 0.00079207 | 0.00093223 | 0.0011351
Distribution Transformers | Distribution Other | Distribution Other | -0.00039102 | -0.00030723 | -0.00030723 | -0.00039102 | -0.00039102 | -0.00039207 | -0.00031142 | -0.00031142 | -0.00039311 | -0.00047481 | -0.00039311
Distribution Switchgear | Pole Mounted Switches | Air Break | -0.00058131 | -0.00084328 | -0.00079089 | -0.0024151 | -0.0032534 | -0.0034545 | -0.0044689 | -0.0040603 | -0.0035494 | -0.0028853 | -0.002068
Distribution Switchgear | HV Fuses | HV Fuses | -0.00028868 | -0.00035971 | -0.00033555 | -0.00029509 | -0.00028558 | -0.00026416 | -0.0002399 | -0.00026814 | -0.00023044 | -0.00017247 | -0.00010469
Distribution Switchgear | Ground Mounted Switchgear | RMU | 0.0011146 | 0.0011146 | 0.0024006 | 0.0033317 | 0.0045565 | 0.005755 | 0.0040718 | 0.0019898 | -0.00041763 | -0.0029159 | -0.0058922
Distribution Switchgear | Circuit Breakers/Reclosers/Sectionalisers | Circuit Breakers/Reclosers/Sectionalisers | -0.00016 | 0.000666 | 0.000736 | 0.000736 | 0.000596 | 0.000596 | -0.0003 | -0.00077 | -0.00077 | -0.00077 | -0.0007
Cables | Low Voltage Cables | Cables | 0.0023605 | 0.0025969 | 0.0028511 | 0.0031243 | 0.0034181 | 0.0036773 | 0.0039516 | 0.0043074 | 0.0046899 | 0.005101 | 0.005543
Cables | Distribution Cables | Cables | 0.0021929 | 0.0024224 | 0.0034981 | 0.0041003 | 0.0043961 | 0.0027039 | 0.001699 | 0.0015699 | 0.0013426 | 0.0013542 | 0.0017931
Cables | Subtransmission Cables | Cables | 0.0013277 | 9.35e-05 | 0 | 0.000187 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total SAIDI/SAIFI
Total SAIDI
CPP
Category | Sub-fleet | FY08 | FY09 | FY10 | FY11 | FY12 | FY13 | FY14 | FY15 | FY16 | FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
Historic | Historic | 36.0329 | 46.2467 | 41.7925 | 56.287 | 30.3594 | 60.0155 | 36.05 | 46.0028 | 48.1279 | 45.8509 | 44.1111 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914 | 45.0914
Asset Renewals | Poles | FY18: 2.6968; FY19: 6.3567; FY20: 9.6323; CPP FY21: 10.6203; CPP FY22: 12.0997; CPP FY23: 12.4148; CPP FY24: 11.7889; CPP FY25: 10.2511; CPP FY26: 10.1759; CPP FY27: 10.1405
Asset Renewals | Crossarms | FY18: -0.10905; FY19: 3.342; FY20: 4.3871; CPP FY21: 6.0292; CPP FY22: 6.9417; CPP FY23: 7.9804; CPP FY24: 6.6632; CPP FY25: 4.9516; CPP FY26: 5.1461; CPP FY27: 5.3307
Asset Renewals | Conductor | FY18: 0.47525; FY19: 1.9958; FY20: 3.5; CPP FY21: 6.4528; CPP FY22: 9.3496; CPP FY23: 10.8794; CPP FY24: 11.7746; CPP FY25: 11.9213; CPP FY26: 12.0257; CPP FY27: 12.0826
Asset Renewals | Transformers and other | FY18: -0.13544; FY19: 0.47473; FY20: 0.50275; CPP FY21: 0.55211; CPP FY22: 0.58427; CPP FY23: 0.62014; CPP FY24: -1.6201; CPP FY25: -1.5605; CPP FY26: -1.5399; CPP FY27: -1.4774
Asset Renewals | Distribution Switchgear | FY18: 0.17805; FY19: 0.40433; FY20: 0.23804; CPP FY21: 0.21706; CPP FY22: 0.35945; CPP FY23: -0.36718; CPP FY24: -0.75208; CPP FY25: -1.0089; CPP FY26: -1.2477; CPP FY27: -1.5051
Asset Renewals | Cables | FY18: 1.5705; FY19: 2.0137; FY20: 2.3045; CPP FY21: 2.4846; CPP FY22: 1.9675; CPP FY23: 1.694; CPP FY24: 1.7483; CPP FY25: 1.7758; CPP FY26: 1.8945; CPP FY27: 2.1707
Network Opex | Opex Deltas | FY18: 0.28561; FY19: 2.9114; FY20: 2.9334; CPP FY21: 2.9127; CPP FY22: 2.8105; CPP FY23: 2.6896; CPP FY24: 2.5526; CPP FY25: 2.3113; CPP FY26: 2.3609; CPP FY27: 2.3193
Network Development | Growth & Security + Automation | FY18: 5.5317; FY19: 8.4444; FY20: 6.8569; CPP FY21: 7.6571; CPP FY22: 8.0093; CPP FY23: 7.1873; CPP FY24: 5.715; CPP FY25: 5.3305; CPP FY26: 6.2158; CPP FY27: 4.6474
| Total SAIDI | 36.0329 | 46.2467 | 41.7925 | 56.287 | 30.3594 | 60.0155 | 36.05 | 46.0028 | 48.1279 | 45.8509 | 54.6046 | 71.0344 | 75.4465 | 82.0171 | 87.2133 | 88.1899 | 82.9617 | 79.0637 | 80.1227 | 78.8
| Forecast Increase (CPP) | FY18: 10.4935; FY19: 25.943; FY20: 30.3551; CPP FY21: 36.9258; CPP FY22: 42.122; CPP FY23: 43.0986; CPP FY24: 37.8703; CPP FY25: 33.9723; CPP FY26: 35.0313; CPP FY27: 33.7086
| Total SAIFI | CPP FY21: CPP
Category | Sub-fleet | FY08 | FY09 | FY10 | FY11 | FY12 | FY13 | FY14 | FY15 | FY16 | FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
Historic | Historic | 0.1945 | 0.20717 | 0.21174 | 0.26839 | 0.13646 | 0.22567 | 0.15024 | 0.19577 | 0.23092 | 0.22747 | 0.18781 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199 | 0.19199
Asset Renewals | Poles | FY18: 0.0172; FY19: 0.038107; FY20: 0.060431; CPP FY21: 0.066353; CPP FY22: 0.075773; CPP FY23: 0.077874; CPP FY24: 0.074436; CPP FY25: 0.065384; CPP FY26: 0.064902; CPP FY27: 0.064671
Asset Renewals | Crossarms | FY18: -0.0001247; FY19: 0.0092911; FY20: 0.012155; CPP FY21: 0.015794; CPP FY22: 0.017744; CPP FY23: 0.019894; CPP FY24: 0.016368; CPP FY25: 0.012026; CPP FY26: 0.012524; CPP FY27: 0.012997
Asset Renewals | Conductor | FY18: 0.001223; FY19: 0.0051193; FY20: 0.0089735; CPP FY21: 0.01657; CPP FY22: 0.024025; CPP FY23: 0.027948; CPP FY24: 0.030244; CPP FY25: 0.030606; CPP FY26: 0.030858; CPP FY27: 0.030986
Asset Renewals | Transformers and other | FY18: -0.00078394; FY19: 0.002185; FY20: 0.0023136; CPP FY21: 0.0025494; CPP FY22: 0.0027026; CPP FY23: 0.002877; CPP FY24: -0.0074714; CPP FY25: -0.0071926; CPP FY26: -0.0070942; CPP FY27: -0.0067907
Asset Renewals | Distribution Switchgear | FY18: 0.00057759; FY19: 0.0020101; FY20: 0.0013575; CPP FY21: 0.0016135; CPP FY22: 0.0026324; CPP FY23: -0.00093707; CPP FY24: -0.0031086; CPP FY25: -0.0049675; CPP FY26: -0.0067437; CPP FY27: -0.0087649
Asset Renewals | Cables | FY18: 0.0051128; FY19: 0.0063492; FY20: 0.0074116; CPP FY21: 0.0078142; CPP FY22: 0.0063812; CPP FY23: 0.0056507; CPP FY24: 0.0058773; CPP FY25: 0.0060324; CPP FY26: 0.0064553; CPP FY27: 0.0073361
Network Opex | Opex Deltas | FY18: 0.0022006; FY19: 0.021967; FY20: 0.022693; CPP FY21: 0.022674; CPP FY22: 0.021749; CPP FY23: 0.021096; CPP FY24: 0.020151; CPP FY25: 0.018771; CPP FY26: 0.019153; CPP FY27: 0.018833
Network Development | Growth & Security + Automation | FY18: 0.024506; FY19: 0.03741; FY20: 0.030378; CPP FY21: 0.033922; CPP FY22: 0.035483; CPP FY23: 0.031841; CPP FY24: 0.025318; CPP FY25: 0.023615; CPP FY26: 0.027537; CPP FY27: 0.020589
| Total SAIFI | 0.1945 | 0.20717 | 0.21174 | 0.26839 | 0.13646 | 0.22567 | 0.15024 | 0.19577 | 0.23092 | 0.22747 | 0.23772 | 0.31442 | 0.3377 | 0.35928 | 0.37848 | 0.37823 | 0.3538 | 0.33626 | 0.33958 | 0.33184
| Forecast Increase (CPP) | FY18: 0.049911; FY19: 0.12244; FY20: 0.14571; CPP FY21: 0.16729; CPP FY22: 0.18649; CPP FY23: 0.18624; CPP FY24: 0.16181; CPP FY25: 0.14427; CPP FY26: 0.14759; CPP FY27: 0.13986
End

## Summary Output
Outputs
Forecast Uplift
Summary Planned SAIDI/SAIFI Uplift
CPP
[7 empty] | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
[8 empty] | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast
SAIDI | [6 empty] | 0 | 10.4935 | 25.943 | 30.3551 | 36.9258 | 42.122 | 43.0986 | 37.8703 | 33.9723 | 35.0313 | 33.7086
SAIFI | [6 empty] | 0 | 0.049911 | 0.12244 | 0.14571 | 0.16729 | 0.18649 | 0.18624 | 0.16181 | 0.14427 | 0.14759 | 0.13986
Total Forecasts
Total Planned SAIDI SAIFI
CPP
|  | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
|  | Actual | Actual | Actual | Actual | Actual | Actual | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast
SAIDI |  | 30.3594 | 60.0155 | 36.05 | 46.0028 | 48.1279 | 45.8509 | 54.6046 | 71.0344 | 75.4465 | 82.0171 | 87.2133 | 88.1899 | 82.9617 | 79.0637 | 80.1227 | 78.8
SAIFI |  | 0.13646 | 0.22567 | 0.15024 | 0.19577 | 0.23092 | 0.22747 | 0.23772 | 0.31442 | 0.3377 | 0.35928 | 0.37848 | 0.37823 | 0.3538 | 0.33626 | 0.33958 | 0.33184
| Planned SAIDI | 2019: Planned SAIFI