## CoverSheet
Electricity Distribution Business
Analysis of EDB Performance 2010–2015
Reliability Analysis
Version 1. 8 June 2016

## Description
Description and Status
General Description
The purpose of this model is to assess recent reliability, as measured by SAIDI and SAIFI, against historical reliability and the reliability standards we set for the 2012-2015 DPP reset.

## Table of Contents
Table of Contents
| Sheet Name | Link
| 2003-2007 ID | Financial Performance and Efficiency Measures 2003—2007
| 2005-2014 ZD | DPP s.53 ZD Information request 2005—2014
| 2008-2012 ID | Information Disclosure database 2008—2012
| 2013-2015 ID | Information Disclosure database 2013—2015
| EDB Select + Calculations | EDB Selection and Calculations
| Chart data | Data for graphs
| Charts | Charts for report

## 2003-2007 ID
Financial Performance and Efficiency Measures 2003—2007
Information disclosures—gazette notice pursuant to section 57T of the Commerce Act 1986
Business-specific data
|  | SAIDI - Class B | SAIDI - Class C | SAIDI - Total | SAIFI - Class B | SAIFI - Class C | SAIFI - Total | Number of Interruptions - Class B | Number of Interruptions - Class C | Number of Interruptions - Total | Unplanned Interruptions not restored within 3 hours (%) | Faults per 100km
Alpine Energy | 2003 | 20 | 162 | 204 | 0.1 | 0.9 | 1.1 | 46 | 65 | 113 | 37% | 2.08 | Alpine Energy, 2003
Alpine Energy | 2004 | 12 | 103 | 115 | 0.1 | 1.5 | 1.6 | 42 | 90 | 132 | 27% | 3.2 | Alpine Energy, 2004
Alpine Energy | 2005 | 12 | 57 | 79 | 0.1 | 0.9 | 1 | 43 | 81 | 126 | 21% | 3 | Alpine Energy, 2005
Alpine Energy | 2006 | 8 | 50 | 81 | 0.1 | 1 | 1.3 | 22 | 83 | 108 | 20% | 3.3 | Alpine Energy, 2006
Alpine Energy | 2007 | 70 | 987 | 1138 | 0.3 | 1.5 | 2.5 | 199 | 91 | 299 | 19% | 3 | Alpine Energy, 2007
Aurora Energy | 2003 | 20.5 | 68.6 | 101.3 | 0.15 | 1.36 | 2.08 | 341 | 464 | 809 | 13.7% | 9.6 | Aurora Energy, 2003
Aurora Energy | 2004 | 16.3 | 80 | 97.3 | 0.14 | 1.47 | 1.72 | 293 | 453 | 747 | 16.6% | 9.5 | Aurora Energy, 2004
Aurora Energy | 2005 | 7.3 | 73.2 | 80.5 | 0.07 | 1.39 | 1.46 | 269 | 445 | 714 | 16.63% | 10 | Aurora Energy, 2005
Aurora Energy | 2006 | 11.7 | 70.8 | 96.5 | 0.09 | 1.4 | 1.72 | 258 | 492 | 750 | 13.2% | 11.1 | Aurora Energy, 2006
Aurora Energy | 2007 | 13.2 | 83.5 | 101.4 | 0.1 | 1.59 | 1.82 | 268 | 487 | 756 | 20.1% | 13.1 | Aurora Energy, 2007
Buller Electricity | 2003 | 222 | 144 | 370 | 0.54 | 1.32 | 1.98 | 29 | 44 | 74 | 13.6% | 9.4 | Buller Electricity, 2003
Buller Electricity | 2004 | 165 | 84 | 256 | 1.01 | 1.22 | 2.41 | 44 | 34 | 79 | 5.9% | 6.7 | Buller Electricity, 2004
Buller Electricity | 2005 | 64 | 65 | 134 | 0.44 | 0.78 | 1.34 | 24 | 32 | 57 | 12% | 7.1 | Buller Electricity, 2005
Buller Electricity | 2006 | 108 | 84 | 196 | 0.62 | 1.18 | 1.88 | 39 | 38 | 78 | 6% | 8.2 | Buller Electricity, 2006
Buller Electricity | 2007 | 109 | 53 | 355 | 0.42 | 0.87 | 3.24 | 30 | 37 | 68 | 8% | 8.9 | Buller Electricity, 2007
Centralines | 2003 | 67 | 187 | 260 | 0.49 | 6.42 | 7.22 | 100 | 230 | 331 | 10.3% | 15.3 | Centralines, 2003
Centralines | 2004 | 7 | 375 | 388 | 0 | 7 | 7 | 36 | 230 | 266 | 22% | 23 | Centralines, 2004
Centralines | 2005 | 15.6 | 155.79 | 171.39 | 0.07 | 4.36 | 4.43 | 28 | 168 | 196 | 11.9% | 15.53 | Centralines, 2005
Centralines | 2006 | 41.2 | 99.5 | 153.2 | 0.14 | 4.75 | 5.58 | 62 | 126 | 188 | 5.6% | 17.71 | Centralines, 2006
Centralines | 2007 | 38.97 | 148.08 | 246.6 | 0.12 | 3.04 | 4.19 | 53 | 136 | 189 | 8.1% | 12.31 | Centralines, 2007
Counties Power | 2003 | 12.59 | 79.44 | 92.03 | 0.09 | 2.55 | 2.64 | 48 | 132 | 180 | 20.45% | 6.8 | Counties Power, 2003
Counties Power | 2004 | 3.39 | 93.06 | 96.45 | 0.03 | 2.69 | 2.72 | 33 | 162 | 195 | 18.52% | 7.9 | Counties Power, 2004
Counties Power | 2005 | 4.4 | 55.2 | 59.6 | 0.04 | 2.09 | 2.13 | 43 | 136 | 179 | 16.18% | 6.7 | Counties Power, 2005
Counties Power | 2006 | 8.16 | 53.57 | 61.73 | 0.06 | 1.59 | 1.65 | 63 | 120 | 183 | 10% | 5.8 | Counties Power, 2006
Counties Power | 2007 | 13.8 | 95.69 | 109.49 | 0.16 | 2.96 | 3.12 | 160 | 171 | 331 | 15.2% | 9.8 | Counties Power, 2007
Eastland Network | 2003 | 56.95 | 285.54 | 426.91 | 0.39 | 2.54 | 3.19 | 130 | 214 | 346 | 26.17% | 7 | Eastland Network, 2003
Eastland Network | 2004 | 38.05 | 295.24 | 356.32 | 0.2 | 1.75 | 2.82 | 112 | 247 | 366 | 38.06% | 8 | Eastland Network, 2004
Eastland Network | 2005 | 31 | 249.98 | 282.53 | 0.19 | 1.92 | 2.13 | 123 | 235 | 360 | 34.04% | 7 | Eastland Network, 2005
Eastland Network | 2006 | 27.5 | 321.8 | 358.95 | 0.15 | 2.46 | 2.65 | 89 | 231 | 326 | 64.07% | 7 | Eastland Network, 2006
Eastland Network | 2007 | 18.76 | 237.62 | 261.5 | 0.15 | 3.78 | 3.96 | 93 | 263 | 361 | 34.98% | 8.07 | Eastland Network, 2007
Electra | 2003 | 5.86 | 49.73 | 61.3 | 0.042 | 0.857 | 1.235 | 78 | 88 | 167 | 0% | 7.32 | Electra, 2003
Electra | 2004 | 9.98 | 107.86 | 133.47 | 0.07 | 2.647 | 3.499 | 80 | 118 | 200 | 2.55% | 9.72 | Electra, 2004
Electra | 2005 | 15.23 | 62.97 | 83.86 | 0.09 | 1.47 | 1.95 | 84 | 106 | 191 | 2.8% | 7.87 | Electra, 2005
Electra | 2006 | 17.56 | 51.43 | 93.99 | 0.1 | 1.23 | 2.87 | 88 | 109 | 201 | 3.1% | 8.19 | Electra, 2006
Electra | 2007 | 18.09 | 69.67 | 185.26 | 0.11 | 1.32 | 3.18 | 81 | 128 | 213 | 9.3% | 6.9 | Electra, 2007
Electricity Ashburton | 2003 | 103.8 | 201.37 | 318.86 | 0.38 | 1.51 | 2.4 | 241 | 293 | 534 | 24.57% | 11 | Electricity Ashburton, 2003
Electricity Ashburton | 2004 | 88.61 | 110.02 | 198.63 | 0.3 | 1.17 | 1.47 | 192 | 214 | 406 | 17.29% | 7.8 | Electricity Ashburton, 2004
Electricity Ashburton | 2005 | 78.88 | 53.81 | 132.69 | 0.25 | 0.92 | 1.17 | 197 | 173 | 370 | 24.86% | 6.5 | Electricity Ashburton, 2005
Electricity Ashburton | 2006 | 62.3 | 87.9 | 150.2 | 0.22 | 1.09 | 1.31 | 272 | 204 | 476 | 18.63% | 8.1 | Electricity Ashburton, 2006
Electricity Ashburton | 2007 | 125.1 | 1793.2 | 1918 | 0.39 | 3.18 | 3.57 | 274 | 267 | 541 | 53.93% | 10.6 | Electricity Ashburton, 2007
Electricity Invercargill | 2003 | 2 | 19.4 | 21.4 | 0.01 | 0.69 | 0.7 | 6 | 15 | 21 | 0% | 6.8 | Electricity Invercargill, 2003
Electricity Invercargill | 2004 | 4.5 | 45.1 | 49.6 | 0.03 | 1.25 | 1.28 | 9 | 19 | 28 | 0% | 8.3 | Electricity Invercargill, 2004
Electricity Invercargill | 2005 | 2.1 | 13.3 | 15.4 | 0.03 | 0.25 | 0.28 | 5 | 15 | 20 | 6.67% | 6.67 | Electricity Invercargill, 2005
Electricity Invercargill | 2006 | 0.2 | 18.9 | 19.8 | 0 | 0.54 | 0.55 | 3 | 20 | 24 | 10% | 8.07 | Electricity Invercargill, 2006
Electricity Invercargill | 2007 | 0.3 | 35.3 | 36.7 | 0 | 1.21 | 1.28 | 3 | 18 | 23 | 22.22% | 7.24 | Electricity Invercargill, 2007
Horizon Energy | 2003 | 20 | 77 | 192 | 0.18 | 0.88 | 1.6 | 57 | 80 | 143 | 15% | 4.3 | Horizon Energy, 2003
Horizon Energy | 2004 | 25 | 108 | 219 | 0.15 | 1.1 | 1.62 | 67 | 83 | 155 | 14.46% | 4.6 | Horizon Energy, 2004
Horizon Energy | 2005 | 22 | 331 | 987 | 0.11 | 2.35 | 3.54 | 51 | 125 | 192 | 33.6% | 6.7 | Horizon Energy, 2005
Horizon Energy | 2006 | 31 | 156 | 292 | 0.16 | 1.89 | 2.48 | 68 | 110 | 187 | 25% | 8.5 | Horizon Energy, 2006
Horizon Energy | 2007 | 16 | 140 | 315 | 0.12 | 1.73 | 3.09 | 53 | 92 | 161 | 25% | 8.5 | Horizon Energy, 2007
MainPower NZ | 2003 | 60.83 | 77.87 | 284.35 | 0.26 | 1.46 | 2.7 | 167 | 102 | 274 | 4.6% | 2.97 | MainPower NZ, 2003
MainPower NZ | 2004 | 48.59 | 45.44 | 99.64 | 0.21 | 0.96 | 1.21 | 212 | 82 | 295 | 7.3% | 2.18 | MainPower NZ, 2004
MainPower NZ | 2005 | 49.7782 | 49.5696 | 115.5685 | 0.2178 | 0.7183 | 1.1657 | 236 | 58 | 297 | 25.8% | 1.66 | MainPower NZ, 2005
MainPower NZ | 2006 | 33.3 | 69.86 | 109.17 | 0.1548 | 1.522 | 1.84 | 201 | 107 | 311 | 10.2% | 2.92 | MainPower NZ, 2006
MainPower NZ | 2007 | 31.66 | 185.45 | 236.53 | 0.22 | 1.53 | 2.27 | 217 | 200 | 427 | 34.5% | 5.56 | MainPower NZ, 2007
Marlborough Lines | 2003 | 67.8 | 124.8 | 200.5 | 0.3 | 2 | 2.6 | 329 | 322 | 655 | 15.5% | 6.1 | Marlborough Lines, 2003
Marlborough Lines | 2004 | 52.5 | 141.2 | 222.4 | 0.3 | 1.4 | 3.4 | 277 | 219 | 507 | 29.7% | 8.8 | Marlborough Lines, 2004
Marlborough Lines | 2005 | 93.4 | 119.8 | 224.9 | 0.4 | 1.5 | 2.5 | 259 | 233 | 498 | 27.9% | 9.3 | Marlborough Lines, 2005
Marlborough Lines | 2006 | 93.6 | 166.5 | 260.2 | 0.3 | 2.5 | 2.9 | 267 | 294 | 561 | 25.2% | 11.6 | Marlborough Lines, 2006
Marlborough Lines | 2007 | 108.7 | 155.2 | 353.1 | 0.4 | 2.5 | 4.2 | 274 | 359 | 646 | 34.5% | 14 | Marlborough Lines, 2007
Nelson Electricity | 2003 | 27.43 | 72.13 | 99.56 | 0.16 | 1.27 | 1.43 | 22 | 13 | 35 | 7.7% | 13.55 | Nelson Electricity, 2003
Nelson Electricity | 2004 | 6.6 | 46.6 | 53.2 | 0.3 | 0.5 | 0.8 | 10 | 7 | 17 | 5.9% | 8 | Nelson Electricity, 2004
Nelson Electricity | 2005 | 12.5 | 38.6 | 51 | 0.1 | 0.8 | 0.8 | 25 | 13 | 38 | 15.4% | 14.7 | Nelson Electricity, 2005
Nelson Electricity | 2006 | 12.2 | 10.1 | 122 | 0.1 | 0.2 | 2.2 | 27 | 4 | 33 | 0% | 4.4 | Nelson Electricity, 2006
Nelson Electricity | 2007 | 9.3 | 25.8 | 249.9 | 0.3 | 0.2 | 2.5 | 22 | 8 | 32 | 0% | 10 | Nelson Electricity, 2007
Network Tasman | 2003 | 16.77 | 90.96 | 151.23 | 0.19 | 1.3 | 1.86 | 66 | 118 | 189 | 17% | 5.45 | Network Tasman, 2003
Network Tasman | 2004 | 25.92 | 95.26 | 164.1 | 0.15 | 1.07 | 1.73 | 76 | 101 | 183 | 23% | 4.53 | Network Tasman, 2004
Network Tasman | 2005 | 28.04 | 118.3 | 210.15 | 0.23 | 1.48 | 2.47 | 110 | 126 | 243 | 22% | 5.69 | Network Tasman, 2005
Network Tasman | 2006 | 24.89 | 96.56 | 224.66 | 0.13 | 0.92 | 2.53 | 138 | 97 | 243 | 19% | 4.37 | Network Tasman, 2006
Network Tasman | 2007 | 32.82 | 76.54 | 285.41 | 0.29 | 1.23 | 3.29 | 216 | 117 | 343 | 19% | 5.21 | Network Tasman, 2007
Network Waitaki | 2003 | 29.6 | 62.1 | 91.6 | 0.15 | 1.12 | 1.27 | 68 | 75 | 143 | 13.3% | 4.39 | Network Waitaki, 2003
Network Waitaki | 2004 | 36.7 | 150.3 | 187 | 0.18 | 1.47 | 1.65 | 102 | 109 | 211 | 34.86% | 6.53 | Network Waitaki, 2004
Network Waitaki | 2005 | 61.14 | 43.71 | 104.85 | 0.35 | 1.03 | 1.38 | 202 | 58 | 260 | 13.79% | 3.37 | Network Waitaki, 2005
Network Waitaki | 2006 | 49.79 | 46.95 | 102.31 | 0.29 | 0.92 | 1.91 | 178 | 64 | 243 | 12.5% | 3.29 | Network Waitaki, 2006
Network Waitaki | 2007 | 41.39 | 291.41 | 505.55 | 0.19 | 1.26 | 3.32 | 216 | 100 | 322 | 35% | 5.74 | Network Waitaki, 2007
Northpower | 2003 | 31.96 | 140.53 | 181.83 | 0.21 | 3.57 | 4.07 | 160 | 361 | 523 | 15.7% | 10.66 | Northpower, 2003
Northpower | 2004 | 36.96 | 82.57 | 145.32 | 0.21 | 2.42 | 2.71 | 149 | 256 | 406 | 15.5% | 7.79 | Northpower, 2004
Northpower | 2005 | 28.95 | 67.66 | 113.24 | 0.21 | 1.9 | 2.6 | 251 | 225 | 478 | 16.4% | 6.61 | Northpower, 2005
Northpower | 2006 | 27.57 | 89.46 | 119.23 | 0.17 | 2.19 | 2.47 | 211 | 290 | 502 | 16.8% | 8.33 | Northpower, 2006
Northpower | 2007 | 29.73 | 110.18 | 151.33 | 0.16 | 2.42 | 2.73 | 208 | 310 | 519 | 17.7% | 8.87 | Northpower, 2007
Orion NZ | 2003 | 10 | 86 | 102 | 0.03 | 0.89 | 1.22 | 356 | 611 | 971 | 25.37% | 10.9 | Orion NZ, 2003
Orion NZ | 2004 | 6.5 | 35.9 | 43.4 | 0.02 | 0.59 | 0.63 | 241 | 403 | 656 | 25% | 7.1 | Orion NZ, 2004
Orion NZ | 2005 | 7.7 | 44 | 52.9 | 0.03 | 0.71 | 0.76 | 316 | 462 | 785 | 24.9% | 8 | Orion NZ, 2005
Orion NZ | 2006 | 6 | 53.3 | 64 | 0.02 | 0.72 | 0.96 | 288 | 499 | 792 | 36% | 8.6 | Orion NZ, 2006
Orion NZ | 2007 | 8.8 | 141.3 | 154.5 | 0.03 | 0.65 | 0.72 | 319 | 520 | 854 | 38% | 8.7 | Orion NZ, 2007
OtagoNet | 2003 | 54 | 161.8 | 224.9 | 0.29 | 2.33 | 2.78 | 107 | 171 | 279 | 0% | 4.51 | OtagoNet, 2003
OtagoNet | 2004 | 59 | 395.4 | 503.9 | 0.29 | 2.87 | 3.49 | 115 | 197 | 315 | 14.7% | 5.15 | OtagoNet, 2004
OtagoNet | 2005 | 75.8 | 98 | 194.1 | 0.45 | 1.27 | 2.12 | 153 | 131 | 288 | 6.1% | 3.42 | OtagoNet, 2005
OtagoNet | 2006 | 174.1 | 133 | 313.2 | 0.76 | 1.99 | 3.97 | 295 | 188 | 487 | 17.6% | 4.56 | OtagoNet, 2006
OtagoNet | 2007 | 293.4 | 176.8 | 484.8 | 1.31 | 2.21 | 4.19 | 347 | 230 | 581 | 25.2% | 5.68 | OtagoNet, 2007
Powerco | 2003 | 46.99 | 234.35 | 295.55 | 0.249 | 2.93 | 3.473 | 864 | 1504 | 2409 | 21.32% | 11 | Powerco, 2003
Powerco | 2004 | 21.93 | 304.35 | 370.41 | 0.1114 | 3.258 | 3.787 | 799 | 2344 | 3198 | 25.6% | 13.72 | Powerco, 2004
Powerco | 2005 | 11.12 | 183.43 | 208.32 | 0.095 | 2.651 | 2.915 | 648 | 1888 | 2682 | 24.2% | 11.06 | Powerco, 2005
Powerco | 2006 | 10.6 | 203 | 235.8 | 0.07 | 2.51 | 2.89 | 662 | 1603 | 2354 | 26.3% | 12.92 | Powerco, 2006
Powerco | 2007 | 17.64 | 164.08 | 220.6 | 0.098 | 2.345 | 2.8 | 800 | 1762 | 2683 | 18.1% | 15.27 | Powerco, 2007
Scanpower | 2003 | 24.8 | 57.23 | 110.47 | 0.18 | 0.56 | 0.98 | 82 | 65 | 148 | 18.46% | 5.59 | Scanpower, 2003
Scanpower | 2004 | 33.96 | 151.24 | 185.2 | 0.26 | 1.41 | 1.67 | 97 | 129 | 226 | 32.6% | 17.27 | Scanpower, 2004
Scanpower | 2005 | 38.82 | 32.49 | 71.31 | 0.29 | 0.54 | 0.83 | 86 | 60 | 146 | 6.7% | 8.04 | Scanpower, 2005
Scanpower | 2006 | 32.31 | 36.28 | 68.59 | 0.29 | 0.69 | 0.98 | 67 | 52 | 119 | 5.8% | 6.94 | Scanpower, 2006
Scanpower | 2007 | 26.14 | 20.53 | 46.67 | 0.2 | 0.64 | 0.84 | 43 | 32 | 75 | 9.4% | 4.24 | Scanpower, 2007
The Lines Company | 2003 | 226.2 | 450.4 | 729 | 1.12 | 5.71 | 7.15 | 659 | 587 | 1251 | 29.18% | 14.2 | The Lines Company, 2003
The Lines Company | 2004 | 78.2 | 264.4 | 400.2 | 0.46 | 3.48 | 4.96 | 334 | 497 | 862 | 28% | 12 | The Lines Company, 2004
The Lines Company | 2005 | 79.5 | 146.1 | 305.6 | 0.43 | 2.52 | 4.02 | 279 | 397 | 729 | 17% | 9.8 | The Lines Company, 2005
The Lines Company | 2006 | 97.5 | 180 | 284.9 | 0.6 | 3.16 | 3.84 | 257 | 395 | 690 | 52% | 10.5 | The Lines Company, 2006
The Lines Company | 2007 | 110.3 | 233 | 368.5 | 0.57 | 2.71 | 3.63 | 330 | 682 | 1190 | 61% | 18.1 | The Lines Company, 2007
The Power Company | 2003 | 18.9 | 147.8 | 167 | 0.11 | 3.22 | 3.33 | 149 | 388 | 540 | 2.3% | 6 | The Power Company, 2003
The Power Company | 2004 | 11.1 | 140.8 | 157.3 | 0.1 | 3.42 | 4.13 | 85 | 391 | 479 | 2.61% | 5.56 | The Power Company, 2004
The Power Company | 2005 | 7.7 | 117.8 | 125.5 | 0.04 | 2.96 | 3 | 63 | 354 | 417 | 2.82% | 4.69 | The Power Company, 2005
The Power Company | 2006 | 14.8 | 143.5 | 161.2 | 0.08 | 2.91 | 3.07 | 152 | 416 | 570 | 15.63% | 5.19 | The Power Company, 2006
The Power Company | 2007 | 42.4 | 135.1 | 182.9 | 0.23 | 2.8 | 3.28 | 356 | 475 | 833 | 20.42% | 6.06 | The Power Company, 2007
Top Energy | 2003 | 37 | 382.9 | 419.9 | 0.3 | 6.1 | 6.4 | 144 | 249 | 393 | 30% | 7.25 | Top Energy, 2003
Top Energy | 2004 | 39.5 | 311.9 | 352.9 | 0.3 | 4.2 | 4.6 | 169 | 219 | 389 | 42% | 7.06 | Top Energy, 2004
Top Energy | 2005 | 39.4 | 343.1 | 496.2 | 0.3 | 4.3 | 6.2 | 147 | 220 | 369 | 46% | 8.07 | Top Energy, 2005
Top Energy | 2006 | 22.3 | 499.8 | 556.1 | 0.1 | 5.4 | 5.6 | 159 | 368 | 528 | 46% | 12.1 | Top Energy, 2006
Top Energy | 2007 | 18.2 | 398.9 | 487.8 | 0.1 | 5.4 | 5.7 | 168 | 330 | 500 | 30% | 10.8 | Top Energy, 2007
Unison Networks | 2003 | 24.52 | 72.08 | 96.61 | 0.14 | 1.28 | 1.45 | 324 | 259 | 583 | 3.68% | 8.96 | Unison Networks, 2003
Unison Networks | 2004 | 30 | 171 | 202 | 0.21 | 2.17 | 2.38 | 490 | 522 | 1012 | 43% | 10.67 | Unison Networks, 2004
Unison Networks | 2005 | 25 | 130 | 156 | 0.16 | 3.05 | 3.21 | 463 | 520 | 983 | 26% | 9.36 | Unison Networks, 2005
Unison Networks | 2006 | 28 | 106 | 134 | 0.18 | 2.65 | 2.83 | 432 | 437 | 869 | 25.23% | 8.92 | Unison Networks, 2006
Unison Networks | 2007 | 33 | 105 | 140 | 0.23 | 1.92 | 2.15 | 543 | 445 | 988 | 31.01% | 9.08 | Unison Networks, 2007
Vector Lines | 2003 | 7.19 | 72.21 | 79.72 | 0.04 | 1.28 | 1.32 | 329 | 896 | 1232 | 16.4% | 12.57 | Vector Lines, 2003
Vector Lines | 2004 | 9.16 | 94.29 | 107.94 | 0.05 | 1.38 | 1.54 | 610 | 1333 | 1951 | 29.9% | 14.52 | Vector Lines, 2004
Vector Lines | 2005 | 3.7 | 78.21 | 83.09 | 0.02 | 1.12 | 1.25 | 416 | 1131 | 1554 | 26.4% | 12.63 | Vector Lines, 2005
Vector Lines | 2006 | 4.7 | 112.57 | 119.81 | 0.03 | 1.47 | 1.67 | 532 | 1400 | 1940 | 29.7% | 15.22 | Vector Lines, 2006
Vector Lines | 2007 | 5.27 | 109.35 | 244.38 | 0.03 | 1.38 | 2.05 | 489 | 1481 | 1994 | 29.7% | 16.19 | Vector Lines, 2007
Waipa Network | 2003 | 73.74 | 162.4 | 247.32 | 0.32 | 3.23 | 4.21 | 122 | 111 | 237 | 23% | 8.37 | Waipa Network, 2003
Waipa Network | 2004 | 19.02 | 244.74 | 491.04 | 0.08 | 4.31 | 5.58 | 50 | 133 | 187 | 29% | 10.18 | Waipa Network, 2004
Waipa Network | 2005 | 9.48 | 152.68 | 278.74 | 0.05 | 3.04 | 4.29 | 38 | 131 | 174 | 26% | 9.81 | Waipa Network, 2005
Waipa Network | 2006 | 16.97 | 154.48 | 176.23 | 0.08 | 2.68 | 3.94 | 51 | 109 | 164 | 31% | 8.42 | Waipa Network, 2006
Waipa Network | 2007 | 36.84 | 132.38 | 541.43 | 0.18 | 2.06 | 4.45 | 61 | 127 | 194 | 24% | 9.74 | Waipa Network, 2007
WEL Networks | 2003 | 1.67 | 92.11 | 93.93 | 0.03 | 1.78 | 1.84 | 30 | 287 | 324 | 17.6% | 9.9 | WEL Networks, 2003
WEL Networks | 2004 | 1.51 | 64.53 | 68.48 | 0.03 | 1.59 | 1.83 | 22 | 224 | 250 | 19.6% | 7.87 | WEL Networks, 2004
WEL Networks | 2005 | 1.12 | 86.53 | 132.43 | 0.01 | 1.64 | 2.42 | 14 | 233 | 251 | 25.3% | 8.25 | WEL Networks, 2005
WEL Networks | 2006 | 2.12 | 67.51 | 69.63 | 0.01 | 1.52 | 1.53 | 18 | 256 | 274 | 22.3% | 9.13 | WEL Networks, 2006
WEL Networks | 2007 | 2.87 | 95.55 | 103.43 | 0.02 | 1.83 | 1.86 | 30 | 283 | 314 | 36.4% | 9.81 | WEL Networks, 2007
Westpower | 2003 | 66.76 | 55.26 | 122.02 | 0.27 | 0.89 | 1.16 | 63 | 57 | 120 | 14% | 6 | Westpower, 2003
Westpower | 2004 | 42.11 | 145.64 | 205.49 | 0.19 | 2.02 | 2.4 | 50 | 171 | 226 | 19.9% | 11 | Westpower, 2004
Westpower | 2005 | 71.31 | 188.54 | 372.06 | 0.34 | 2.89 | 4.23 | 140 | 136 | 284 | 29.4% | 12.9 | Westpower, 2005
Westpower | 2006 | 76.39 | 69.49 | 151.12 | 0.28 | 1.1 | 2.04 | 63 | 122 | 187 | 13.9% | 4.8 | Westpower, 2006
Westpower | 2007 | 55.65 | 110.49 | 309.87 | 0.33 | 2.64 | 7.88 | 121 | 135 | 265 | 39.3% | 12.3 | Westpower, 2007
Note on I116: Updated 20/5 - incorrectly entered in Class A in source data
Note on J116: Updated 20/5 - incorrectly entered in Class B in source data

## 2005-2014 ZD
DPP s.53 ZD Information request 2005—2014
As acquired through a s.53ZD requested in 2014
Business-specific data
|  | SAIDI - Class B and C | SAIDI - Normalised | SAIFI - Class B and C | SAIFI - Normalised | Number of Interruptions - B&C
Alpine Energy | 2011 |  | 225.89 |  | 1.708 |  | Alpine Energy, 2011
Alpine Energy | 2012 |  | 161.6007 |  | 1.2611 |  | Alpine Energy, 2012
Alpine Energy | 2013 |  | 148.2651 |  | 1.2979 |  | Alpine Energy, 2013
Alpine Energy | 2014 |  | 274.7657 |  | 1.999 |  | Alpine Energy, 2014
Electricity Ashburton | 2011 |  | 189.1629 |  | 1.8137 |  | Electricity Ashburton, 2011
Electricity Ashburton | 2012 |  | 183.0637 |  | 1.5122 |  | Electricity Ashburton, 2012
Electricity Ashburton | 2013 |  | 150.3124 |  | 1.4771 |  | Electricity Ashburton, 2013
Electricity Ashburton | 2014 |  | 239.5109 |  | 2.4979 |  | Electricity Ashburton, 2014
Aurora Energy | 2011 |  | 110.9469 |  | 1.4783 |  | Aurora Energy, 2011
Aurora Energy | 2012 |  | 102.5043 |  | 1.7037 |  | Aurora Energy, 2012
Aurora Energy | 2013 |  | 53.8041 |  | 0.92894 |  | Aurora Energy, 2013
Aurora Energy | 2014 |  | 94.4829 |  | 1.2105 |  | Aurora Energy, 2014
Centralines | 2011 |  | 192.6684 |  | 4.7415 |  | Centralines, 2011
Centralines | 2012 |  | 156.797 |  | 3.6727 |  | Centralines, 2012
Centralines | 2013 |  | 123.854 |  | 2.6965 |  | Centralines, 2013
Centralines | 2014 |  | 163.0072 |  | 3.3154 |  | Centralines, 2014
Eastland Network | 2011 |  | 333.9967 |  | 3.4827 |  | Eastland Network, 2011
Eastland Network | 2012 |  | 392.1459 |  | 3.4124 |  | Eastland Network, 2012
Eastland Network | 2013 |  | 287.1738 |  | 3.8352 |  | Eastland Network, 2013
Eastland Network | 2014 |  | 279.7998 |  | 2.67 |  | Eastland Network, 2014
Horizon Energy | 2011 |  | 177.4069 |  | 2.3927 |  | Horizon Energy, 2011
Horizon Energy | 2012 |  | 174.6412 |  | 2.2389 |  | Horizon Energy, 2012
Horizon Energy | 2013 |  | 191.6029 |  | 2.2956 |  | Horizon Energy, 2013
Horizon Energy | 2014 |  | 186.3412 |  | 1.7721 |  | Horizon Energy, 2014
Electricity Invercargill | 2011 |  | 44.7686 |  | 1.1821 |  | Electricity Invercargill, 2011
Electricity Invercargill | 2012 |  | 63.6322 |  | 1.295 |  | Electricity Invercargill, 2012
Electricity Invercargill | 2013 |  | 31.7908 |  | 0.33463 |  | Electricity Invercargill, 2013
Electricity Invercargill | 2014 |  | 25.1027 |  | 0.52124 |  | Electricity Invercargill, 2014
Nelson Electricity | 2011 |  | 56.5143 |  | 0.57912 |  | Nelson Electricity, 2011
Nelson Electricity | 2012 |  | 55.6856 |  | 0.64769 |  | Nelson Electricity, 2012
Nelson Electricity | 2013 |  | 43.6371 |  | 0.56205 |  | Nelson Electricity, 2013
Nelson Electricity | 2014 |  | 22.3763 |  | 0.49858 |  | Nelson Electricity, 2014
OtagoNet | 2011 |  | 247.08 |  | 2.26 |  | OtagoNet, 2011
OtagoNet | 2012 |  | 276.6353 |  | 2.3091 |  | OtagoNet, 2012
OtagoNet | 2013 |  | 253 |  | 2.3 |  | OtagoNet, 2013
OtagoNet | 2014 |  | 348.1493 |  | 2.9514 |  | OtagoNet, 2014
Powerco | 2011 |  | 241.7699 |  | 2.6224 |  | Powerco, 2011
Powerco | 2012 |  | 209.8509 |  | 2.5746 |  | Powerco, 2012
Powerco | 2013 |  | 175.7846 |  | 1.864 |  | Powerco, 2013
Powerco | 2014 |  | 206.9535 |  | 2.2892 |  | Powerco, 2014
Network Tasman | 2011 |  | 178.0397 |  | 1.6366 |  | Network Tasman, 2011
Network Tasman | 2012 |  | 159.3889 |  | 1.3802 |  | Network Tasman, 2012
Network Tasman | 2013 |  | 130.2789 |  | 1.4889 |  | Network Tasman, 2013
Network Tasman | 2014 |  | 129.3755 |  | 1.3334 |  | Network Tasman, 2014
The Lines Company | 2011 |  | 264.5704 |  | 3.6632 |  | The Lines Company, 2011
The Lines Company | 2012 |  | 311.8821 |  | 3.987 |  | The Lines Company, 2012
The Lines Company | 2013 |  | 199.5652 |  | 2.3174 |  | The Lines Company, 2013
The Lines Company | 2014 |  | 268.7521 |  | 3.7201 |  | The Lines Company, 2014
Top Energy | 2011 |  | 440.012 |  | 4.926 |  | Top Energy, 2011
Top Energy | 2012 |  | 436.48 |  | 6.385 |  | Top Energy, 2012
Top Energy | 2013 |  | 327.1732 |  | 4.671 |  | Top Energy, 2013
Top Energy | 2014 |  | 464.9145 |  | 5.458 |  | Top Energy, 2014
Unison Networks | 2011 |  | 127.4762 |  | 1.8284 |  | Unison Networks, 2011
Unison Networks | 2012 |  | 160.6207 |  | 2.6162 |  | Unison Networks, 2012
Unison Networks | 2013 |  | 89.2375 |  | 1.637 |  | Unison Networks, 2013
Unison Networks | 2014 |  | 112.8192 |  | 1.7665 |  | Unison Networks, 2014
Vector Lines | 2005 | 96.3 | 96.3 | 1.39 | 1.39 | 1334 | Vector Lines, 2005
Vector Lines | 2006 | 145.7 | 125.5 | 1.84 | 1.84 | 1713 | Vector Lines, 2006
Vector Lines | 2007 | 141 | 128.1 | 1.66 | 1.66 | 1713 | Vector Lines, 2007
Vector Lines | 2008 | 252.1 | 102.6 | 1.8 | 1.64 | 1679 | Vector Lines, 2008
Vector Lines | 2009 | 153.4 | 105.5 | 1.68 | 1.65 | 1682 | Vector Lines, 2009
Vector Lines | 2010 | 66.7792 | 66.7792 | 1.0182 | 1.0182 | 1444 | Vector Lines, 2010
Vector Lines | 2011 | 123.1543 | 113.7629 | 1.2399 | 1.2399 | 2058 | Vector Lines, 2011
Vector Lines | 2012 | 95.6887 | 95.6887 | 1.1189 | 1.1189 | 2177 | Vector Lines, 2012
Vector Lines | 2013 | 95.8454 | 95.8454 | 1.0104 | 1.0104 | 2051 | Vector Lines, 2013
Vector Lines | 2014 | 150.9017 | 141.304 | 1.451 | 1.451 | 2672 | Vector Lines, 2014
Wellington Electricity | 2005 | 39.9527 | 36.1092 | 0.38573 | 0.38573 | 213 | Wellington Electricity, 2005
Wellington Electricity | 2006 | 31.4153 | 31.4153 | 0.50511 | 0.50511 | 221 | Wellington Electricity, 2006
Wellington Electricity | 2007 | 34.9815 | 34.9815 | 0.64631 | 0.64631 | 257 | Wellington Electricity, 2007
Wellington Electricity | 2008 | 31.6536 | 31.6536 | 0.51436 | 0.51436 | 233 | Wellington Electricity, 2008
Wellington Electricity | 2009 | 35.3278 | 35.3278 | 0.53051 | 0.53051 | 258 | Wellington Electricity, 2009
Wellington Electricity | 2010 | 40.4778 | 40.4778 | 0.57275 | 0.57275 | 327 | Wellington Electricity, 2010
Wellington Electricity | 2011 | 34.7384 | 34.7384 | 0.537 | 0.537 | 259 | Wellington Electricity, 2011
Wellington Electricity | 2012 | 45.8791 | 45.8791 | 0.71522 | 0.71522 | 338 | Wellington Electricity, 2012
Wellington Electricity | 2013 | 43.2901 | 43.2901 | 0.57329 | 0.57329 | 316 | Wellington Electricity, 2013
Wellington Electricity | 2014 | 190.7702 | 78.8765 | 1.1067 | 1.1067 | 499 | Wellington Electricity, 2014

## 2008-2012 ID
Information Disclosure database 2008—2012
Information disclosure database—as submitted under the Electricity Distribution (Information Disclosure) Requirements 2008
Business-specific data
Description, Year | Alpine Energy | Aurora Energy | Buller Electricity | Centralines | Counties Power | Eastland Network | Electra | Electricity Ashburton | Electricity Invercargill | Horizon Energy | MainPower NZ | Marlborough Lines | Nelson Electricity | Network Tasman | Network Waitaki | Northpower | Orion NZ | OtagoNet | Powerco | Scanpower | The Lines Company | The Power Company | Top Energy | Unison Networks | Vector Lines | WEL Networks | Waipa Network | Wellington Electricity | Westpower | Description | Year
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
Class C interruptions restored outside of 3 hours, 2008 | 11 | 76 | 11 | 6 | 50 | 80 | 29 | 23 | 4 | 12 | 14 | 112 | 1 | 22 | 11 | 134 | 141 | 84 | 534 | 4 | 184 | 144 | 156 | 112 | 563 | 71 | 32 | 0 | 38 | Class C interruptions restored outside of 3 hours | 2008
Class C interruptions restored outside of 3 hours, 2009 | 35 | 55 | 13 | 24 | 65 | 92 | 27 | 46 | 8 | 12 | 28 | 100 | 2 | 24 | 18 | 86 | 191 | 45 | 546 | 2 | 374 | 110 | 205 | 120 | 548 | 48 | 34 | 36 | 76 | Class C interruptions restored outside of 3 hours | 2009
Class C interruptions restored outside of 3 hours, 2010 | 51 | 66 | 21 | 20 | 27 | 138 | 23 | 34 | 6 | 13 | 26 | 94 | 1 | 31 | 17 | 64 | 123 | 54 | 270 | 3 | 220 | 78 | 164 | 123 | 276 | 81 | 28 | 62 | 60 | Class C interruptions restored outside of 3 hours | 2010
Class C interruptions restored outside of 3 hours, 2011 | 34 | 103 | 20 | 23 | 53 | 133 | 18 | 61 | 8 | 24 | 41 | 87 | 1 | 34 | 21 | 51 | 0 | 58 | 647 | 4 | 214 | 122 | 164 | 163 | 498 | 89 | 24 | 46 | 45 | Class C interruptions restored outside of 3 hours | 2011
Class C interruptions restored outside of 3 hours, 2012 | 56 | 133 | 19 | 25 | 44 | 133 | 33 | 47 | 7 | 17 | 20 | 97 | 0 | 49 | 20 | 65 | 346 | 87 | 757 | 32 | 340 | 137 | 179 | 182 | 467 | 131 | 39 | 72 | 35 | Class C interruptions restored outside of 3 hours | 2012
Class C interruptions restored within 3 hours, 2008 | 63 | 317 | 36 | 160 | 120 | 137 | 165 | 128 | 21 | 64 | 73 | 266 | 7 | 108 | 51 | 353 | 308 | 168 | 1328 | 39 | 597 | 430 | 179 | 258 | 900 | 237 | 69 | 0 | 41 | Class C interruptions restored within 3 hours | 2008
Class C interruptions restored within 3 hours, 2009 | 54 | 333 | 31 | 118 | 147 | 145 | 153 | 196 | 15 | 82 | 104 | 233 | 8 | 119 | 75 | 241 | 327 | 120 | 1436 | 35 | 882 | 389 | 238 | 234 | 741 | 237 | 102 | 99 | 79 | Class C interruptions restored within 3 hours | 2009
Class C interruptions restored within 3 hours, 2010 | 93 | 361 | 43 | 111 | 102 | 155 | 102 | 181 | 18 | 86 | 141 | 282 | 8 | 107 | 69 | 191 | 280 | 138 | 1578 | 48 | 679 | 323 | 124 | 188 | 585 | 125 | 69 | 161 | 50 | Class C interruptions restored within 3 hours | 2010
Class C interruptions restored within 3 hours, 2011 | 147 | 387 | 31 | 131 | 154 | 195 | 74 | 198 | 23 | 94 | 184 | 231 | 1 | 128 | 67 | 211 | 0 | 145 | 1550 | 45 | 649 | 483 | 144 | 220 | 707 | 140 | 55 | 158 | 70 | Class C interruptions restored within 3 hours | 2011
Class C interruptions restored within 3 hours, 2012 | 94 | 351 | 37 | 99 | 103 | 161 | 110 | 214 | 22 | 100 | 122 | 190 | 4 | 97 | 54 | 254 | 697 | 125 | 1578 | 113 | 833 | 454 | 215 | 252 | 688 | 302 | 78 | 181 | 83 | Class C interruptions restored within 3 hours | 2012
Faults per 100 circuit kilometers, 2008 | 1.8426 | 11.69 | 13.8333 | 14.12 | 5.714 | 7.53 | 7.58 | 5.27 | 13.33 | 4.0672 | 2.4 | 13.79 | 7.77 | 5.7737 | 3.5717 | 13.73 | 7.3 | 6.58 | 16.3609 | 4.87 | 18.62 | 7.39 | 8.1791 | 7.65 | 16.1346 | 10.6667 | 7.6955 | 0 | 3.79 | Faults per 100 circuit kilometers | 2008
Faults per 100 circuit kilometers, 2009 | 2.1675 | 9.24 | 9.3971 | 9.37 | 7.0455 | 8.22 | 6.87 | 5.3 | 12.195 | 5.0614 | 3.61 | 12.91 | 9.96 | 6.3302 | 4.7 | 8.96 | 8.7 | 4.19 | 7.72 | 4.1406 | 46.51 | 6.375 | 11.5448 | 6.95 | 17.02 | 9.69 | 10.2613 | 7.1 | 7.46 | Faults per 100 circuit kilometers | 2009
Faults per 100 circuit kilometers, 2010 | 3.4096 | 9.11 | 13.3 | 8.6387 | 4.268 | 10.17 | 4.85 | 6.034 | 9.87 | 5.47 | 4.47 | 14.55 | 9.94 | 6.0881 | 4.9 | 7.06 | 6.68 | 4.74 | 6.2826 | 5.89 | 21.06 | 5.15 | 7.4911 | 6.18 | 11.4346 | 7.28 | 7.2954 | 12.55 | 5.31 | Faults per 100 circuit kilometers | 2010
Faults per 100 circuit kilometers, 2011 | 4.2718 | 10.6 | 10.5 | 10.14 | 6.8253 | 11.41 | 3.565 | 7.1952 | 14.32 | 6.5073 | 5.9 | 12.25 | 2.27 | 7.15 | 4.68 | 6.7327 | 0 | 4.94 | 9.619 | 4.59 | 21.6 | 7.21 | 8 | 7.56 | 15.7 | 7.96 | 5.9143 | 11.9035 | 5.35 | Faults per 100 circuit kilometers | 2011
Faults per 100 circuit kilometers, 2012 | 3.4923 | 11.2 | 11.2 | 8.2 | 4.8119 | 10.24 | 5.6335 | 7.8227 | 12.84 | 6.428 | 3.68 | 11.01 | 4.54 | 6.4 | 4.16 | 8.23 | 15.81 | 5.21 | 19.285 | 13.94 | 26.756 | 7.07 | 10.21 | 8.2954 | 14.9631 | 14.63 | 8.7493 | 13.2995 | 5.38 | Faults per 100 circuit kilometers | 2012
Number of interruptions - Class B, 2008 | 260 | 224 | 33 | 46 | 98 | 110 | 114 | 297 | 0 | 62 | 316 | 271 | 5 | 207 | 141 | 176 | 318 | 397 | 1037 | 44 | 284 | 401 | 264 | 596 | 448 | 43 | 45 | 0 | 86 | Number of interruptions - Class B | 2008
Number of interruptions - Class B, 2009 | 229 | 223 | 32 | 82 | 167 | 197 | 123 | 312 | 1 | 33 | 335 | 289 | 36 | 152 | 132 | 268 | 436 | 414 | 1192 | 66 | 559 | 383 | 293 | 547 | 393 | 55 | 94 | 49 | 89 | Number of interruptions - Class B | 2009
Number of interruptions - Class B, 2010 | 258 | 249 | 60 | 116 | 132 | 204 | 40 | 309 | 8 | 51 | 363 | 274 | 28 | 208 | 144 | 310 | 408 | 404 | 1186 | 86 | 331 | 469 | 159 | 448 | 583 | 76 | 77 | 106 | 104 | Number of interruptions - Class B | 2010
Number of interruptions - Class B, 2011 | 239 | 368 | 55 | 152 | 125 | 169 | 45 | 259 | 8 | 61 | 376 | 247 | 28 | 214 | 93 | 326 | 0 | 468 | 1311 | 99 | 300 | 880 | 131 | 399 | 853 | 104 | 84 | 56 | 112 | Number of interruptions - Class B | 2011
Number of interruptions - Class B, 2012 | 239 | 272 | 37 | 113 | 140 | 210 | 32 | 199 | 18 | 56 | 403 | 243 | 17 | 136 | 126 | 362 | 269 | 469 | 729 | 103 | 341 | 755 | 167 | 358 | 1086 | 283 | 91 | 85 | 124 | Number of interruptions - Class B | 2012
Number of interruptions - Class C, 2008 | 74 | 393 | 47 | 166 | 170 | 217 | 194 | 151 | 25 | 76 | 87 | 378 | 8 | 130 | 62 | 487 | 449 | 252 | 1862 | 43 | 812 | 574 | 335 | 370 | 1463 | 308 | 101 | 0 | 79 | Number of interruptions - Class C | 2008
Number of interruptions - Class C, 2009 | 89 | 388 | 44 | 142 | 212 | 237 | 180 | 242 | 23 | 94 | 132 | 333 | 10 | 143 | 93 | 327 | 518 | 165 | 1982 | 37 | 1256 | 499 | 443 | 354 | 1289 | 285 | 136 | 135 | 155 | Number of interruptions - Class C | 2009
Number of interruptions - Class C, 2010 | 144 | 427 | 64 | 131 | 129 | 293 | 125 | 215 | 24 | 99 | 167 | 376 | 9 | 138 | 86 | 255 | 403 | 192 | 1848 | 50 | 899 | 401 | 288 | 311 | 861 | 206 | 97 | 225 | 110 | Number of interruptions - Class C | 2010
Number of interruptions - Class C, 2011 | 181 | 490 | 51 | 154 | 207 | 328 | 92 | 259 | 31 | 118 | 225 | 318 | 2 | 162 | 88 | 262 | 0 | 203 | 2197 | 49 | 863 | 605 | 308 | 383 | 1205 | 229 | 79 | 204 | 115 | Number of interruptions - Class C | 2011
Number of interruptions - Class C, 2012 | 150 | 484 | 56 | 124 | 147 | 294 | 143 | 261 | 29 | 117 | 142 | 287 | 4 | 146 | 74 | 319 | 1043 | 212 | 2335 | 145 | 1173 | 591 | 394 | 434 | 1155 | 433 | 117 | 253 | 118 | Number of interruptions - Class C | 2012
Number of interruptions - Total, 2008 | 337 | 619 | 83 | 212 | 270 | 331 | 330 | 450 | 25 | 153 | 404 | 649 | 13 | 341 | 203 | 663 | 797 | 649 | 2920 | 87 | 1103.98 | 980 | 600 | 971 | 1918 | 351 | 152 | 0 | 173 | Number of interruptions - Total | 2008
Number of interruptions - Total, 2009 | 327 | 614 | 77 | 224 | 381 | 435 | 303 | 555 | 25 | 137 | 467 | 622 | 47 | 301 | 225 | 596 | 963 | 580 | 3199 | 103 | 1827 | 892 | 740 | 920 | 1689 | 344 | 235 | 186 | 247 | Number of interruptions - Total | 2009
Number of interruptions - Total, 2010 | 403 | 678 | 124 | 248 | 272 | 503 | 165 | 524 | 32 | 157 | 533 | 650 | 38 | 352 | 230 | 568 | 816 | 599 | 3066 | 137 | 1365 | 874 | 449 | 785 | 1455 | 282 | 180 | 334 | 220 | Number of interruptions - Total | 2010
Number of interruptions - Total, 2011 | 422 | 858 | 106 | 316 | 332 | 500 | 137 | 518 | 39 | 205 | 601 | 565 | 30 | 382 | 181 | 588 | 0 | 671 | 3592 | 148 | 1328 | 1485 | 439 | 815 | 2061 | 333 | 173 | 261 | 232 | Number of interruptions - Total | 2011
Number of interruptions - Total, 2012 | 396 | 769 | 94 | 248 | 287 | 515 | 182 | 460 | 47 | 212 | 546 | 530 | 21 | 285 | 200 | 682 | 1321 | 682 | 3102 | 248 | 1524 | 1346 | 561 | 829 | 2253 | 716 | 216 | 340 | 247 | Number of interruptions - Total | 2012
SAIDI - Class B, 2008 | 62.32 | 13.29 | 99 | 50.17 | 19.2487 | 31.54 | 27.76 | 107.71 | 0 | 26.5165 | 61.11 | 100.8 | 4.667 | 45.85 | 24.14 | 22.1 | 10.19 | 187.24 | 36.0329 | 14.13 | 80.71 | 40.96 | 36.633 | 39.1582 | 3.8611 | 2.71 | 9.99 | 0 | 44.46 | SAIDI - Class B | 2008
SAIDI - Class B, 2009 | 82.8103 | 8.82 | 98.64 | 66.24 | 26.9855 | 53.25 | 21.04 | 89 | 0.006 | 11.0275 | 65.87 | 96.32 | 28.63 | 30.41 | 10.76 | 27.6 | 21.19 | 163.55 | 46.87 | 16.36 | 57.71 | 45.196 | 73.8958 | 50.8782 | 4.94 | 2.4443 | 39.84 | 0.57 | 43.45 | SAIDI - Class B | 2009
SAIDI - Class B, 2010 | 64.7 | 11.17 | 147.8 | 68.64 | 12.5993 | 73.61 | 4.47 | 105.5936 | 2.759 | 16.8833 | 75.18 | 103.56 | 54.38 | 61.88 | 14.68 | 27.03 | 20.72 | 168.903 | 41.7925 | 29.39 | 89.1 | 77.373 | 23.0886 | 38.04 | 9.627 | 9.8352 | 43.28 | 2.94 | 54.18 | SAIDI - Class B | 2010
SAIDI - Class B, 2011 | 62.25 | 16.92 | 150.9 | 84.81 | 17.9464 | 76.6 | 16.89 | 80.4406 | 6.59 | 14.7409 | 65 | 84 | 8.95 | 48.17 | 11.35 | 30.73 | 0 | 114.59 | 56.29 | 38.84 | 63.59 | 71.27 | 20.972 | 25.7 | 20.39 | 16.7299 | 28.35 | 0.76 | 46.92 | SAIDI - Class B | 2011
SAIDI - Class B, 2012 | 54.3 | 13.46 | 78.2 | 33.86 | 20.0139 | 116.29 | 10.19 | 73.3555 | 10.235 | 12.27 | 70.82 | 72.5 | 9.17 | 51.72 | 13.52 | 46.51 | 9.9 | 99.865 | 30.3594 | 43.2 | 71.7 | 58.014 | 15.331 | 28.4502 | 18.4257 | 8.78 | 46.32 | 1.3723 | 44.26 | SAIDI - Class B | 2012
SAIDI - Class C, 2008 | 87.18 | 115.82 | 152 | 106.92 | 148.5323 | 213.43 | 76.21 | 91.56 | 54.66 | 116.561 | 49 | 164.5 | 12.268 | 111.69 | 70.54 | 760.98 | 34.66 | 315.27 | 292.6237 | 44.18 | 186.4 | 253.82 | 781.669 | 78.6406 | 195.5686 | 77.42 | 102.68 | 0 | 106.06 | SAIDI - Class C | 2008
SAIDI - Class C, 2009 | 118.1322 | 59.15 | 150.67 | 132.52 | 144.6926 | 189.84 | 662.08 | 248.32 | 32.866 | 122.2355 | 80.29 | 153.56 | 87.18 | 214.62 | 58.6 | 226.74 | 40.42 | 106.65 | 243.82 | 19.21 | 227.43 | 165.031 | 841.2604 | 78.3664 | 148.5 | 81.7178 | 194.61 | 25.78 | 339.02 | SAIDI - Class C | 2009
SAIDI - Class C, 2010 | 267.67 | 61.3 | 154.5 | 64.36 | 65.695 | 238.66 | 158.82 | 80.4712 | 27.232 | 123.0164 | 64.93 | 180.23 | 24.916 | 86.42 | 49.61 | 105.27 | 40.44 | 163.735 | 184.2927 | 36.49 | 204.16 | 132.137 | 439.9433 | 72.84 | 57.1522 | 65.1449 | 83.54 | 37.69 | 225.12 | SAIDI - Class C | 2010
SAIDI - Class C, 2011 | 163.28 | 94.62 | 137.7 | 106.64 | 120.2289 | 257.39 | 57.823 | 182.2387 | 38.18 | 162.666 | 272.1 | 338.92 | 105.71 | 129.87 | 49.96 | 104.08 | 0 | 132.49 | 217.64 | 64.81 | 228.84 | 137.79 | 419.045 | 102.28 | 102.76 | 65.8224 | 85.92 | 33.9784 | 250.36 | SAIDI - Class C | 2011
SAIDI - Class C, 2012 | 107.3 | 130.01 | 174.9 | 233.47 | 68.0021 | 278.99 | 121.71 | 119.3409 | 53.397 | 162.35 | 45.64 | 167.2 | 54.29 | 106.78 | 37.33 | 99.51 | 220.6 | 220.904 | 300.9311 | 55.59 | 252.83 | 180.08 | 419.65 | 220.791 | 77.3599 | 60.24 | 195.58 | 44.5068 | 92.09 | SAIDI - Class C | 2012
SAIDI - Total, 2008 | 149.5 | 140.1 | 428 | 157.09 | 167.781 | 258.13 | 193.9 | 199.27 | 54.66 | 345.5193 | 110.67 | 265.3 | 16.935 | 172 | 94.67 | 783.08 | 53.76 | 502.51 | 358.7574 | 58.31 | 267.31 | 294.78 | 818.3 | 117.8 | 220.2022 | 80.13 | 497.29 | 0 | 150.52 | SAIDI - Total | 2008
SAIDI - Total, 2009 | 200.9425 | 68.01 | 273.26 | 198.76 | 171.6781 | 248.82 | 683.1 | 337.32 | 51.43 | 201.9758 | 146.16 | 249.88 | 185.4 | 342.31 | 69.36 | 254.34 | 62.85 | 274.25 | 320.09 | 35.57 | 297.13 | 217.343 | 915.1562 | 129.2446 | 172.34 | 88.7441 | 236.99 | 26.3 | 382.47 | SAIDI - Total | 2009
SAIDI - Total, 2010 | 332.37 | 82.68 | 302.3 | 132.94 | 98.1017 | 322.73 | 163.28 | 186.0648 | 29.992 | 139.8998 | 143.08 | 283.79 | 169.419 | 226.39 | 64.29 | 132.29 | 61.16 | 341.2 | 253.2003 | 65.88 | 293.26 | 214.436 | 463.0319 | 110.88 | 119.7363 | 74.9801 | 284.02 | 40.629 | 279.31 | SAIDI - Total | 2010
SAIDI - Total, 2011 | 225.92 | 111.54 | 288.7 | 191.45 | 138.1753 | 340.8 | 74.713 | 262.6793 | 44.77 | 177.4069 | 337.8 | 422.91 | 114.66 | 236.57 | 61.33 | 134.81 | 0 | 247.08 | 306.42 | 103.65 | 292.43 | 209.06 | 440.017 | 127.98 | 123.95 | 82.5523 | 199.34 | 34.7384 | 330.82 | SAIDI - Total | 2011
SAIDI - Total, 2012 | 161.6 | 148.95 | 253 | 267.33 | 88.016 | 437.6 | 131.9 | 192.6964 | 63.632 | 174.62 | 124.05 | 239.7 | 63.47 | 173.7 | 50.85 | 146.02 | 230.56 | 320.769 | 400.5241 | 98.79 | 324.52 | 238.095 | 434.981 | 249.2412 | 97.14 | 69.01 | 274.3 | 45.8791 | 146.2 | SAIDI - Total | 2012
SAIFI - Class B, 2008 | 0.3 | 0.1 | 0.38 | 0.15 | 0.1082 | 0.23 | 0.16 | 0.31 | 0 | 0.14535 | 0.28 | 0.53 | 0.029 | 0.2 | 0.13 | 0.16 | 0.04 | 0.81 | 0.19618 | 0.13 | 0.71 | 0.27 | 0.34235 | 0.28689 | 0.025069 | 0.019953 | 0.047 | 0 | 0.23 | SAIFI - Class B | 2008
SAIFI - Class B, 2009 | 0.36251 | 0.054953 | 0.4 | 0.26 | 0.15029 | 0.38 | 0.08 | 0.38 | 0.0006 | 0.058846 | 0.27 | 0.34 | 0.21 | 0.13 | 0.07 | 0.185 | 0.08 | 0.72 | 0.21 | 0.12 | 0.81 | 0.2405 | 0.59954 | 0.24682 | 0.03 | 0.018751 | 0.196 | 0.005 | 0.1919 | SAIFI - Class B | 2009
SAIFI - Class B, 2010 | 0.35 | 0.09 | 0.49 | 0.28 | 0.11735 | 0.51 | 0.02 | 0.38627 | 0.0172 | 0.098942 | 0.52 | 0.41 | 0.182 | 0.28 | 0.07 | 0.18 | 0.08 | 0.7392 | 0.21174 | 0.17 | 0.54 | 0.3485 | 0.15457 | 0.2 | 0.046975 | 0.076165 | 0.1988 | 0.03 | 0.18 | SAIFI - Class B | 2010
SAIFI - Class B, 2011 | 0.27 | 0.11709 | 0.79 | 0.42 | 0.1077 | 0.33 | 0.103 | 0.31076 | 0.03 | 0.1188 | 0.272 | 0.53 | 0.04 | 0.27 | 0.05 | 0.232 | 0 | 0.48 | 0.27 | 0.17 | 0.48 | 0.42 | 0.095 | 0.18 | 0.1 | 0.12565 | 0.1237 | 0.005 | 0.17 | SAIFI - Class B | 2011
SAIFI - Class B, 2012 | 0.25339 | 0.09 | 0.51 | 0.22 | 0.13572 | 0.55 | 0.06 | 0.25903 | 0.0417 | 0.151 | 0.41 | 0.32 | 0.04 | 0.32 | 0.07 | 0.238 | 0.04 | 0.4643 | 0.13647 | 0.25 | 0.51 | 0.3046 | 0.084 | 0.2076 | 0.091027 | 0.1 | 0.1583 | 0.010541 | 0.19 | SAIFI - Class B | 2012
SAIFI - Class C, 2008 | 1.38 | 1.37 | 1.68 | 2.53 | 2.0886 | 3.68 | 1.45 | 1.13 | 1.15 | 1.4201 | 0.969 | 2.42 | 0.155 | 1.33 | 1.97 | 4.47 | 0.59 | 2.29 | 2.3 | 1.17 | 2.97 | 3.48 | 6.0533 | 1.7377 | 1.4673 | 1.3909 | 1.8314 | 0 | 1.18 | SAIFI - Class C | 2008
SAIFI - Class C, 2009 | 1.3295 | 1.1713 | 1.12 | 4.67 | 3.469 | 3.02 | 2.86 | 1.96 | 0.8446 | 2.1604 | 1.06 | 1.64 | 1.68 | 1.53 | 1 | 3.068 | 0.52 | 2.08 | 2.55 | 0.77 | 3.45 | 3.8258 | 10.2823 | 1.8231 | 1.65 | 1.6221 | 2.3331 | 0.383 | 2.9001 | SAIFI - Class C | 2009
SAIFI - Class C, 2010 | 1.83 | 1.25 | 1.75 | 2.06 | 1.9973 | 2.95 | 3.13 | 1.0843 | 0.8258 | 2.2641 | 1.31 | 2.42 | 0.575 | 1.48 | 1.39 | 2.19 | 0.49 | 2.5199 | 2.2671 | 0.57 | 2.09 | 2.5328 | 4.0381 | 1.39 | 0.97126 | 1.0848 | 1.7097 | 0.56 | 1.84 | SAIFI - Class C | 2010
SAIFI - Class C, 2011 | 1.43 | 1.3614 | 1.28 | 4.3 | 2.8441 | 3.15 | 1.514 | 1.8224 | 1.15 | 2.2739 | 2.628 | 2.31 | 0.54 | 1.37 | 0.76 | 2.092 | 0 | 1.77 | 2.35 | 1.46 | 2.99 | 2.79 | 4.831 | 1.64 | 1.14 | 1.1297 | 1.4382 | 0.531 | 2.45 | SAIFI - Class C | 2011
SAIFI - Class C, 2012 | 1.0077 | 1.67 | 1.3 | 3.5 | 2.2041 | 2.86 | 2.23 | 1.2532 | 1.2533 | 2.088 | 0.71 | 1.72 | 1.05 | 1.06 | 0.88 | 2.31 | 2.17 | 1.9049 | 2.4957 | 1 | 3.48 | 2.7355 | 6.287 | 2.4086 | 1.0282 | 0.95 | 2.3804 | 0.70468 | 1.68 | SAIFI - Class C | 2012
SAIFI - Total, 2008 | 1.69 | 1.82 | 6.2 | 2.68 | 2.1968 | 4 | 2.82 | 1.47 | 1.15 | 2.4534 | 1.2628 | 2.94 | 0.184 | 1.63 | 2.1 | 4.63 | 0.74 | 3.1 | 2.93 | 1.29 | 3.68 | 3.75 | 6.3957 | 2.02 | 1.6629 | 1.41 | 5.1615 | 0 | 1.41 | SAIFI - Total | 2008
SAIFI - Total, 2009 | 1.692 | 1.23 | 2.52 | 4.93 | 3.6193 | 3.42 | 2.94 | 2.34 | 1.258 | 3.12 | 1.33 | 1.98 | 2.9 | 2.33 | 1.07 | 3.253 | 0.72 | 3.02 | 2.75 | 0.89 | 4.769 | 4.3664 | 10.8818 | 2.07 | 1.89 | 1.6834 | 3.0843 | 0.388 | 3.09 | SAIFI - Total | 2009
SAIFI - Total, 2010 | 2.18 | 1.48 | 2.24 | 2.34 | 2.3148 | 3.88 | 3.15 | 1.4705 | 0.843 | 2.363 | 2.02 | 2.83 | 1.756 | 2.594 | 1.46 | 2.37 | 0.58 | 3.78 | 2.6226 | 0.74 | 2.63 | 3.164 | 4.1926 | 1.59 | 1.5608 | 1.1609 | 3.2542 | 0.583 | 2.02 | SAIFI - Total | 2010
SAIFI - Total, 2011 | 1.71 | 1.4774 | 2.07 | 4.72 | 2.9518 | 3.52 | 1.617 | 2.1332 | 1.18 | 2.3927 | 2.9 | 2.83 | 0.58 | 1.91 | 0.82 | 2.324 | 0 | 2.26 | 2.9496 | 1.63 | 3.47 | 3.21 | 4.926 | 1.83 | 1.24 | 1.2554 | 3.2633 | 0.536 | 3.73 | SAIFI - Total | 2011
SAIFI - Total, 2012 | 1.2611 | 2.07 | 1.81 | 3.71 | 2.3398 | 4.48 | 2.29 | 1.5122 | 1.295 | 2.239 | 1.278 | 2.04 | 1.1 | 1.45 | 0.95 | 2.549 | 2.22 | 2.3692 | 3.0448 | 1.25 | 3.99 | 3.0401 | 6.371 | 2.6162 | 1.16 | 1.05 | 3.5765 | 0.71522 | 2.75 | SAIFI - Total | 2012

## 2013-2015 ID
Information Disclosure database 2013—2015
Information disclosure database—as submitted under the Electricity Distribution Information Disclosure Determination 2012
Business-specific data
Description, Year | Alpine Energy | Aurora Energy | Buller Electricity | Centralines | Counties Power | Eastland Network | Electra | Electricity Ashburton | Electricity Invercargill | Horizon Energy | MainPower NZ | Marlborough Lines | Nelson Electricity | Network Tasman | Network Waitaki | Northpower | Orion NZ | OtagoNet | Powerco | Scanpower | The Lines Company | The Power Company | Top Energy | Unison Networks | Vector Lines | WEL Networks | Waipa Network | Wellington Electricity | Westpower |  | Description | Year
PQ Regulated | DPP | DPP | No | DPP | No | DPP | No | DPP | DPP | DPP | No | No | DPP | DPP | No | No | CPP | DPP | DPP | No | DPP | No | DPP | DPP | DPP | No | No | DPP | No
Class C interruptions restored outside of 3 hours, 2013 | 52 | 71 | 14 | 11 | 54 | 82 | 13 | 33 | 11 | 18 | 31 | 93 | 1 | 32 | 16 | 33 | 288 | 39 | 473 | 8 | 153 | 113 | 96 | 104 | 420 | 144 | 32 | 48 | 40 | 29 | Class C interruptions restored outside of 3 hours | 2013
Class C interruptions restored outside of 3 hours, 2014 | 130 | 270 | 12 | 17 | 40 | 127 | 18 | 105 | 9 | 18 | 52 | 181 | 1 | 26 | 28 | 65 | 470 | 76 | 706 | 12 | 249 | 99 | 194 | 127 | 599 | 168 | 34 | 163 | 126 | 29 | Class C interruptions restored outside of 3 hours | 2014
Class C interruptions restored outside of 3 hours, 2015 | 71 | 128 | 16 | 15 | 39 | 139 | 45 | 50 | 6 | 23 | 52 | 85 | 1 | 35 | 18 | 146 | 250 | 84 | 841 | 9 | 235 | 184 | 223 | 151 | 871 | 255 | 45 | 62 | 78 | 29 | Class C interruptions restored outside of 3 hours | 2015
Class C interruptions restored within 3 hours, 2013 | 96 | 286 | 31 | 85 | 79 | 132 | 71 | 207 | 4 | 110 | 132 | 210 | 7 | 104 | 57 | 182 | 563 | 117 | 1409 | 84 | 537 | 385 | 185 | 185 | 724 | 411 | 58 | 168 | 97 | 29 | Class C interruptions restored within 3 hours | 2013
Class C interruptions restored within 3 hours, 2014 | 118 | 440 | 26 | 81 | 108 | 136 | 84 | 239 | 12 | 74 | 248 | 328 | 5 | 100 | 68 | 263 | 643 | 147 | 1533 | 86 | 661 | 437 | 200 | 193 | 824 | 411 | 95 | 222 | 40 | 29 | Class C interruptions restored within 3 hours | 2014
Class C interruptions restored within 3 hours, 2015 | 100 | 360 | 32 | 69 | 132 | 223 | 77 | 239 | 19 | 97 | 223 | 226 | 8 | 109 | 107 | 323 | 633 | 142 | 1919 | 100 | 432 | 436 | 178 | 217 | 748 | 401 | 118 | 158 | 143 | 29 | Class C interruptions restored within 3 hours | 2015
Interruptions per 100 circuit km, 2013 | 7.9738 | 12.6835 | 13.7246 | 15.4949 | 10.2857 | 11.5215 | 5.5408 | 12.9556 | 3.1963 | 11.0847 | 10.5777 | 15.8782 | 8.1792 | 9.099 | 8.3178 | 10.0671 | 11.4243 | 15.4071 | 13.1686 | 15.2964 | 26.0828 | 14.1426 | 13.6901 | 9.3331 | 12.0456 | 17.9833 | 9.1503 | 7.0646 | 10.4766 | 29 | Interruptions per 100 circuit km | 2013
Interruptions per 100 circuit km, 2014 | 10.0844 | 12.2498 | 11.75 | 14.846 | 7.447 | 12.0805 | 9.2355 | 15.5474 | 5.1735 | 7.0548 | 19.1147 | 22.6624 | 7.8846 | 8.7482 | 8.7096 | 11.5491 | 14.2136 | 16.8102 | 14.7197 | 16.547 | 31.4777 | 13.8611 | 13.4502 | 9.9584 | 15.0159 | 18.9843 | 10.2401 | 10.9944 | 11.7237 | 29 | Interruptions per 100 circuit km | 2014
Interruptions per 100 circuit km, 2015 | 9.5694 | 13.8443 | 14.9789 | 11.4155 | 8.7361 | 13.7075 | 10.9043 | 15.1394 | 4.0815 | 8.4591 | 17.7761 | 15.7966 | 9.282 | 8.6253 | 15.1441 | 14.6758 | 13.5473 | 14.0236 | 16.4231 | 18.0095 | 33.1629 | 15.4169 | 14.4231 | 10.3158 | 15.3454 | 21.4814 | 12.047 | 8.7326 | 13.7198 | 29 | Interruptions per 100 circuit km | 2015
Number of interruptions - Class B, 2013 | 176 | 346 | 40 | 168 | 182 | 204 | 41 | 143 | 6 | 118 | 346 | 221 | 13 | 168 | 71 | 366 | 391 | 520 | 1461 | 68 | 343 | 730 | 256 | 456 | 998 | 380 | 91 | 111 | 94 | 29 | Number of interruptions - Class B | 2013
Number of interruptions - Class B, 2014 | 160 | 257 | 37 | 187 | 79 | 165 | 106 | 121 | 13 | 70 | 625 | 254 | 14 | 167 | 66 | 348 | 424 | 541 | 1238 | 75 | 359 | 685 | 137 | 558 | 1249 | 406 | 78 | 119 | 97 | 29 | Number of interruptions - Class B | 2014
Number of interruptions - Class B, 2015 | 222 | 317 | 48 | 138 | 102 | 175 | 123 | 167 | 2 | 84 | 596 | 223 | 18 | 162 | 165 | 396 | 606 | 422 | 1319 | 81 | 338 | 737 | 171 | 565 | 1161 | 482 | 82 | 183 | 89 | 29 | Number of interruptions - Class B | 2015
Number of interruptions - Class C, 2013 | 148 | 357 | 45 | 96 | 133 | 214 | 84 | 240 | 15 | 128 | 163 | 303 | 8 | 136 | 73 | 215 | 851 | 156 | 1882 | 92 | 690 | 498 | 281 | 289 | 1144 | 555 | 90 | 216 | 137 | 29 | Number of interruptions - Class C | 2013
Number of interruptions - Class C, 2014 | 248 | 453 | 38 | 98 | 148 | 263 | 102 | 344 | 21 | 92 | 300 | 509 | 6 | 126 | 96 | 328 | 1113 | 223 | 2239 | 98 | 910 | 536 | 394 | 320 | 1423 | 579 | 129 | 385 | 166 | 29 | Number of interruptions - Class C | 2014
Number of interruptions - Class C, 2015 | 171 | 488 | 48 | 84 | 171 | 362 | 122 | 289 | 25 | 120 | 274 | 311 | 9 | 144 | 125 | 469 | 883 | 226 | 2760 | 109 | 667 | 620 | 401 | 368 | 1619 | 656 | 163 | 220 | 221 | 29 | Number of interruptions - Class C | 2015
Number of interruptions - Total, 2013 | 329 | 703 | 87 | 267 | 315 | 420 | 125 | 384 | 21 | 263 | 509 | 524 | 21 | 307 | 145 | 581 | 1246 | 677 | 3803 | 160 | 1132 | 1229 | 537 | 750 | 2150 | 935 | 190 | 327 | 233 | 29 | Number of interruptions - Total | 2013
Number of interruptions - Total, 2014 | 418 | 710 | 75 | 290 | 229 | 441 | 209 | 465 | 34 | 168 | 925 | 764 | 21 | 297 | 166 | 678 | 1543 | 764 | 4082 | 173 | 1338 | 1221 | 532 | 886 | 2697 | 995 | 215 | 510 | 264 | 29 | Number of interruptions - Total | 2014
Number of interruptions - Total, 2015 | 400 | 805 | 96 | 222 | 273 | 542 | 246 | 456 | 27 | 211 | 871 | 534 | 27 | 308 | 292 | 865 | 1491 | 649 | 4571 | 190 | 1436 | 1358 | 574 | 937 | 2780 | 1138 | 255 | 409 | 310 | 29 | Number of interruptions - Total | 2015
SAIDI - Class B, 2013 | 38.3167 | 21.81 | 72.04 | 82.5937 | 42.965 | 90.17 | 7.949 | 48.38 | 8.254 | 32.0597 | 67.462 | 68.4514 | 10.24 | 36.9822 | 4.8444 | 55.6027 | 11.34 | 130.52 | 60.0155 | 25.24 | 83.0125 | 81.021 | 144.3908 | 33.7182 | 20.1 | 14.7153 | 52.05 | 1.4065 | 65.6 | 29 | SAIDI - Class B | 2013
SAIDI - Class B, 2014 | 33.9899 | 22.7841 | 121.2858 | 78.8682 | 33.0502 | 71.3 | 14.494 | 56.7011 | 9.704 | 16.4561 | 88.3544 | 56.7 | 1.7648 | 53.6 | 7.6874 | 52.1 | 10.65 | 154.1 | 36.05 | 28.555 | 83.6106 | 66.818 | 21.8057 | 32.1818 | 23 | 21.9844 | 36.3 | 1.6662 | 41.26 | 29 | SAIDI - Class B | 2014
SAIDI - Class B, 2015 | 48.5904 | 24.3266 | 65.2575 | 50.9751 | 20.9 | 49.2279 | 16.18 | 66.7184 | 0.996 | 25.8838 | 89.03 | 52.03 | 2.548 | 57.7 | 12.7209 | 69.404 | 10.6874 | 133.106 | 46.0028 | 26.837 | 75.0734 | 82.832 | 251.8022 | 34.3841 | 19.9729 | 24.6445 | 28.47 | 3.5469 | 45.22 | 29 | SAIDI - Class B | 2015
SAIDI - Class C, 2013 | 109.95 | 53.8 | 111.59 | 41.2547 | 83.5821 | 196.99 | 50.1 | 114.5071 | 23.537 | 159.5431 | 186.62 | 70.9283 | 33.4 | 93.5464 | 49.8845 | 61.358 | 82.44 | 122.49 | 115.7691 | 63.3 | 116.5526 | 110.376 | 250.9141 | 55.5193 | 75.7 | 60.3967 | 100.03 | 41.8837 | 147.3 | 29 | SAIDI - Class C | 2013
SAIDI - Class C, 2014 | 824.4071 | 71.7163 | 50.7808 | 84.139 | 92.3326 | 213.5 | 52.8 | 775.1915 | 15.399 | 181.5238 | 862.9174 | 189.5 | 20.6115 | 75.88 | 87.4404 | 103.6 | 463.12 | 317.3 | 190.3603 | 42.688 | 186.845 | 110.951 | 478.3197 | 80.6385 | 128 | 69.1696 | 87.1 | 189.104 | 67.02 | 29 | SAIDI - Class C | 2014
SAIDI - Class C, 2015 | 91.2955 | 105.6977 | 2681.298 | 90.3923 | 99.1756 | 206.5562 | 123.119 | 131.5155 | 40.35 | 146.9737 | 102.42 | 77.88 | 17.389 | 122.77 | 38.1223 | 310.1953 | 115.4268 | 222.921 | 231.7952 | 41.326 | 203.9434 | 176.285 | 1585.99 | 85.9911 | 476.2473 | 80.4106 | 172.1 | 35.2098 | 555.16 | 29 | SAIDI - Class C | 2015
SAIDI - Limit, 2015 | 164.2206 | 98.29 |  | 197.5487 |  | 302.38 |  | 222.0731 | 45.65 | 220.0583 |  |  | 71.5364 | 162.5348 |  |  | 103.8 | 361.07 | 210.13 |  | 307.6921 | 0 | 579.7 | 148 | 127.3 | 0 |  | 40.74 |  | 19 | SAIDI - Limit | 2015
SAIDI - Normalised, 2013 | 148.2667 | 75.6 | 183.63 | 123.8484 | 126.5471 | 287.1738 | 58.04 | 150.3124 | 31.79 | 191.6029 | 137.36 | 34.3905 | 43.64 | 130.5287 | 54.7289 | 116.985 | 85.5 | 253 | 175.78 | 88.54 | 199.5651 | 191.4 | 327.1732 | 89.2375 | 95.8 | 75.1119 | 152.08 | 43.2901 | 206.27 | 29 | SAIDI - Normalised | 2013
SAIDI - Normalised, 2014 | 274.7657 | 94.5004 | 172.0666 | 163.0072 | 125.3828 | 279.8 | 67.294 | 239.5109 | 25.1 | 186.3412 | 206.271 | 246.2 | 22.3763 | 129.48 | 81.3724 | 147.7 | 106.28 | 348.2 | 206.9535 | 71.2433 | 270.4555 | 177.77 | 464.9094 | 112.8202 | 141 | 91.1541 | 123.4 | 78.8765 | 108.28 | 29 | SAIDI - Normalised | 2014
SAIDI - Normalised, 2015 | 140.2837 | 123.5875 | 287.5983 | 141.3674 | 120.1 | 255.7842 | 149.24 | 188.551 | 41.346 | 172.8575 | 163.45 | 129.91 | 19.937 | 157.7921 | 50.8431 | 203.5089 | 94.071 | 353.21 | 217.6524 | 65.6246 | 233.5435 | 259.117 | 599.923 | 115.2563 | 155.2704 | 103.1225 | 199.3 | 38.7572 | 152.58 | 29 | SAIDI - Normalised | 2015
SAIDI - Total, 2013 | 155.7667 | 75.61 | 195.61 | 388.9137 | 126.5471 | 454.15 | 58.049 | 182.0034 | 31.791 | 219.3913 | 254.082 | 139.3796 | 43.64 | 169.9311 | 56.1692 | 116.9607 | 94.32 | 258.85 | 224.5081 | 88.54 | 218.9449 | 194.307 | 395.3049 | 119.7489 | 96.9 | 75.1119 | 377.43 | 43.2901 | 220.5 | 29 | SAIDI - Total | 2013
SAIDI - Total, 2014 | 875.2381 | 94.5004 | 172.0666 | 249.9739 | 151.6118 | 379.3 | 67.394 | 831.8926 | 25.103 | 228.3637 | 951.2718 | 246.2 | 61.9653 | 157.22 | 95.2342 | 174.2 | 476.89 | 471.4 | 264.7373 | 71.243 | 285.0454 | 177.769 | 512.2978 | 127.6797 | 157.66 | 108.0136 | 494.43 | 218.2231 | 108.9 | 29 | SAIDI - Total | 2014
SAIDI - Total, 2015 | 161.0349 | 130.0243 | 2746.556 | 141.3674 | 120.0756 | 368.7452 | 158.827 | 198.2338 | 41.346 | 390.7028 | 191.67 | 129.91 | 19.937 | 210.256 | 51.0726 | 379.5993 | 126.2638 | 357.698 | 322.1018 | 68.163 | 299.9068 | 295.536 | 1887.816 | 121.3107 | 496.2202 | 106.7923 | 495.22 | 40.0652 | 600.38 | 29 | SAIDI - Total | 2015
SAIFI - Class B, 2013 | 0.15446 | 0.12 | 0.486 | 0.39269 | 0.1742 | 0.55 | 0.024 | 0.18108 | 0.0247 | 0.16905 | 0.2734 | 0.29975 | 0.05 | 0.33487 | 0.088708 | 0.26191 | 0.037 | 0.55 | 0.22567 | 0.13 | 0.5412 | 0.3696 | 0.644 | 0.31894 | 0.14 | 0.15332 | 0.1614 | 0.012425 | 0.23 | 29 | SAIFI - Class B | 2013
SAIFI - Class B, 2014 | 0.14863 | 0.10457 | 0.40844 | 0.48158 | 0.34334 | 0.42 | 0.056 | 0.19814 | 0.0295 | 0.12142 | 0.32732 | 0.26 | 0.20555 | 0.28 | 0.037782 | 0.22674 | 0.03 | 0.58 | 0.15024 | 0.16 | 0.46379 | 0.3174 | 0.14502 | 0.29225 | 0.14 | 0.20381 | 0.1409 | 0 | 0.19 | 29 | SAIFI - Class B | 2014
SAIFI - Class B, 2015 | 0.27527 | 0.12163 | 0.29092 | 0.2747 | 0.13056 | 0.34229 | 0.047 | 0.27611 | 0.0023 | 0.22173 | 0.315 | 0.23 | 0.903 | 0.2234 | 0.062765 | 0.25359 | 0.036954 | 0.5046 | 0.19577 | 0.159 | 0.42355 | 0.3494 | 0.96322 | 0.24944 | 0.099487 | 0.15718 | 0.1005 | 0.024389 | 0.191 | 29 | SAIFI - Class B | 2015
SAIFI - Class C, 2013 | 1.1435 | 0.93 | 1.24 | 2.3035 | 1.6239 | 3.27 | 0.909 | 1.5971 | 0.3099 | 2.1265 | 1.5223 | 1.065 | 0.51 | 1.1548 | 1.3219 | 1.567 | 0.933 | 1.75 | 1.6349 | 1.29 | 1.7762 | 2.2167 | 4.027 | 1.3181 | 0.87 | 1.2843 | 1.3397 | 0.56086 | 2.89 | 29 | SAIFI - Class C | 2013
SAIFI - Class C, 2014 | 2.0481 | 1.1062 | 1.1818 | 2.8338 | 2.3901 | 2.25 | 1.197 | 2.6937 | 0.4917 | 1.6507 | 2.6154 | 1.39 | 0.29302 | 1.06 | 1.6052 | 2.1 | 1.29 | 2.44 | 2.139 | 1.184 | 3.6668 | 2.5482 | 5.3407 | 1.4743 | 1.31 | 1.1631 | 1.7302 | 1.0954 | 1.51 | 29 | SAIFI - Class C | 2014
SAIFI - Class C, 2015 | 0.87136 | 1.2463 | 2.8215 | 2.1263 | 2.4521 | 3.6334 | 2.198 | 1.7755 | 0.7899 | 1.7597 | 1.159 | 1.18 | 0.669 | 1.179 | 1.0317 | 3.3336 | 1.137 | 2.767 | 2.096 | 0.705 | 3.6388 | 2.6951 | 5.4216 | 1.7227 | 1.7728 | 1.3702 | 2.1004 | 0.56176 | 3.1488 | 29 | SAIFI - Class C | 2015
SAIFI - Limit, 2015 | 1.6937 | 1.67 |  | 4.2538 |  | 4.26 |  | 1.9966 | 1.13 | 2.3962 |  |  | 1.1256 | 1.744 |  |  | 1.36 | 3.11 | 2.798 |  | 4.1547 | 0 | 7.66 | 2.725 | 1.86 | 0 |  | 0.602 |  | 19 | SAIFI - Limit | 2015
SAIFI - Normalised, 2013 | 1.2979 | 1.05 | 1.726 | 2.6962 | 1.7982 | 3.8158 | 0.93 | 1.4771 | 0.3346 | 2.2956 | 1.31 | 0.22622 | 0.56 | 1.4897 | 1.4106 | 1.8293 | 0.971 | 2.3 | 1.86 | 1.421 | 2.3174 | 2.59 | 4.671 | 1.637 | 1.01 | 1.4377 | 1.5011 | 0.573 | 2.7255 | 29 | SAIFI - Normalised | 2013
SAIFI - Normalised, 2014 | 1.999 | 1.2107 | 1.5903 | 3.3154 | 2.7334 | 2.67 | 1.253 | 2.4979 | 0.52 | 1.7721 | 2.05 | 1.65 | 0.49858 | 1.34 | 1.3087 | 2.32 | 1.225 | 2.95 | 2.2892 | 1.2013 | 4.1306 | 2.87 | 5.4857 | 1.7666 | 1.45 | 1.3669 | 1.8711 | 1.1067 | 1.71 | 29 | SAIFI - Normalised | 2014
SAIFI - Normalised, 2015 | 1.1566 | 1.3679 | 3.0664 | 2.401 | 2.58 | 3.9757 | 2.63 | 1.8406 | 0.7922 | 1.9815 | 1.4047 | 1.41 | 1.572 | 1.3989 | 1.0944 | 3.55 | 1.09 | 3.27 | 2.2918 | 0.8639 | 3.7429 | 3.04 | 6.3495 | 1.9722 | 1.8391 | 1.5274 | 2.2 | 0.58614 | 2.14 | 29 | SAIFI - Normalised | 2015
SAIFI - Total, 2013 | 1.5529 | 1.05 | 2.41 | 4.141 | 1.7981 | 4.83 | 0.933 | 2.2813 | 0.3346 | 3.011 | 1.7957 | 1.3647 | 0.56 | 1.9365 | 1.5066 | 1.8289 | 0.973 | 2.52 | 2.2862 | 1.42 | 2.6401 | 3.0001 | 4.671 | 1.9347 | 1.03 | 1.4377 | 2.0587 | 0.57329 | 3.47 | 29 | SAIFI - Total | 2013
SAIFI - Total, 2014 | 2.4494 | 1.2107 | 1.5903 | 6.4626 | 2.9806 | 5.17 | 1.283 | 2.8919 | 0.5212 | 2.1149 | 2.9427 | 1.65 | 1.4991 | 2.07 | 1.6433 | 2.7167 | 1.325 | 3.02 | 2.6305 | 1.344 | 4.6561 | 2.8656 | 5.6946 | 2.1514 | 1.59 | 1.6468 | 2.5851 | 1.5764 | 1.76 | 29 | SAIFI - Total | 2014
SAIFI - Total, 2015 | 1.4394 | 1.3679 | 3.1125 | 2.401 | 2.5827 | 5.0169 | 2.628 | 2.0516 | 0.7922 | 3.3083 | 1.478 | 1.41 | 1.572 | 1.841 | 1.096 | 3.5872 | 1.1758 | 3.386 | 2.549 | 0.864 | 4.4998 | 3.4564 | 7.3824 | 2.0223 | 1.8723 | 1.5495 | 3.4026 | 0.72424 | 3.3398 | 29 | SAIFI - Total | 2015
Note on O30: Taken from 2014 ID as excluded in 2015 ID
Note on AD31: Incorrect in 2013 ID
Note on O33: Equals 2015 Class B + Class C SAIDI (cross checked with compliance statement
Note on O43: Taken from 2014 ID as excluded in 2015 ID
Note on AD44: Incorrect in 2013 ID
Note on O46: Equals 2015 Class B + Class C SAIFI (cross checked with compliance statement

## EDB Select + Calculations
EDB Selection and Calculations
EDB | Top Energy
PQ Regulated | DPP
|  |  | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015
SAIDI
SAIDI - Class B |  |  | 37 | 39.5 | 39.4 | 22.3 | 18.2 | 36.633 | 73.8958 | 23.0886 | 20.972 | 15.331 | 144.3908 | 21.8057 | 251.8022
SAIDI - Class C |  |  | 382.9 | 311.9 | 343.1 | 499.8 | 398.9 | 781.669 | 841.2604 | 439.9433 | 419.045 | 419.65 | 250.9141 | 478.3197 | 1585.99
SAIDI - Class B and C | Vector & WE*
SAIDI - Normalised |  |  | 2011: 440.012; 2012: 436.48; 2013: 327.1732; 2014: 464.9094; 2015: 599.923
SAIDI - Limit | Applicable 2011-2015 |  | 2015: 579.7
SAIFI
SAIFI - Class B |  |  | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.34235 | 0.59954 | 0.15457 | 0.095 | 0.084 | 0.644 | 0.14502 | 0.96322
SAIFI - Class C |  |  | 6.1 | 4.2 | 4.3 | 5.4 | 5.4 | 6.0533 | 10.2823 | 4.0381 | 4.831 | 6.287 | 4.027 | 5.3407 | 5.4216
SAIFI - Class B and C | Vector & WE*
SAIFI - Normalised |  |  | 2011: 4.926; 2012: 6.385; 2013: 4.671; 2014: 5.4857; 2015: 6.3495
SAIFI - Limit | Applicable 2011-2015 |  | 2015: 7.66
Interruptions
Number of Interruptions - Class B |  |  | 144 | 169 | 147 | 159 | 168 | 264 | 293 | 159 | 131 | 167 | 256 | 137 | 171
Number of Interruptions - Class C |  |  | 249 | 219 | 220 | 368 | 330 | 335 | 443 | 288 | 308 | 394 | 281 | 394 | 401
Number of Interruptions - B&C | Vector & WE*
Calculations
SAIDI - Class B and C |  |  | 419.9 | 351.4 | 382.5 | 522.1 | 417.1 | 818.302 | 915.1562 | 463.0319 | 440.017 | 434.981 | 395.3049 | 500.1254 | 1837.7922
Non-normalised SAIDI, 2003-2010 |  | 536.1863
Non-normalised SAIDI, 2011-2015 |  | 721.6441
Non-normalised SAIDI, Change |  | 34.59%
SAIFI - Class B and C |  | 6.4 |  | 4.5 | 4.6 | 5.5 | 5.5 | 6.3957 | 10.8818 | 4.1926 | 4.926 | 6.371 | 4.671 | 5.4857 | 6.3848
Non-normalised SAIFI, 2003-2010 |  | 5.9963
Non-normalised SAIFI, 2011-2015 |  | 5.5677
Non-normalised SAIFI, Change |  | -7.147%
Number of Interruptions - Class B and C |  |  | 393 | 388 | 367 | 527 | 498 | 599 | 736 | 447 | 439 | 561 | 537 | 531 | 572
Number of Interruptions, 2003-2010 |  | 494.375
Number of Interruptions, 2011-2015 |  | 528
Number of Interruptions, Change |  | 6.802%
Normalised SAIDI relative to limit, 2011-2015 |  | -21.74%
Normalised SAIFI relative to limit, 2011-2015 |  | -27.37%
Exceeds SAIDI Limit |  |  | 2011: FALSE; 2012: FALSE; 2013: FALSE; 2014: FALSE; 2015: TRUE
Exceeds SAIFI Limit |  |  | 2011: FALSE; 2012: FALSE; 2013: FALSE; 2014: FALSE; 2015: FALSE
Limit exceeded - SAIDI or SAIFI |  |  | 2011: FALSE; 2012: FALSE; 2013: FALSE; 2014: FALSE; 2015: TRUE
Compliance breach? |  |  | 2012: FALSE; 2013: FALSE; 2014: FALSE; 2015: FALSE
Exceeds SAIDI Limit - Count, 2011-2015 |  | 1
Exceeds SAIFI Limit - Count, 2011-2015 |  | 0
Total compliance breaches |  | 0
Data Table for industry average
| xxx | Alpine Energy | Aurora Energy | Buller Electricity | Centralines | Counties Power | Eastland Network | Electra | Electricity Ashburton | Electricity Invercargill | Horizon Energy | MainPower NZ | Marlborough Lines | Nelson Electricity | Network Tasman | Network Waitaki | Northpower | Orion NZ | OtagoNet | Powerco | Scanpower | The Lines Company | The Power Company | Top Energy | Unison Networks | Vector Lines | WEL Networks | Waipa Network | Wellington Electricity | Westpower | Industry | PQR | ID only
Non-normalised SAIDI, 2003-2010 | 536.1863 | 270.4766 | 89.3312 | 237.5762 | 202.9987 | 104.6317 | 295.3463 | 169.845 | 428.4556 | 32.3279 | 167.78 | 131.091 | 240.3088 | 59.1626 | 144.6162 | 130.1775 | 226.9112 | 70.89 | 340.831 | 255.3652 | 76.695 | 338.8887 | 186.8021 | 536.1863 | 135.3154 | 142.5465 | 81.849 | 184.5837 | 35.6602 | 211.7413 | 190.6342 | 208.5987 | 165.1844
Non-normalised SAIDI, 2011-2015 | 721.6441 | 306.7359 | 111.0289 | 728.7904 | 177.4006 | 119.6394 | 311.4028 | 94.251 | 329.6779 | 41.3284 | 182.8934 | 370.0728 | 235.6219 | 52.8147 | 155.4037 | 62.572 | 186.618 | 184.8328 | 329.6572 | 257.0427 | 86.0772 | 273.1995 | 215.0874 | 721.6441 | 139.9308 | 192.3912 | 84.5787 | 166.444 | 70.6869 | 271.038 | 222.7194 | 225.7689 | 218.3992
Non-normalised SAIFI, 2003-2010 | 5.9963 | 1.5065 | 1.4745 | 1.7775 | 4.5425 | 2.5239 | 3.0375 | 1.9545 | 1.8326 | 0.85602 | 1.8522 | 1.4577 | 2.42 | 0.84512 | 1.4925 | 1.4488 | 2.9641 | 0.68625 | 2.8661 | 2.7566 | 0.99875 | 3.9163 | 3.321 | 5.9963 | 2.2093 | 1.5647 | 1.5841 | 2.7933 | 0.52867 | 2.184 | 2.1859 | 2.2332 | 2.119
Non-normalised SAIFI, 2011-2015 | 5.5677 | 1.5205 | 1.3734 | 2.0617 | 3.3705 | 2.4812 | 3.4711 | 1.6676 | 2.0734 | 0.8246 | 2.1362 | 2.0465 | 1.8609 | 0.86012 | 1.4504 | 1.1816 | 2.523 | 1.1348 | 2.6422 | 2.3387 | 1.3016 | 3.5941 | 2.9493 | 5.5677 | 1.9624 | 1.3383 | 1.3275 | 1.9347 | 0.70121 | 2.53 | 2.0767 | 2.1388 | 1.9888
Number of Interruptions, 2003-2010 | 494.375 | 227 | 709.25 | 78.875 | 231.5 | 247 | 374.375 | 217 | 481.625 | 24.25 | 150.125 | 372.75 | 594.25 | 30.875 | 267.875 | 228.75 | 530.5 | 818.375 | 469.75 | 2747.625 | 129.875 | 1069.75 | 694.5 | 494.375 | 882.625 | 1594.1667 | 296.25 | 185.375 | 252.1667 | 210.125 | 14610.9583 | 10825.7083 | 3785.25
Number of Interruptions, 2011-2015 | 528 | 386.8 | 766.4 | 91 | 262.8 | 286.8 | 476.8 | 178 | 456.4 | 33.6 | 192.8 | 690 | 583.2 | 23.8 | 312.2 | 195.4 | 678.2 | 1116 | 688 | 3494.2 | 183.8 | 1196.8 | 1327.4 | 528 | 826 | 2378.6 | 821.4 | 200.8 | 366.4 | 254.6 | 18996.2 | 13505.6 | 5490.6
Data Table for output tables
| xxx | Alpine Energy | Aurora Energy | Buller Electricity | Centralines | Counties Power | Eastland Network | Electra | Electricity Ashburton | Electricity Invercargill | Horizon Energy | MainPower NZ | Marlborough Lines | Nelson Electricity | Network Tasman | Network Waitaki | Northpower | Orion NZ | OtagoNet | Powerco | Scanpower | The Lines Company | The Power Company | Top Energy | Unison Networks | Vector Lines | WEL Networks | Waipa Network | Wellington Electricity | Westpower | Industry | PQR | ID only
Non-normalised SAIDI, change (%) | 34.59% | 13.41% | 24.29% | 206.8% | -12.61% | 14.34% | 5.437% | -44.51% | -23.05% | 27.84% | 9.008% | 182.3% | -1.95% | -10.73% | 7.459% | -51.93% | -17.76% | 160.7% | -3.278% | 0.6569% | 12.23% | -19.38% | 15.14% | 34.59% | 3.411% | 34.97% | 3.335% | -9.827% | 98.22% | 28% | 16.83% | 8.231% | 32.22%
Non-normalised SAIFI, change (%) | -7.147% | 0.9285% | -6.856% | 15.99% | -25.8% | -1.691% | 14.28% | -14.68% | 13.14% | -3.671% | 15.33% | 40.39% | -23.1% | 1.774% | -2.82% | -18.44% | -14.88% | 65.36% | -7.815% | -15.16% | 30.32% | -8.227% | -11.19% | -7.147% | -11.18% | -14.47% | -16.2% | -30.74% | 32.64% | 15.84% | -4.994% | -4.225% | -6.143%
Number of Interruptions, change (%) | 6.802% | 70.4% | 8.058% | 15.37% | 13.52% | 16.11% | 27.36% | -17.97% | -5.237% | 38.56% | 28.43% | 85.11% | -1.859% | -22.91% | 16.55% | -14.58% | 27.84% | 36.37% | 46.46% | 27.17% | 41.52% | 11.88% | 91.13% | 6.802% | -6.416% | 49.21% | 177.3% | 8.321% | 45.3% | 21.17% | 30.01% | 24.75% | 45.05%
Normalised SAIDI relative to limit, 2011-2015 | -21.74% | 15.8% | 3.192% | N/A | -21.27% | N/A | 2.447% | N/A | -14.39% | -9.469% | -17.94% | N/A | N/A | -44.6% | -7.069% | N/A | N/A | N/A | -18.13% | 0.1291% | N/A | -16.8% | N/A | -21.74% | -18.19% | -5.495% | N/A | N/A | 18.58% | N/A
Normalised SAIFI relative to limit, 2011-2015 | -27.37% | -12.35% | -18.44% | N/A | -20.89% | N/A | -18.51% | N/A | -8.429% | -27.01% | -10.85% | N/A | N/A | -31.46% | -16.91% | N/A | N/A | N/A | -15.83% | -16.81% | N/A | -14.12% | N/A | -27.37% | -27.92% | -28.41% | N/A | N/A | 16.88% | N/A
Number of times SAIDI limit exceeded | 1 | 2 | 3 | N/A | 0 | N/A | 2 | N/A | 1 | 1 | 0 | N/A | N/A | 0 | 1 | N/A | N/A | N/A | 0 | 2 | N/A | 1 | N/A | 1 | 1 | 2 | N/A | N/A | 3 | N/A
Number of times SAIFI limit exceeded | 0 | 2 | 1 | N/A | 1 | N/A | 0 | N/A | 1 | 2 | 0 | N/A | N/A | 1 | 0 | N/A | N/A | N/A | 1 | 0 | N/A | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 2 | N/A
Total technical breaches | 0 | 0 | 1 | N/A | 0 | N/A | 1 | N/A | 0 | 1 | 0 | N/A | N/A | 0 | 0 | N/A | N/A | N/A | 0 | 0 | N/A | 0 | N/A | 0 | 0 | 1 | N/A | N/A | 2 | N/A
Note on B11: For a longer time series we have used data provided from an information request as part of the 2015 DPP reset.
Note on B18: For a longer time series we have used data provided from an information request as part of the 2015 DPP reset.
Note on B25: For a longer time series we have used data provided from an information request as part of the 2015 DPP reset.

## Chart data
Data for graphs
|  | Non-normalised SAIDI, 2011-2015 |  |  | Non-normalised SAIDI, 2011-2015 |  |  |  |  | Non-normalised SAIDI, change (%) |  |  | Non-normalised SAIDI, change (%) |  |  |  |  | Non-normalised SAIFI, 2011-2015 |  |  | Non-normalised SAIFI, 2011-2015 |  |  |  |  | Non-normalised SAIFI, change (%) |  |  | Non-normalised SAIFI, change (%) |  |  |  |  | Normalised SAIDI relative to limit, 2011-2015 | [5 empty] | Normalised SAIFI relative to limit, 2011-2015
| 12 | Alpine Energy | 306.7359 | 1 | Electricity Invercargill | 41.3284 |  |  | 6 | Alpine Energy | 13.4057 | 1 | Wellington Electricity | 98.2237 |  |  | 7 | Alpine Energy | 1.5205 | 1 | Wellington Electricity | 0.70121 |  |  | 6 | Alpine Energy | 0.92848 | 1 | Wellington Electricity | 32.6362 |  |  | 2 | Alpine Energy | 15.7963 | 1 | Wellington Electricity | 18.577 | 4 | Alpine Energy | -12.3474 | 1 | Wellington Electricity | 16.8795
| 4 | Aurora Energy | 111.0289 | 2 | Nelson Electricity | 52.8147 |  |  | 5 | Aurora Energy | 24.289 | 2 | Vector Lines | 34.9673 |  |  | 5 | Aurora Energy | 1.3734 | 2 | Electricity Invercargill | 0.8246 |  |  | 9 | Aurora Energy | -6.8562 | 2 | Horizon Energy | 15.3295 |  |  | 3 | Aurora Energy | 3.1924 | 2 | Alpine Energy | 15.7963 | 9 | Aurora Energy | -18.4357 | 2 | Electricity Ashburton | -8.4293
| 7 | Centralines | 177.4006 | 3 | Wellington Electricity | 70.6869 |  |  | 14 | Centralines | -12.61 | 3 | Top Energy | 34.5883 |  |  | 13 | Centralines | 3.3705 | 3 | Nelson Electricity | 0.86012 |  |  | 16 | Centralines | -25.8003 | 3 | Eastland Network | 14.2761 |  |  | 14 | Centralines | -21.2662 | 3 | Aurora Energy | 3.1924 | 11 | Centralines | -20.8852 | 3 | Horizon Energy | -10.8543
| 13 | Eastland Network | 311.4028 | 4 | Aurora Energy | 111.0289 |  |  | 9 | Eastland Network | 5.4365 | 4 | Electricity Invercargill | 27.8414 |  |  | 14 | Eastland Network | 3.4711 | 4 | Vector Lines | 1.3383 |  |  | 3 | Eastland Network | 14.2761 | 4 | Electricity Ashburton | 13.143 |  |  | 4 | Eastland Network | 2.4473 | 4 | Eastland Network | 2.4473 | 10 | Eastland Network | -18.5138 | 4 | Alpine Energy | -12.3474
| 15 | Electricity Ashburton | 329.6779 | 5 | Unison Networks | 139.9308 |  |  | 16 | Electricity Ashburton | -23.0544 | 5 | Aurora Energy | 24.289 |  |  | 9 | Electricity Ashburton | 2.0734 | 5 | Aurora Energy | 1.3734 |  |  | 4 | Electricity Ashburton | 13.143 | 5 | Nelson Electricity | 1.7738 |  |  | 9 | Electricity Ashburton | -14.3885 | 5 | Powerco | 0.12913 | 2 | Electricity Ashburton | -8.4293 | 5 | The Lines Company | -14.1161
| 1 | Electricity Invercargill | 41.3284 | 6 | Network Tasman | 155.4037 |  |  | 4 | Electricity Invercargill | 27.8414 | 6 | Alpine Energy | 13.4057 |  |  | 2 | Electricity Invercargill | 0.8246 | 6 | Network Tasman | 1.4504 |  |  | 8 | Electricity Invercargill | -3.671 | 6 | Alpine Energy | 0.92848 |  |  | 8 | Electricity Invercargill | -9.4691 | 6 | Vector Lines | -5.4954 | 12 | Electricity Invercargill | -27.0108 | 6 | OtagoNet | -15.8259
| 8 | Horizon Energy | 182.8934 | 7 | Centralines | 177.4006 |  |  | 7 | Horizon Energy | 9.0079 | 7 | Horizon Energy | 9.0079 |  |  | 10 | Horizon Energy | 2.1362 | 7 | Alpine Energy | 1.5205 |  |  | 2 | Horizon Energy | 15.3295 | 7 | Network Tasman | -2.82 |  |  | 11 | Horizon Energy | -17.9445 | 7 | Network Tasman | -7.0686 | 3 | Horizon Energy | -10.8543 | 7 | Powerco | -16.8122
| 2 | Nelson Electricity | 52.8147 | 8 | Horizon Energy | 182.8934 |  |  | 13 | Nelson Electricity | -10.7297 | 8 | Network Tasman | 7.4594 |  |  | 3 | Nelson Electricity | 0.86012 | 8 | Unison Networks | 1.9624 |  |  | 5 | Nelson Electricity | 1.7738 | 8 | Electricity Invercargill | -3.671 |  |  | 16 | Nelson Electricity | -44.6007 | 8 | Electricity Invercargill | -9.4691 | 16 | Nelson Electricity | -31.4638 | 8 | Network Tasman | -16.9101
| 6 | Network Tasman | 155.4037 | 9 | Vector Lines | 192.3912 |  |  | 8 | Network Tasman | 7.4594 | 9 | Eastland Network | 5.4365 |  |  | 6 | Network Tasman | 1.4504 | 9 | Electricity Ashburton | 2.0734 |  |  | 7 | Network Tasman | -2.82 | 9 | Aurora Energy | -6.8562 |  |  | 7 | Network Tasman | -7.0686 | 9 | Electricity Ashburton | -14.3885 | 8 | Network Tasman | -16.9101 | 9 | Aurora Energy | -18.4357
| 14 | OtagoNet | 329.6572 | 10 | Powerco | 257.0427 |  |  | 12 | OtagoNet | -3.2784 | 10 | Unison Networks | 3.4108 |  |  | 12 | OtagoNet | 2.6422 | 10 | Horizon Energy | 2.1362 |  |  | 11 | OtagoNet | -7.8146 | 10 | Top Energy | -7.1471 |  |  | 12 | OtagoNet | -18.1253 | 10 | The Lines Company | -16.7989 | 6 | OtagoNet | -15.8259 | 10 | Eastland Network | -18.5138
| 10 | Powerco | 257.0427 | 11 | The Lines Company | 273.1995 |  |  | 11 | Powerco | 0.65688 | 11 | Powerco | 0.65688 |  |  | 11 | Powerco | 2.3387 | 11 | Powerco | 2.3387 |  |  | 15 | Powerco | -15.1571 | 11 | OtagoNet | -7.8146 |  |  | 5 | Powerco | 0.12913 | 11 | Horizon Energy | -17.9445 | 7 | Powerco | -16.8122 | 11 | Centralines | -20.8852
| 11 | The Lines Company | 273.1995 | 12 | Alpine Energy | 306.7359 |  |  | 15 | The Lines Company | -19.3837 | 12 | OtagoNet | -3.2784 |  |  | 15 | The Lines Company | 3.5941 | 12 | OtagoNet | 2.6422 |  |  | 12 | The Lines Company | -8.2273 | 12 | The Lines Company | -8.2273 |  |  | 10 | The Lines Company | -16.7989 | 12 | OtagoNet | -18.1253 | 5 | The Lines Company | -14.1161 | 12 | Electricity Invercargill | -27.0108
| 16 | Top Energy | 721.6441 | 13 | Eastland Network | 311.4028 |  |  | 3 | Top Energy | 34.5883 | 13 | Nelson Electricity | -10.7297 |  |  | 16 | Top Energy | 5.5677 | 13 | Centralines | 3.3705 |  |  | 10 | Top Energy | -7.1471 | 13 | Unison Networks | -11.1767 |  |  | 15 | Top Energy | -21.7355 | 13 | Unison Networks | -18.1877 | 13 | Top Energy | -27.3704 | 13 | Top Energy | -27.3704
| 5 | Unison Networks | 139.9308 | 14 | OtagoNet | 329.6572 |  |  | 10 | Unison Networks | 3.4108 | 14 | Centralines | -12.61 |  |  | 8 | Unison Networks | 1.9624 | 14 | Eastland Network | 3.4711 |  |  | 13 | Unison Networks | -11.1767 | 14 | Vector Lines | -14.4692 |  |  | 13 | Unison Networks | -18.1877 | 14 | Centralines | -21.2662 | 14 | Unison Networks | -27.9241 | 14 | Unison Networks | -27.9241
| 9 | Vector Lines | 192.3912 | 15 | Electricity Ashburton | 329.6779 |  |  | 2 | Vector Lines | 34.9673 | 15 | The Lines Company | -19.3837 |  |  | 4 | Vector Lines | 1.3383 | 15 | The Lines Company | 3.5941 |  |  | 14 | Vector Lines | -14.4692 | 15 | Powerco | -15.1571 |  |  | 6 | Vector Lines | -5.4954 | 15 | Top Energy | -21.7355 | 15 | Vector Lines | -28.4094 | 15 | Vector Lines | -28.4094
| 3 | Wellington Electricity | 70.6869 | 16 | Top Energy | 721.6441 |  |  | 1 | Wellington Electricity | 98.2237 | 16 | Electricity Ashburton | -23.0544 |  |  | 1 | Wellington Electricity | 0.70121 | 16 | Top Energy | 5.5677 |  |  | 1 | Wellington Electricity | 32.6362 | 16 | Centralines | -25.8003 |  |  | 1 | Wellington Electricity | 18.577 | 16 | Nelson Electricity | -44.6007 | 1 | Wellington Electricity | 16.8795 | 16 | Nelson Electricity | -31.4638
|  | PQR | 225.7689 | [6 empty] | PQR | 8.2312 | [6 empty] | PQR | 2.1388 | [6 empty] | PQR | -4.2251
|  | Non-normalised SAIDI, 2011-2015 | [7 empty] | Non-normalised SAIDI, change (%) | [7 empty] | Non-normalised SAIFI, 2011-2015 | [7 empty] | Non-normalised SAIFI, change (%)
|  | PQR | 225.7689 | [6 empty] | PQR | 8.2312 | [6 empty] | PQR | 2.1388 | [6 empty] | PQR | -4.2251
|  | ID only | 218.3992 | [6 empty] | ID only | 32.2154 | [6 empty] | ID only | 1.9888 | [6 empty] | ID only | -6.1427
|  | Non-normalised SAIDI, 2011-2015 |  |  | Non-normalised SAIDI, 2011-2015 | Default price-quality path | Information disclosure only | Customised price-quality path |  | Non-normalised SAIDI, change (%) |  |  | Non-normalised SAIDI, change (%) | Default price-quality path | Information disclosure only | Customised price-quality path |  | Non-normalised SAIFI, 2011-2015 |  |  | Non-normalised SAIFI, 2011-2015 | Default price-quality path | Information disclosure only | Customised price-quality path |  | Non-normalised SAIFI, change (%) |  |  | Non-normalised SAIFI, change (%) | Default price-quality path | Information disclosure only | Customised price-quality path
| 23 | Alpine Energy | 306.7359 | 1 | Electricity Invercargill | 41.3284 |  |  | 12 | Alpine Energy | 13.4057 | 1 | Buller Electricity |  | 206.7606 |  | 11 | Alpine Energy | 1.5205 | 1 | Wellington Electricity | 0.70121 |  |  | 11 | Alpine Energy | 0.92848 | 1 | Orion NZ |  |  | 65.361 |  | Alpine Energy | DPP
| 8 | Aurora Energy | 111.0289 | 2 | Nelson Electricity | 52.8147 |  |  | 9 | Aurora Energy | 24.289 | 2 | MainPower NZ |  | 182.3022 |  | 9 | Aurora Energy | 1.3734 | 2 | Electricity Invercargill | 0.8246 |  |  | 15 | Aurora Energy | -6.8562 | 2 | MainPower NZ |  | 40.3872 |  |  | Aurora Energy | DPP
| 29 | Buller Electricity | 728.7904 | 3 | Network Waitaki |  | 62.572 |  | 1 | Buller Electricity | 206.7606 | 3 | Orion NZ |  |  | 160.7319 | 17 | Buller Electricity | 2.0617 | 3 | Nelson Electricity | 0.86012 |  |  | 5 | Buller Electricity | 15.9912 | 3 | Wellington Electricity | 32.6362 |  |  |  | Buller Electricity | ID
| 13 | Centralines | 177.4006 | 4 | Wellington Electricity | 70.6869 |  |  | 24 | Centralines | -12.61 | 4 | Wellington Electricity | 98.2237 |  |  | 26 | Centralines | 3.3705 | 4 | Orion NZ |  |  | 1.1348 | 28 | Centralines | -25.8003 | 4 | Scanpower |  | 30.3229 |  |  | Centralines | DPP
| 9 | Counties Power | 119.6394 | 5 | WEL Networks |  | 84.5787 |  | 11 | Counties Power | 14.3433 | 5 | Vector Lines | 34.9673 |  |  | 21 | Counties Power | 2.4812 | 5 | Network Waitaki |  | 1.1816 |  | 12 | Counties Power | -1.6914 | 5 | Buller Electricity |  | 15.9912 |  |  | Counties Power | ID
| 24 | Eastland Network | 311.4028 | 6 | Scanpower |  | 86.0772 |  | 16 | Eastland Network | 5.4365 | 6 | Top Energy | 34.5883 |  |  | 27 | Eastland Network | 3.4711 | 6 | Scanpower |  | 1.3016 |  | 8 | Eastland Network | 14.2761 | 6 | Westpower |  | 15.8407 |  |  | Eastland Network | DPP
| 7 | Electra | 94.251 | 7 | Electra |  | 94.251 |  | 28 | Electra | -44.5076 | 7 | Westpower |  | 28.0043 |  | 12 | Electra | 1.6676 | 7 | WEL Networks |  | 1.3275 |  | 22 | Electra | -14.6789 | 7 | Horizon Energy | 15.3295 |  |  |  | Electra | ID
| 26 | Electricity Ashburton | 329.6779 | 8 | Aurora Energy | 111.0289 |  |  | 27 | Electricity Ashburton | -23.0544 | 8 | Electricity Invercargill | 27.8414 |  |  | 18 | Electricity Ashburton | 2.0734 | 8 | Vector Lines | 1.3383 |  |  | 9 | Electricity Ashburton | 13.143 | 8 | Eastland Network | 14.2761 |  |  |  | Electricity Ashburton | DPP
| 1 | Electricity Invercargill | 41.3284 | 9 | Counties Power |  | 119.6394 |  | 8 | Electricity Invercargill | 27.8414 | 9 | Aurora Energy | 24.289 |  |  | 2 | Electricity Invercargill | 0.8246 | 9 | Aurora Energy | 1.3734 |  |  | 14 | Electricity Invercargill | -3.671 | 9 | Electricity Ashburton | 13.143 |  |  |  | Electricity Invercargill | DPP
| 14 | Horizon Energy | 182.8934 | 10 | Unison Networks | 139.9308 |  |  | 14 | Horizon Energy | 9.0079 | 10 | The Power Company |  | 15.1418 |  | 19 | Horizon Energy | 2.1362 | 10 | Network Tasman | 1.4504 |  |  | 7 | Horizon Energy | 15.3295 | 10 | Nelson Electricity | 1.7738 |  |  |  | Horizon Energy | DPP
| 27 | MainPower NZ | 370.0728 | 11 | Network Tasman | 155.4037 |  |  | 2 | MainPower NZ | 182.3022 | 11 | Counties Power |  | 14.3433 |  | 16 | MainPower NZ | 2.0465 | 11 | Alpine Energy | 1.5205 |  |  | 2 | MainPower NZ | 40.3872 | 11 | Alpine Energy | 0.92848 |  |  |  | MainPower NZ | ID
| 19 | Marlborough Lines | 235.6219 | 12 | Waipa Network |  | 166.444 |  | 20 | Marlborough Lines | -1.9503 | 12 | Alpine Energy | 13.4057 |  |  | 13 | Marlborough Lines | 1.8609 | 12 | Electra |  | 1.6676 |  | 27 | Marlborough Lines | -23.1014 | 12 | Counties Power |  | -1.6914 |  |  | Marlborough Lines | ID
| 2 | Nelson Electricity | 52.8147 | 13 | Centralines | 177.4006 |  |  | 23 | Nelson Electricity | -10.7297 | 13 | Scanpower |  | 12.2331 |  | 3 | Nelson Electricity | 0.86012 | 13 | Marlborough Lines |  | 1.8609 |  | 10 | Nelson Electricity | 1.7738 | 13 | Network Tasman | -2.82 |  |  |  | Nelson Electricity | DPP
| 11 | Network Tasman | 155.4037 | 14 | Horizon Energy | 182.8934 |  |  | 15 | Network Tasman | 7.4594 | 14 | Horizon Energy | 9.0079 |  |  | 10 | Network Tasman | 1.4504 | 14 | Waipa Network |  | 1.9347 |  | 13 | Network Tasman | -2.82 | 14 | Electricity Invercargill | -3.671 |  |  |  | Network Tasman | DPP
| 3 | Network Waitaki | 62.572 | 15 | Orion NZ |  |  | 184.8328 | 29 | Network Waitaki | -51.9333 | 15 | Network Tasman | 7.4594 |  |  | 5 | Network Waitaki | 1.1816 | 15 | Unison Networks | 1.9624 |  |  | 26 | Network Waitaki | -18.44 | 15 | Aurora Energy | -6.8562 |  |  |  | Network Waitaki | ID
| 16 | Northpower | 186.618 | 16 | Northpower |  | 186.618 |  | 25 | Northpower | -17.7573 | 16 | Eastland Network | 5.4365 |  |  | 22 | Northpower | 2.523 | 16 | MainPower NZ |  | 2.0465 |  | 23 | Northpower | -14.8836 | 16 | Top Energy | -7.1471 |  |  |  | Northpower | ID
| 15 | Orion NZ | 184.8328 | 17 | Vector Lines | 192.3912 |  |  | 3 | Orion NZ | 160.7319 | 17 | Unison Networks | 3.4108 |  |  | 4 | Orion NZ | 1.1348 | 17 | Buller Electricity |  | 2.0617 |  | 1 | Orion NZ | 65.361 | 17 | OtagoNet | -7.8146 |  |  |  | Orion NZ | CPP
| 25 | OtagoNet | 329.6572 | 18 | The Power Company |  | 215.0874 |  | 21 | OtagoNet | -3.2784 | 18 | WEL Networks |  | 3.335 |  | 24 | OtagoNet | 2.6422 | 18 | Electricity Ashburton | 2.0734 |  |  | 17 | OtagoNet | -7.8146 | 18 | The Lines Company | -8.2273 |  |  |  | OtagoNet | DPP
| 20 | Powerco | 257.0427 | 19 | Marlborough Lines |  | 235.6219 |  | 19 | Powerco | 0.65688 | 19 | Powerco | 0.65688 |  |  | 20 | Powerco | 2.3387 | 19 | Horizon Energy | 2.1362 |  |  | 24 | Powerco | -15.1571 | 19 | Unison Networks | -11.1767 |  |  |  | Powerco | DPP
| 6 | Scanpower | 86.0772 | 20 | Powerco | 257.0427 |  |  | 13 | Scanpower | 12.2331 | 20 | Marlborough Lines |  | -1.9503 |  | 6 | Scanpower | 1.3016 | 20 | Powerco | 2.3387 |  |  | 4 | Scanpower | 30.3229 | 20 | The Power Company |  | -11.1911 |  |  | Scanpower | ID
| 22 | The Lines Company | 273.1995 | 21 | Westpower |  | 271.038 |  | 26 | The Lines Company | -19.3837 | 21 | OtagoNet | -3.2784 |  |  | 28 | The Lines Company | 3.5941 | 21 | Counties Power |  | 2.4812 |  | 18 | The Lines Company | -8.2273 | 21 | Vector Lines | -14.4692 |  |  |  | The Lines Company | DPP
| 18 | The Power Company | 215.0874 | 22 | The Lines Company | 273.1995 |  |  | 10 | The Power Company | 15.1418 | 22 | Waipa Network |  | -9.8274 |  | 25 | The Power Company | 2.9493 | 22 | Northpower |  | 2.523 |  | 20 | The Power Company | -11.1911 | 22 | Electra |  | -14.6789 |  |  | The Power Company | ID
| 28 | Top Energy | 721.6441 | 23 | Alpine Energy | 306.7359 |  |  | 6 | Top Energy | 34.5883 | 23 | Nelson Electricity | -10.7297 |  |  | 29 | Top Energy | 5.5677 | 23 | Westpower |  | 2.53 |  | 16 | Top Energy | -7.1471 | 23 | Northpower |  | -14.8836 |  |  | Top Energy | DPP
| 10 | Unison Networks | 139.9308 | 24 | Eastland Network | 311.4028 |  |  | 17 | Unison Networks | 3.4108 | 24 | Centralines | -12.61 |  |  | 15 | Unison Networks | 1.9624 | 24 | OtagoNet | 2.6422 |  |  | 19 | Unison Networks | -11.1767 | 24 | Powerco | -15.1571 |  |  |  | Unison Networks | DPP
| 17 | Vector Lines | 192.3912 | 25 | OtagoNet | 329.6572 |  |  | 5 | Vector Lines | 34.9673 | 25 | Northpower |  | -17.7573 |  | 8 | Vector Lines | 1.3383 | 25 | The Power Company |  | 2.9493 |  | 21 | Vector Lines | -14.4692 | 25 | WEL Networks |  | -16.1993 |  |  | Vector Lines | DPP
| 5 | WEL Networks | 84.5787 | 26 | Electricity Ashburton | 329.6779 |  |  | 18 | WEL Networks | 3.335 | 26 | The Lines Company | -19.3837 |  |  | 7 | WEL Networks | 1.3275 | 26 | Centralines | 3.3705 |  |  | 25 | WEL Networks | -16.1993 | 26 | Network Waitaki |  | -18.44 |  |  | WEL Networks | ID
| 12 | Waipa Network | 166.444 | 27 | MainPower NZ |  | 370.0728 |  | 22 | Waipa Network | -9.8274 | 27 | Electricity Ashburton | -23.0544 |  |  | 14 | Waipa Network | 1.9347 | 27 | Eastland Network | 3.4711 |  |  | 29 | Waipa Network | -30.7352 | 27 | Marlborough Lines |  | -23.1014 |  |  | Waipa Network | ID
| 4 | Wellington Electricity | 70.6869 | 28 | Top Energy | 721.6441 |  |  | 4 | Wellington Electricity | 98.2237 | 28 | Electra |  | -44.5076 |  | 1 | Wellington Electricity | 0.70121 | 28 | The Lines Company | 3.5941 |  |  | 3 | Wellington Electricity | 32.6362 | 28 | Centralines | -25.8003 |  |  |  | Wellington Electricity | DPP
| 21 | Westpower | 271.038 | 29 | Buller Electricity |  | 728.7904 |  | 7 | Westpower | 28.0043 | 29 | Network Waitaki |  | -51.9333 |  | 23 | Westpower | 2.53 | 29 | Top Energy | 5.5677 |  |  | 6 | Westpower | 15.8407 | 29 | Waipa Network |  | -30.7352 |  |  | Westpower | ID

## Charts
Charts for report
Price-quality businesses
| Non-normalised SAIDI, 2011-2015 | Non-normalised SAIDI, change (%) | Non-normalised SAIFI, 2011-2015 | Non-normalised SAIFI, change (%)
All electricity distributors
| Non-normalised SAIDI, 2011-2015 | Non-normalised SAIDI, change (%) | Non-normalised SAIFI, 2011-2015 | Non-normalised SAIFI, change (%)
Price-quality vs. ID only businesses
| Non-normalised SAIDI, 2011-2015 | Non-normalised SAIDI, change (%) | Non-normalised SAIFI, 2011-2015 | Non-normalised SAIFI, change (%)
Reliability relative to compliance limit
| Normalised SAIDI relative to limit, 2011-2015 | Normalised SAIFI relative to limit, 2011-2015